CITY WATER & WASTE

PRO-FORMA

GENERIC ELECTRICAL AND AUTOMATION

SPECIFICATION ISSUE 4.3

PROJECT NAME

CONTENTS

INTRODUCTION

1	SCOPE OF WORK

1.1	PRELIMINARY

1.2	PROJECT NAME

1.3	PROJECT LOCATION

1.4	KEY PERSONNEL

1.5	PROJECT BACKGROUND AND REQUIRED OUTCOMES

1.6	PROJECT PROGRAMME

1.7	SPECIFIC HEALTH AND SAFETY REQUIREMENTS

1.8	OPERATIONAL RESPONSE

1.9	SPECIFIC PROJECT TECHNICAL REQUIREMENTS

1.10	DELIVERY OF EQUIPMENT

1.11	DOCUMENTATION

1.12	SCOPE OF WORK

1.13	CONTRACTORS DESIGN RESPONSIBILITIES

1.14	DETAILED SCOPE OF WORK

2	PREFERRED SUPPLIERS & EQUIPMENT

2.1	PRELIMINARY

2.2	ELECTRICAL CONTRACTORS

2.3	SUPPLIERS

2.4	SYSTEM INTEGRATORS

2.5	EQUIPMENT

2.6	VENDOR PACKAGES

3	GENERAL SITE AND PROJECT REQUIREMENTS

3.1	PRELIMINARY

3.2	SITE INFORMATION

3.3	HEALTH AND SAFETY

3.4	OPERATIONAL RESPONSE

3.5	GENERAL STANDARDS

3.6	STANDARDS AND REGULATIONS

3.7	QUALITY ASSURANCE

3.8	SPECIFICATIONS AND DRAWINGS

3.9	IDENTIFICATION AND LABELLING

3.10	TECHNICAL

3.11	POWER SUPPLY

3.12	TESTING AND COMMISSIONING

3.13	SOFTWARE FOR DEVICE CONFIGURATION

3.14	DOCUMENTATION

3.15	MEETINGS AND REPORTING

3.16	CLEANUP

3.17	OPERATOR TRAINING

3.18	ASSET DATA

4	SITE SPECIFIC REQUIREMENTS

4.1	CWTP SHUTTLE DRIVE, BROMLEY

4.2	POTABLE WATER SITES

4.3	PUMP STATIONS

5	GENERAL INSTALLATION & TECHNICAL REQUIREMENTS

5.1	GENERAL

5.2	RATINGS

5.3	STANDARDS AND REGULATIONS

5.4	CABLES

5.5	CABLE SUPPORT AND PROTECTION SYSTEMS

5.6	CABLE JOINTING

5.7	CABLE TERMINATIONS

5.8	UNDERGROUND CABLING

5.9	CABLE MARKING

5.10	LUMINAIRES

5.11	GENERAL PURPOSE OUTLETS

5.12	VARIABLE SPEED OR FREQUENCY DRIVES (VSD)

5.13	SWITCHBOARDS & MCCS

5.14	VALVE ACTUATORS

5.15	MOTORS

6	SWITCHBOARDS AND CONTROL PANELS

6.1	GENERAL

6.2	TECHNICAL SPECIFICATION

6.3	MOTOR STARTERS

6.4	VENTILATION AND AIR CONDITIONING

6.5	FACTORY TESTING

6.6	DELIVERY

6.7	APPROVALS

6.8	DOCUMENTATION

7	INSTRUMENTATION

7.1	PRELIMINARY

7.2	GENERAL

7.3	DESIGN AND SELECTION

7.4	MOUNTING

7.5	STANDARDS

7.6	EARTHING

7.7	CALIBRATION CERTIFICATES

7.8	DOCUMENTATION

8	AUTOMATION

8.1	GLOSSARY OF TERMS

8.2	GENERAL

8.3	TAG NAMES AND CONVENTION

8.4	PROGRAMMABLE LOGIC CONTROLLER (PLC)

8.5	DOCUMENTATION

9	COMMUNICATIONS

9.1	GENERAL

9.2	PLC TO CONTROL DEVICES

9.3	PLC TO SCADA, PLC AND HMI

9.4	SCADA TO SCADA

9.5	CCC INTRANET TO SITE CONTROL NETWORK

9.6	ETHERNET COMMUNICATION

9.7	COMMUNICATION CABLING

9.8	ENCLOSURES

9.9	DOCUMENTATION

10	SCADA

10.1	GENERAL

10.2	REMOTE SUPPORT

10.3	HARDWARE

10.4	SOFTWARE

10.5	DOCUMENTATION

11	GENERATOR AND DIESEL ENGINES

11.1	GENERAL

11.2	CONTROLS AND CHANGEOVER

11.3	COOLING SYSTEM

11.4	FUEL SYSTEM

11.5	NOISE LEVELS

11.6	DOCUMENTATION

# INTRODUCTION

This specification is intended to be used by CCC staff, External Consultants and Contractors to:

- Describe and specify the work required to be carried out for any electrical project to be implemented on Christchurch Water and Waste (CWW) sites including treatment plants and pump stations.

- Describe in detail the acceptable levels of electrical design and installation.

- Provide a base document for periodic reviews which will be updated as requirements change and as relevant information needs to be added.

It has been compiled from many electrical specifications used within the City Council but does not propose to contain all information that is relevant to electrical work carried out for CWW.

Where this document is used for multi-disciplined projects it may need to be accompanied by NZ 3910 contract documents preceding the specification and by other project scope and technical requirements applicable to the particular project. The author of the document will decide on the use of a contract document front end.

Where this document is used for small projects the contract document front end may only require the CCC conditions attached to a works order.

HOW TO USE THIS DOCUMENT.

All Electrical projects carried out for CWW sites shall comply with these design and installation standards. Where these standards are inappropriate for a particular project or part of a project

The author shall seek Council approval for any deviations.

The term “Author” is used in this document to refer to the person preparing a scope of work for a Contractor on any CWW site. Items in Yellow are explanatory notes for the author.

The Scope of works Section is intended to be used to describe the specific project and any additions or modifications to the clauses used in the General Section and the specific Technical Sections. The General or Technical Sections are not to be added to or have clauses deleted when used for a particular project. In clause 1.9 of the Scope of Works all modifications to the General or Technical Section clauses shall be listed under the particular clause number of that Technical Section.

This document is divided into the following sections;

SECTION 1 – Scope of Work

This section will detail the scope of works for a specific project and detail any deviations from the generic specification. This section must be altered to suit each project.

Sections 2 onwards shall be updated and revised from time to time by CCC but shall otherwise remain unchanged. These shall apply to all electrical projects for CWW at treatment plants and pump stations.

SECTION 2 – Preferred Suppliers & Equipment

Identifies the Contractors and suppliers who are presently approved or preferred. This list is subject to frequent revision and may be altered depending on the specific requirements of your project with CCC approval.

SECTION 3 – General Site and Project Requirements

This section will contain all of the general clauses related to electrical work that are not detailed in the contract document section.

SECTION 4 – Site Specific Requirements

This section identifies differing requirements applicable to particular sites, such as the Pages Road Wastewater Treatment Plant (CCWwTP) and typical requirements as these differ, such as between water and waste water sites.

SECTION 5 – General Installation & Technical Requirements

This section details the requirements for the installation of electrical switchgear, cables, cable supports and service devices installed.

SECTION 6 – Switchboards and Control Panels

This section details the requirements for the supply of electrical switchgear to be installed.

SECTION 7 – Instrumentation

This section details the requirements for the supply and installation of instrumentation for the measurement and transmission of plant data to the automation and SCADA systems.

SECTION 8 – Automation

This section details the requirements for the selection, installation, programming and testing of equipment related to automation.

SECTION 9 – Communications

This sections details the requirements for Ethernet and other communications protocols to be used.

SECTION 10 – SCADA

This section details the requirements for the selection, installation, programming, display and testing of equipment related to the gathering and manipulation of plant data related to the operation of the plant. Supporting information can be found within the Councils SCADA User requirements Specification (URS) TRIM ref. 09/309407.

SECTION 11 – Generator and Diesel Engines

This section identifies some of the requirements for diesel generators, additional detailed technical specifications will be required for any generator installations.

# SCOPE OF WORK

## PRELIMINARY

Refer to the enclosing Contract Conditions or Purchase Order terms and conditions as applicable which shall apply to this Pro-forma CWW Generic Electrical Specification.

## PROJECT NAME

The name of this project is:

Inset the Project name and Contract Number

## PROJECT LOCATION

This project will be carried out at:

Describe the location of the project and specific area of the plant that the project will affect directly and indirectly.

## KEY PERSONNEL

The following personnel are associated with this project:

### CCC

- Operations Manager

- Plant Manager

- Plant Operator

- Network Operator

- Capital Program Group Electrical Engineer

- SCADA Engineer

### Project team

- Project Manager

- Site Engineer

### Others

Note that roles and responsibilities listed in the remainder of the document are generic, the CCC asset owners and technical lead roles must be confirmed for each project on the basis of the project requirements. List key project personnel with contact phone numbers

## PROJECT BACKGROUND AND REQUIRED OUTCOMES

Write a précis of the project history and required outcome to give the contractor an idea why the project is being carried out

## PROJECT PROGRAMME

Refer to a specific program of works or list key dates here or refer to the Contract Documents Synopsis

## SPECIFIC HEALTH AND SAFETY REQUIREMENTS

Record any specific project Health and Safety requirements or know hazards other than those cited in Sections.

## OPERATIONAL RESPONSE

Identify any specific operational support requirements

## SPECIFIC PROJECT TECHNICAL REQUIREMENTS

Insert relevant clause numbers associated with technical clauses that have specific specifications to the generic clause.

## DELIVERY OF EQUIPMENT

Delivery, offloading and removal of any equipment is the responsibility of the contractor.

For Bromley access to site and specific area with in the Treatment Plant shall be coordinated with the Shift Controller.

Add any other specific details to the contract specification here.

## DOCUMENTATION

Where applicable identify any additional existing documentation that must be updated. E.g.

- Piping (Process) Instrumentation Diagram(s) (P&ID)

- CCC SCADA Operations & Engineering Manuals

- CCC IP Radio Network Schedule TRIM:09/319895

- CCC IP Network Port Schedules TRIM:09/319895

- Electrical drawings

- CCC SCADA Operations Manual

- CCC SCADA Engineering Manual

- Water, Wastewater or Stormwater Supply Network Schematics

- CCC SCADA Reports

Include typical examples of documentation or drawings where needed to clarify preferred CWW solutions.

## SCOPE OF WORK

The scope includes all work necessary to provide a complete working installation as indicated in this Pro-forma CWW Generic Electrical Specification and referenced documentation.

List the major items of work to be carried out with references to drawings and supply and installation of major items.

## CONTRACTORS DESIGN RESPONSIBILITIES

Identify the contractor’s design responsibilities.

## DETAILED SCOPE OF WORK

Add as required. Additional elements may include:

- Switchboard ratings, Single Line Drawings and Schedules as appropriate

- Process and functional requirements

- Interface points

- Any other information necessary to adequately describe the scope

# PREFERRED SUPPLIERS & EQUIPMENT

Alter as CWW standards are revised and as appropriate to suit the project.

## PRELIMINARY

This section identifies preferred suppliers and preferred equipment. Alternatives may only be employed with the prior written specific approval of the CCC Water and Waste Asset Management Electrical Team Leader.

## ELECTRICAL CONTRACTORS

The following contractors are preferred for electrical installations construction.

- Melray

- Millennium Electrical

- O’Donnell Griffin

- Swarm Intelligence

- Fitzwilliam Electrical

- Aotea Electrical

## SUPPLIERS

The following contractors are approved for construction and supply of electrical switchgear (as defined in the electrical switchgear section).

- TLJ Switchgear

- IC Switchgear

- AML Switchgear

- Vynco

- Bremca Industries

- Rickland

## SYSTEM INTEGRATORS

The following contractors are approved for work involving modification to the CWW SCADA System HMI, RTUs, PLCs and Local HMI panels.

- Industrial Controls Christchurch

- Millenium Electrical

- Control Web

- Bremca Industries

- Swarm Intelligence

- Industry Software

- Yokogawa New Zealand Limited

## EQUIPMENT

The following equipment is preferred but alternatives may be offered for approval at time of tender. These are grouped for ease of location only.

### SCADA System

- Archestra

### PLCs and RTUs

- Yokogawa				Stardom FCN,FCR & FCJ

- Bromley, CCWwTP Site	  	Schneider Quantum & M340

- Iota					"Onebox" Low Pressure Sewer System controller

### UPS

- UPS equipment 			Emerson Network Power (Christchurch)

### Field HMI Panels

- Magellis programmed with the current CCC version of Vijeo Citect SCADA package

### Pressure Transmitter

- Yokogawa , ABB or Siemens

### Flow Meter

- Khrone 				(purchased through Streat Control (2002) Ltd)

- ABB 				( purchased through ABB NZ Ltd)

- Yokogawa 				(purchased through Yokogawa NZ Ltd)

- Siemens 				(purchased through Siemens (N.Z.) Ltd.

- Endress & Hauser 			(purchased through EMC Industrial Group Ltd)

### Cable & core labelling

- Raychem Shrinkmark system

- Legrand Memocab cable marking system

- Graphoplast spark crimp on pins

### Miscellaneous

- Panel Sounder			Askari

- Battery				Century Commander, Century Yuasa

- Wireless modem 			Available on request

### Switchgear

- Main Incomer >800A		ABB, Schneider / Telemecanique ACB

- Main Incomer			Schneider / Telemecanique or Merlin Gerin NSX						Intelligent MCCB up to including 630

- MCCB				Schneider / Telemecanique, ABB or Terasaki

- Power Monitors			Merlin Gerin Power Logic series

- Isolator				GE, K&N, Stromberg, Merlin Gerin

- Fuse Sw.				General Electric(GE) Fulos-Lockable or Stromberg

- RCD 				Merlin Gerin or GE

- MCBs				Merlin Gerin or GE

- Phase fail unit			Crouzet FWA-400, Telemecanique Zielo

- 32A Fuse holders			NZI

- Terminals				Schneider AB1 –VV435U 4mm², ABB  Weidmuller 					Z series

- Fuse Terminals			Schneider AB1-FU10135U Weidmuller

- SCADA Analogue Terminals	Link blade disconnect type 4.0mm² Electrade CTK 					4U,ABB, Weidmuller or Schneider

- 230v Skt internal			PDL 692

- 1/3 Ph External Equipment		PDL 56 Series

- Lamps				Allen Bradley 800A Series 22 mm dia, Telemecanique

- Bulbs				Allen Bradley LED

- Pushbuttons			Allen Bradley 800A Series. 22 mm dia, Telemecanique

- Overloads				Telemecanique K or D type to suit.

- Reset Solenoid			Telemecanique LA-D03 230V AC

- Control Relays			Finder 60.12 and base 230v with neon and mech activation

- SCADA Control Relays		Finder 56.32 and base 24v dc with neon and mech					activation (12v where required for existing						equipment)

- Contactors				Schneider / Telemecanique LC1 – Bypass

- Timer				Schneider / Telemecanique LA2-DT2, Crouzet

- MCB Chassis			Merlin Gerin or Vynkier

- Ammeters/Voltmeters		Crompton 96mm²

- Voltmeter sw.			Kraus & Naimer CA10-623 E

- Auto Off Man switch			Kraus & Naimer

- Current Transformer		Electrade

- Hour Meter				Omron H7EN-front reset disabled

- Analogue Ammeters		Electrade 4-20mA 96 x 96 mm, Carell and Carell

- DC Power Supplies			12/24-10/20 amp- Enatel RW series, Phaseo

- Local Control and Display		Telemecanique LCCD

### Motor Starters and Drives

- DOL Starters			Te SyS ‘T’ or ‘U’

- Display device			Telemecanique LCCD

- Soft Starters			Aucom EMX3

- Variable Speed Drives		ABB or Schneider Electric (Telemecanique)

### General

- Externally mounted 
sockets/switches			PDL 56 Orange Series

- External Cabinets

  - 316 Stainless steel

  - Polycarbonate

  - Glass Reinforced Polyester (UV inhibited)

  - Aluminium Painted

- Cable Support			Aluminium, stainless steel, Fibreglass (UV inhibited)

- Fixings and fittings			316 Stainless Steel

- Valve actuators			Rotork (with Modbus Communications Card)

## VENDOR PACKAGES

In specific cases it may be appropriate to identify a “vendor package” where the vendor’s standard software and control system hardware does not comply with CCC requirements with regard to PLC/RTU, HMI, function blocks and tag naming scheme.

Vendor packages will generally only be acceptable where the supplier has a standard offering with pre-existing drawings, documentation and displays that will be essentially unchanged for the project and can make a compelling case in terms of the reliability, maintenance and functionality.

Vendor packages must be identified in the tender, with supporting information and explicitly identifying the proposed areas of non-compliance. Vendor packages must be specifically accepted in writing by CCC.

# GENERAL SITE AND PROJECT REQUIREMENTS

## PRELIMINARY

The following parts of this specification cover the General requirements that apply to any electrical contract carried out for CWW sites. Any deviations or exception from this shall be identified in Section 1.

## SITE INFORMATION

### Introduction

All persons performing work on CWW sites are required to undergo a site induction prior to commencing any work.

This induction process is presented by a member of the CCC staff and consists of:

- An explanation of the site Health, Safety and Environment rules

- The identification of known site hazards

- Issue of a Health & Safety Handbook

Those being orientated are required to acknowledge understanding and acceptance of the conditions detailed in this booklet for this site by completing the receipt at the back of the Health & Safety handbook prior to commencing any work on CWW sites. The receipt shall be handed to the CCC staff member undertaking the induction.

Inductions are managed through reception at the CCWwTP site on Shuttle Drive in Bromley.

### Site Rules

- All persons must sign site visitor registers on arrival at site indicating date and time.

- Non-inducted personnel must be accompanied by inducted personnel at all times.

- When leaving the site, all persons must sign out in the visitor book and record the exit time.

- Always follow instructions given by the Plant Manager and obey all safety signs around the plant.

- All workers must wear safety boots.  All visitors must wear sturdy closed shoes.  Hard hats and hi-viz vests must be used during construction/crane use activities.

- Smoking is prohibited on the CWW sites.

- Matches, lighters and other sources of ignition are not permitted in hazardous areas.

- Horse play and practical jokes will not be tolerated at any time.

- All incidents/accidents must be reported immediately to the Plant Manager and an accident form completed.

- Check with the Plant Manager prior to working on any site and complete the necessary work clearance forms.

- When riding in site vehicles personnel must be seated in proper seating.

- Personal Protective Equipment (PPE) must be used where signs and / or common sense dictate its use. Contractors must supply their own PPE.

- No drugs or firearms are permitted on site.  Personnel who are intoxicated in the opinion of CCC staff will be escorted off the site.

- Blasting explosives shall not be taken on site without the prior written approval of the Plant Manager.

- Confined Space Clearances must be available at the work site.

- No plant equipment is to be operated without the Plant Manager’s permission.

- The CWW Control Room (at CCWwTP Bromley) is to be briefed on the status of plant at the end of each work session.

- No animals are permitted on the CWW sites at any time.

- Children are only permitted on CWW sites when formally escorted by CWW or approved CCC staff.

- Site documentation is to remain on site at all times.

### Work Permits

- A “Permit for Work” is required for all work undertaken.

- A procedural description of the access and work permit system is documented in the Guidelines for entering and working in Confined Spaces, TRIM ref: 14/373123.

- All Plant, unless isolated and tagged, must be considered “Live” and may start automatically at any time.

### Work Procedures

Site access keys are available for the works duration at the Network Operator at the CCWwTP Bromley. Notify the Network Operator each time entering and vacating the site.  Do not leave the door to swing freely as this gives multiple security alarms.

All isolation and operation of pumps and generators is to be co-coordinated through the Network Operator. Pumps can be started automatically at any time. Wear ear muffs if pumps or diesel motor are running in the room.

Once the site is handed over, if working alone at one location, contact the Shift Controller every two hours to confirm all is okay. Be contactable by the Network Operator e.g. by cell phone.

### Hot Work Permits

Hot Work Permits are required for any work or activity that has the potential to create an ignition source.  These activities include grinding, welding, cutting and the use of any power tools.

### Water Contamination

Contractors shall identify the specific cross contamination risks from waste water to water supplies that may arise from tools, equipment or work practices. Contractors shall adopt measures applicable to their specific work methodology to eliminate the possibility of cross contamination.

### Environmental Issues

CWW sites operate alongside bays and rivers used extensively for recreation by the public.  For this reason CCC is very concerned about the impact of the operations of the plant on the environment.

To minimise the risk of environmental damage you are requested to:

- Under no circumstances should the Plant or Network operation be compromised, (i.e. bypass or overflow) due to your activities.  You will be held accountable for any such breaches of Consents.

- Do not compromise the process or collection systems, plant equipment, or structure that would cause a reduction in the quality of the effluent (bypass) or contaminate the immediate area (overflow or spill).

- Do not allow any sewage to be drawn into any storm water or water supply system.

- No tanks or vessels are to be drained without the expressed permission of the Plant Manager.

- All plants and landscaped areas must be protected when carrying out work.

- Do not discharge pollutants on site.

- Work area is to be left clean and free of rubbish.

- Waste is to be disposed of in the bins provided or removed from the work site.

- Hazardous waste or pollutants (including oils) are to be removed from site using appropriate containers and/or vehicles and disposed of in accordance with local / national regulations.

- Do not light any fires or burn rubbish on any site.

- All vehicle movements must be on designated roadways only.

- Inform the Plant Manager if you witness an occupational health and safety or environmental incident; or suspect that one may occur.

- Immediately contain any spill.  Notify the Plant Manager as soon as you see or have any spill.

- Only authorised personnel holding a confined spaces certification may enter confined spaces.

### Hazardous Areas

Some CWW sites have areas classified as hazardous. Warning signs are generally posted around the areas affected however this is site specific. Familiarise yourself with the issues applicable at the specific site and use appropriate safety measures.

All work in hazardous areas must be in accordance with the requirements of the New Zealand Standard for Hazardous Areas.

Mobile phones, torches and cameras are not intrinsically safe (unless specifically certified) and shall not be used in such areas unless they are intrinsically safe.

All work to be carried out in confined spaces or hazardous areas will be done using a calibrated portable gas detector.  If the alarms activate, report the incident to the Plant Manager

No Hot Work is allowed on pipelines that contain flammable gas until they have been purged and proved safe AND a ‘Hot Work Permit’ has been issued.

### Chemicals

A range of chemicals are stored at, and are present at CWW sites.  Some of these chemicals are corrosive so care should be taken when working with these chemicals or working in close proximity to the storage areas and/or associated pipework.  Ensure you are familiar with the relevant material safety datasheets if you are working with any chemicals.

Other hazardous chemicals can occur in wastewater, identify and manage the potential risks at the work site.

### Biological Hazards

To prevent disease associated with viruses and bacteria that may be found in the wastewater systems, strict hygiene practices shall be adhered to.  These include:

- Washing of hands prior to eating

- Laundering of contaminated work clothes through a laundry and showering prior to leaving the site if necessary.

- Change clothes immediately if they have been splashed with effluent.

- Eating in designated areas only (ie lunch rooms).

- Ensure that qualified first aiders attend to any cut or abrasion.  This is particularly important!

There have been confirmed cases of cellulitis at Wastewater Treatment Plants.

- Ensure that ALL injuries, including minor cuts and abrasions are reported to the Plant Manager.

- Please advise the person conducting this induction if you have any cuts and/or abrasions.  These must be attended to before performing the work on sites handling wastewater.

- Please advise the Plant Manager if you develop a rash whilst working at a CWW site.

It is STRONGLY RECOMMENDED that you are immunised for Hepatitis A and B, Polio, Typhoid and have had a recent (last five years) tetanus vaccination prior to the commencement of work on any CWW site containing wastewater, biosolids, or sludges.

### Environmental Conditions

In the absence of other specific information specification, design and supply of equipment for installation at the plant shall allow for the following environmental conditions at the site without any equipment exceeding manufacturers recommended environmental specifications.

Temperature:

- Highest 			35ºC

- Lowest				-4ºC

- Humidity 			67-90%

## HEALTH AND SAFETY

### General

The Contractor shall take all necessary steps to ensure that the obligations placed on principal employers and owners pursuant with the provisions of the Health & Safety in Employment Act 1992, are at all times complied with.  The Contractor shall comply with all enactment’s, regulations and working rules relating to the safety, and welfare of everyone associated with this contract, as defined by Local Bodies, Christchurch City Council’s Health & Safety policy, any other legislation applicable to the work.

Another specific requirement is compliance with the CCC 'Guidelines for Entering and Working in Confined Spaces'.  An associated booklet is available from the CCC, and should be provided to all applicable staff.

Personnel involved with working in confined spaces and at above normal heights shall only do so with a suitable qualification. Evidence of this qualification may be asked for by the Engineer.

As part of the CCC Health & Safety requirements all contractors on site shall inform the Network Operator each time he arrives or departs the site. If a contractor is on site alone he must check in with the Network Operator every 2 hours. As part of this contract the contractor will supply a signed Health and Safety Policy as outlined in the contract documentation.

### Hazard Identification and Control

All persons performing work at this site shall advise on-duty operators of any new hazards that are identified during the course of or resulting from their activities.  Appropriate risk control mechanisms, with respect to these new hazards, must be put in place to minimise, isolate or eliminate such hazards.

To ensure good health and safety outcomes the contractor must ensure that his employees under his authority take measures to safeguard their safety.

Loose clothing and long hair must be restrained to prevent it being caught in moving or rotating plant.

All contractors are responsible for keeping their work area in a tidy, orderly and safe condition.  All surplus material and rubbish must be tidied from the work site upon completing work.  Failure to keep work areas tidy may lead to expulsion from the site and/or recovery of any costs incurred by CCC in cleaning up work areas.

The Contractor is to update the site hazard board and notify the Plant Manager of any hazards.

Common hazards at CWW sites include:

- Confined spaces

- Flammable gas

- Chemicals

- Biological Hazards associated with wastewater

- Rotating and moving mechanical plant

- Manual handling of heavy components

- Slips, Trips and Falls

- Open floor ducts and trenches.

- Floor mounted objects and pipes

- Elevated work areas

- Fumes

- Electricity – low, medium and high voltage

- Rockfall

### Fall Protection

Whenever work is performed from an elevated position or location in excess of three metres above the ground, fall protection is required.  When work is accessed by the use of a ladder, the ladder shall be tied off at the top and securely footed on a level surface.  When work is performed from a ladder appropriate safety measures must be taken.

### Scaffolding

Scaffolding of a height greater than three metres must be erected by certified scaffolders or other certified persons (eg riggers).  Scaffolding over three metres in height require a guardrail, midrail and toe-boards.  Mobile scaffolds must have the wheels locked when people are working from it.  Do not ride on mobile scaffolds under any circumstances.

### Forklift and Crane Use

Only licensed operators may operate a forklift or crane on any Christchurch City Council site.  Carrying of passengers on a forklift or crane is prohibited unless used with a certified personnel cage and according to an approved procedure.

Use of forklifts and cranes on the site must be conditional upon compliance with Codes of Practices – “Training operators and instructors of powered industrial lift trucks” and “Cranes and lifting appliances”

### Excavations

Wherever possible, personnel are not to work in excavated trenches or holes.  Where it is necessary to work in such spaces, a permit to work – excavations is to be obtained.  These permits can be obtained from the on-duty Plant Manager.

### Safety Equipment

The contractor shall supply the following where necessary:

- Hi Viz Jackets

- Hard Hats

- Safety Shoes

- Harnesses

- Eye wear

- Ear Muffs

- Any other specialised safety equipment

The Christchurch City Council is not responsible for supplying any safety equipment to the contractor.

### Fit for Work

All persons performing work at the site must be “fit for work” they are undertaking.  This is to ensure that people are not exposed to risk from themselves or others in the course of their work.  Fitness for work can be affected by:

- Physical problems

- Emotional stress

- Use of alcohol or drugs

Contractors whose employees are not fit for work will be asked to leave the site.  The terms of the Fit for Work policy will apply to those people whose judgement is impaired at work.

## OPERATIONAL RESPONSE

The Contractor shall provide a 24 hour number for any site at which work is being carried out. This shall be notified to the Network Operator and recorded on site attached to the equipment being altered or on the site board as appropriate.

## GENERAL STANDARDS

### Standard Designs

CWW best design standards are continuously evolving. Request a drawing set for the current best practice for a related site type from the Capital Program Group Electrical Engineer and SCADA Engineer before undertaking a design, designs shall follow these details as appropriate for the project. Details of any differences shall be reviewed prior to tender or construction design issue.

### Workmanship

All work carried out under this contract shall be carried out;

- By suitably qualified persons skilled in the installation of this type of work.

- Under the supervision of a suitably qualified supervisor.

- In accordance with all relevant standards and codes of practice.

- In a neat and professional manner to the satisfaction of the Engineer.

- Using new and high quality materials.

- Under a work permit issued by the Shift Engineer or Plant Manager.

- In accordance with the relevant Technical Specification.

### Materials

Any product or materials supplied for this project shall be supplied to comply with the following;

- Be new or used and approved by the Engineer

- Be the latest version of the device

- Be supplied with appropriate software

- Be suitable for the intended use

- Have a proven track record in similar installations

- Be compatible with other associated equipment

- Be supported by local suppliers or agents

- Be designed to operate in the environment it is to be installed in

- Be suitable for installation in to areas that are accessible for maintenance

- Have the manufacturers label attached

- Where the material or device is to be hidden from view and is a motor or machine and appropriate name plate duplicate shall be supplied.

- Be protected against the electrolytic corrosion due to the action of dissimilar metals.

### Alternatives and Specification

Materials supplied shall be as specified or an approved equivalent.

Where designed equipment  layouts ,types ,positions or installation differs from that shown on generic drawings the contractor shall submit alternative layouts, types and location of equipment for approval by the Engineer before any work is carried out.  Alternatives are not permitted without written approval from the Engineer.

### Protection and Security

The contractor shall be responsible for protection of the works and the surrounding buildings, machinery, gardens, lawns that could be affected by the contract works. He shall erect barriers, install covers and erect signage where necessary to minimise the risks to the surrounding areas, plant staff and contractors.

Where damage does occur as a direct consequence of contractor negligence he shall rectify the damage and incur all cost in the rectification.

The contractor shall take all reasonable steps to insure the contract works do not infringe on the day to day running of the plant, create excessive noise, dust or odours.

For the duration of the contract works the Contractor shall provide locks and keys for equipment included in the contract works, supplying keys to nominated CCC staff if access is required during the works. At the completion of contract works all locks are to be changed to meet the CCC standard locking standard.

### Guarantees

All Contract deliverables, except lamps and tubes, shall be provided with a twelve-month guarantee, from the date of practical completion. Lamps and tubes shall be guaranteed for a period of three months.

During the guarantee period return any defective equipment supplied by others to the source for repair or replacement at the Contractor’s expense.

Be available to attend a callout to a station defect within 4 hours of being requested to do so within a normal working day. If a callout is required outside working hours, be onsite within 6 hours of being requested to do so.

### Warranties and Licences

It is the contractor’s responsibility to:

- Provide all warranties in writing at hand over on all hardware supplied. This needs to detail all components, serial numbers, where purchased, date of purchase and length of warranty.

- Provide license certificates and documentation on all software supplied.

- Minimum warranty on all hardware should be (12 months) from (issue of handover certificate)

### Coordination

The contractor shall be responsible for the coordination of the contract work with other contract work, existing plant operation and other plant equipment by:

- Coordination with other contractors to ensure that on site excavations, crane usage, temporary power supplies ,disruptions to plant operations  are not duplicated by different contracts.

- Ensuring that new plant is installed in locations that do not inhibit it’s and existing plant maintenance and operation.

- Informing the Engineer of any discrepancy existing between the drawings, specification and any site feature that may inhibit the correct installation or operation of any new or existing plant.

- Ensuring that the Plant Manager is fully informed of any contract function that will affect the normal operation of the plant process.

## STANDARDS AND REGULATIONS

The installation and all materials used shall comply with relevant statutory regulations, manufacturer recommendations and the following:

- Electricity Act 1992

- Electricity (Safety) Regulations 2010

- AS/NZS 3000:2007 Wiring Rules

- AS/NZS 60069.14 Hazardous areas

- Electrical Codes of Practice ECP34 to ECP 60

- AS/NZS 3820:2009 Essential Safety for low voltage equipment

- NZS 3019:2004 Electrical Installations - In service testing

- All applicable Network Company connection standards

The contractor shall supply ‘Producer Statements ‘ for all specially manufactured equipment and shall supply an Electrical Certificate of Compliance for all electrical work.

## QUALITY ASSURANCE

The contractor shall be responsible for:

- Checking that the works are installed and tested in accordance with the specification and relevant codes and standards.

- Ensuring that all workmanship and material quality is of the highest standard.

- Supplying a basic quality plan at time of tender and a detailed plan 10 days after award of tender or as advised by the Engineers. The plan should outline the method of ensuring that quality of materials and workmanship is monitored at all phases of the project.

- Maintaining a written record of the plan and record all compliance checks.

## SPECIFICATIONS AND DRAWINGS

The position of equipment and the layout of equipment inside cabinets and switchboards, as shown on the drawings, are to be considered approximate only and there is no warranty expressed or implied that each and every detail and item to be included is shown. Any reference to dimensions and distances shall be confirmed on site.  The drawings and specifications are intended to be mutually self-explanatory and complete but all work called for in one, even if not the other shall be fully executed.  Should any contradiction appear to exist between drawings, or between drawings and specifications etc, the Contractor shall notify the Engineer of any such discrepancy and shall not execute any of the work concerned until the Engineer’s decision is given in writing

## IDENTIFICATION AND LABELLING

Labelling and identification of equipment shall be in accordance with the treatment plant master Tagging system (TRIM File Ref: ELEC06/6074 - CWW Tagging Convention).  A copy is attached in Appendix A.

All equipment shall have a label identifying:

- Description of equipment

- Its “Tagname”

Labels shall be white/black/white except danger and warning labels which must be red/white/red traffolyte, with 5mm and 3mm lettering for switchboards and stamped stainless steel with 5mm lettering for field devices.  Labels shall be screwed to the device or attached by stainless steel wire or chain so that they can be removed and re-used if the equipment is replaced.. If it is impractical to fix a label to a piece of equipment then the label should be fixed to a surface as close to the equipment as possible.

All cables and individual cores shall be labelled at both ends.

All cores shall be numbered with a unique reference within the switchboard or grouping of equipment provided in this Contract. Core numbering shall change across devices but shall generally not change across terminals, with the exception of PLC/RTU terminals. PLC/RTU I/O labels shall identify type, rack, slot and point at the first terminal, the label out to the field from the first terminal shall change to suit the cabinet labelling scheme.

All components inside cabinets shall be labelled as per the name shown on the label schedule drawings.

All cabinet doors shall be labelled with engraved labels describing the function of the cell. Labels shall be white with black lettering.  All warning or danger labels shall be red with white lettering.

## TECHNICAL

### Earthing and Bonding

Earthing shall be installed in compliance with the Electricity Regulations 1997, associated Electrical Codes of Practice (particularly NZECP 35), AS/NZS 3000, and Orion Electricity Network Design Standards (particularly NW70.59.01).

A separate instrument earth bar shall be used for termination of instrument earth cables and shields.

Earth bars and wires, etc, shall be of adequate size, thickness and spacing to provide a robust, efficient and electrically sound installation.

All cable sheaths and earthing conductors shall be directly connected to dedicated earth bars or the associated earth electrode. All connections shall be made using appropriate welding methods or compression type lugs (conductor) and bolted connections to the bars.

### Cooling and Ventilation

All rooms or interior spaces housing electrical assemblies and equipment shall have sufficient ventilation and/or cooling to limit the maximum temperature (inside the room or space) to 40C. Should forced ventilation be required, appropriate filters shall be used to limit dust or ingress of other substances (e.g. hydrogen sulphide).

Care shall be taken when installing equipment in locations exposed to direct and prolonged sunlight to ensure that the equipment has been designed (UV stabilised plastics, adequate ventilation, etc) for that type of environment.

Equipment shall not be installed in polluted atmospheres unless special precautions have been taken in the design of the equipment and it is suitable for installation in the particular environment.

### Seismic Requirements

All fixed plant, equipment, appliances and the installation thereof shall comply with the seismic design requirements of NZS 4219:2009 and any additional Local Authority requirements.

Fixings must be able to withstand normal operating loads plus seismic forces at 1.0G in a horizontal direction acting through the centre of gravity of the item.

The Contractor shall design and install switchboard and plant  securing systems for all switchgear, drives , filters and other electrical equipment to NZS 4219 :1983 Seismic Resistance for Engineering Systems in Buildings’ Loadings shall be calculated in accordance with NZS 4203:1992 section 4.12 Application Risk = 1.3.  An Engineers design certificate shall be produced as part of the documentation for inclusion within the Operation and Maintenance manual.

The contractor shall confirm locations of seismic joints and allow flexible connections across them. Rigid cable supports shall not be bridged across seismic joints.

### Environmental

CWW sites are commonly exposed to corrosive atmospheres. For waste water treatment sites this typically includes the presence of H2S, for waste water sites all exposed copper conductors shall have a complete tinned finish and all circuit boards shall have conformal coating to IEC 60721-3-3 3C3.

### Manufacturer’s Instructions

Equipment shall be installed, configured, tested and commissioned in accordance with manufacturer’s instructions and recommended practices. Configuration details shall be recorded and submitted according to manufacturer’s configuration sheets where available, these shall include all user configurable adjustments.

## POWER SUPPLY

Allow to provide a power supply to site. Provide load calculations and connection request to the Line Company. Provide mains cables, metering and comply with all power company requirements for the connection of supply. Arrange first power with the CCC nominated Energy Retailer.

Provide any power conditioning equipment required to meet power factor and harmonic standards required by the line company.

Costs associated with design and alterations within the line company network and on the line company side of the point of connection will be paid by CCC.

## TESTING AND COMMISSIONING

### General

Testing is to be carried out and documented by the Contractor prior to Commissioning.

A Commissioning Plan shall be submitted to the Engineer for approval 2 weeks before the start of commissioning. This shall be accompanied by a Preliminary Operations & Maintenance Manual containing data sheets for all items of plant to be commissioned.

Commissioning is carried out by the Contractor and his Sub Contractors.

The correct operation of the plant shall be demonstrated to the Engineer at the completion of Commissioning.

Clauses for related to testing and commissioning of specialist equipment are contained in the relevant Technical Specification.

The contractor is to supply all equipment necessary to test and commission the plant.

Testing and Commissioning shall be carried out using pre-approved written Testing and Commissioning Procedures Sheets.

All results shall be recorded on the Testing and Commissioning Procedures sheets.

Testing and Commissioning shall be carried out in accordance with the Plant Manager’s written authority where the plant being tested or commissioned is part of the ‘live’ plant process.

### Testing

Testing is carried out to ensure that basic work has been completed in a specific area before power is applied to a device.

Tests shall include, but are not limited to:

- General testing as described in AS/NZS 3000

- Continuity of connection between devices

- Correct earthing

- Correct voltage applied

- Device location allows adequate access for maintenance

- Correct sizing of cables and power supply

- Correct environmental protection

- Device is as specified

- Installation is to manufacturer’s recommendations

- Hazardous area classification compliance is correct

- Labelling and device tagging is as per the CWW requirements

- Drawings are marked up to ‘As Built’ to include all information relating to the actual installation.

- Equipment is installed in a safe, neat and function manner.

- Device is setup correctly and any automatic functions are disabled.

- Rotation of motors is correct. This test to be carried out in manual.

- Transducer calibration and set up.

- Primary instrument testing (switch etc)

- Analogue and digital and communications I/O testing

- PLC I/O set up and calibration sheet marked up with test and calibration results that include confirmation of indication in both the PLC code using the programming tool and the SCADA alarm and mimic displays

### Commissioning

Commissioning is carried out to check that the plant performs all of its designed functionality. It shall test automatic functions, manual overrides, emergency functions, compatibility with other plant functions and equipment and enable operation of the plant so that minor adjustments and settings can be made to ensure reliable operation .All adjustments and settings shall be recorded and information handed to the Engineer. Commissioning shall;

- Be carried out by skilled and qualified persons

- Be coordinated to ensure correct functionality of complete process and interfacing with other plant functions

- Demonstrate to the Engineer and CWW staff the complete automatic and manual operation of the plant and process.

Testing and Commissioning shall be carried out by the Contractor prior to Practical Completion. The Engineer shall demonstrate to the Operations Manager’s representative that the Works efficiently meet the specified performances, and have been successfully tested and commissioned as a complete and integrated installation, under operating conditions. The Contractor shall allow 10hrs to assist the Engineer.

If a second inspection of the work is required by the Engineer because the work is not completed in accordance with the specifications then a sum of $200 may be deducted from the Contract price.  Each subsequent inspection required until the work has been completed to the extent that a Certificate of Practical Completion can be issued shall result in an additional $200 being deducted from the Contract price.

### As Built Documentation

The contractor shall keep a clean set of contract drawings specifically to record any changes to the drawings due to variations, changes in position of equipment, changes in design and any other event which cause the drawing to change.

This set of ‘As Built’ drawings shall be presented to the originator of the drawings after successful commissioning of the plant for updating prior to providing them for insertion into the Operation and Maintenance Manuals.

Where the contractor has carried out the design he shall present drawings in the ‘AUTOCAD’ 2010 native format.

## SOFTWARE FOR DEVICE CONFIGURATION

Unless specifically agreed otherwise, for all devices able to be configured the Contractor shall supply the software configuration tools and the device configuration settings in a format that is able to be used and modified by CCC. This shall include the right to use common configuration settings and programs across other CCC devices and assets.

Where configuration software is not freely available and not included as a deliverable in this Contract the software required shall be adequately described to allow CCC to independently purchase if they wish.

Configuration files shall be supplied without passwords and both in native application form suitable for editing and loading onto the device and as a pdf document.

## DOCUMENTATION

Original site documentation is to remain on site at all times. Once new documents have been approved the site documentation is to be updated with the new documentation set. Redundant site documentation is to be removed once the updated set has been approved.

Documentation shall include Operation and Maintenance Manual in the City Council City Water and Waste department generic format. This template is for a complete multidiscipline project and it is not expected that the contractor complete a manual such as this but it shall be used as a template for the electrical manual.

Documentation shall adhere to the following requirements:-

- Two printed copies and one CDROM copy of operations manuals describing:

  - Start-up and shutdown of systems

  - Normal operational procedures

  - Fault finding procedures

  - Maintenance activities

  - Spares and consumable requirements

  - Manufacturers manuals and data sheets for all items

  - Drawings

  - A text searchable PDF copy of all documents and drawings

- A CDROM containing all software tools and configuration files including a description on how these are to be used.

- All supporting documents must be supplied in formats acceptable to CCC at the time of undertaking such work. Acceptable formats include:

  - Word DOCX

  - AutoCAD DWG

  - Excel XLSX

- For all supplied hardware and software, manufacturer manuals, installation and support media including CDROMs or floppy disks must be provided to CCC.

- Provide warranty applications (Manufacturer Statements) as appropriate with a copy of all documentation at project completion.

## MEETINGS AND REPORTING

The Contractor shall attend meetings and provide reports as required by the engineer. These shall be monthly during general construction periods and more frequent as may be required during commissioning. Generally the contractor will be expected to give written progress reports to the Engineer covering all aspects of the project including;

- Progress to date in comparison to contract program

- Any problems with procurement of materials

- Health and Safety issues

- Variations

- Issues effecting future progress

## CLEANUP

The Contractor is responsible for ensuring that the work site is left in a tidy state, that all temporary works are disestablished and removed from the site. The new plant should be thoroughly cleaned to the satisfaction of the Engineer. The Certificate of Practical Completion will not be issued until this work has been carried out.

## OPERATOR TRAINING

The contractor is responsible for caring out any training required to Plant Manager and other selected staff .After handover the Contractor shall arrange a training session or sessions to fully explain the operation of the new plant. A training facility available in the Operations building and this can be booked by contacting reception and booking the facility.

Training should commence during commissioning with formal sessions away from the site if required.

The contractor shall arrange to have the relevant trained personnel available, provide all written materials and manuals and other materials to carry out the required level of training to enable staff to effectively operate the plant.

## ASSET DATA

The installation and removal of equipment in the plant has implications on the recorded data about that asset. It is very important that the asset data is upgraded when work is carried out at the plant.

Please contact the asset unit within the CCC to obtain the relevant documentation to record any additions/deletions or changes to assets. TRIM 14/141308 911 Asset Management - CWW - Station Asset Templates

## OWNERSHIP OF REDUNDANT EQUIPMENT

Ownership of redundant equipment remains with CCC unless explicitly stated otherwise. Allow to remove from site and deliver to a CCC nominated address. Equipment shall be properly disconnected, provided together with all ancillary parts, cleaned, but otherwise in an as-found condition.

# SITE SPECIFIC REQUIREMENTS

## CCWwTP, SHUTTLE DRIVE, BROMLEY

### Operational Staff

Where notifications are required to the Network Operator, at CCWwTP Bromley these shall be to the Shift Operator.

### Health & Safety

Refer to the CCWwTP Safety Induction Manual for additional site specific requirements.

### Hazardous Ares

This plant has areas classified as hazardous as per the “Hazardous Areas Classification Plan”. Gas zones are indicated by a yellow line on the bottom and a sign.

The site overhead cranes may only be operated by suitable trained operators.  Site staff control the use of site cranes.  CCWwTP staff trained in the use of the site cranes and will perform lifting operations where necessary.

Gas detection equipment may available for specialist jobs in hazardous areas on site.

### Site Rules

- Prior to access of plant, all persons must report to the Administration Building and sign in the visitor register provided indicating date and time.

- All visitors (including plant inducted personnel) must obtain a pass and record their name, company in the visitor register.

- Always follow instructions given by the Shift Engineer.

- Do not go outside the fence.  If access is required, advise the Maintenance Supervisor.

- Site speed limit is 10 km/h.

- Confined Space Clearances must be available at the work site.  Other permits are held in the control room and signed off at the end of the day. No extension of work beyond one day is permitted without the signed approval of the CCWwTP Engineer.

- No plant equipment is to be operated without the Shift Engineer’s permission.

- The CCWwTP Control Room is to be briefed on the status of plant at the end of each work session.

### Security

The CCWwTP site is a secure site with motorized security gates on the front entrance from Shuttle Drive and the rear entrance from Cuthberts Road.  All external and some internal doors are protected and require security cards and codes for access to the site buildings. The main reception area in the Operations Building must be visited to obtain a security visitors pass.  Initially contractors will need to be accompanied by a staff member to visit any part of the site.  Once a contract is in place and contractors are on site to carry out contract work a revised security clearance system will be used.

### Isolations

Plant isolations must only be performed by CCWwTP Shift Engineer or as nominated by the Shift Engineer and as recorded on the Permit to Work.

### Chemicals

Hazardous chemicals stored in bulk (refer to location list) and used at the CCWwTP are:

- Diesel Fuel

- Polymer

- Biogas

Other chemicals are stored in lesser quantities on site.

Hazardous chemicals that are produced during the treatment of sewerage and sludge are:

- Hydrogen Sulphide Gas (H2S)

- Ammonia Gas (NH3)

- Methane Gas (CH4)

### Environmental Conditions

The environment at the CCWwTP is particularly corrosive and all equipment to be supplied under this specification must take this into consideration when designing and building this type of equipment.

Specification, design and supply of equipment for installation at the plant shall allow for the following environmental conditions at the site without any equipment exceeding manufacturers recommended environmental specifications.

- Air Contaminants

- Hydrogen Sulphide (H2S) 	2 ppm

- Salt laden air

- Temperature

- Highest 			35ºC

- Lowest				-4ºC

- Humidity 			67-90%

### Switchgear

All bare copper bars shall be Tin coated after all drilling has been completed.

### Switchrooms

Generally switchrooms shall be positively pressurized with filtered air to minimize the corrosive effects of H2S. To this end any user terminals shall be placed outside the protected area in a separate stainless steel cabinet that is positively pressurized using a filtered air supply. Any key board shall have a protective membrane.

### Power Supply

CCWwTP is supplied through two 11kV points of connection. Metering is installed at these connections, as such low voltage installations do not require metering. All electrical systems shall have Power Factor Correction fitted to maintain or achieve a Power Factor of .95 lagging minimum. The consultant/contractor shall ensure that all designs consider power factor and install it as static or automatic correction.

Within the context of the larger site it is not always necessary to provide Active Filters or to reduce the harmonic current of a specific item of equipment. An assessment of the harmonic impact for a particular project shall be made and an approach agreed with the CCWwTP Site Manager.

## POTABLE WATER SITES

### Environmental

Ensure that the risk of Coliform contamination of the water supply is minimised during the works. Any works involving pipes or surfaces designed to come into contact with potable water (including wells) are to be confirmed as sterile by collecting a 100ml water sample and analysing the sample for absence of E. Coli and Faecal Coliforms. Contact the Laboratory Team, City Water and Waste Unit ph 03 941 5711 who will arrange for the samples to be collected and analysed. Allow 48 hours for this process.

### Security

Drinking water standards require secured, monitored access to water treatment and storage facilities. All access doors and hatches shall have door switches fitted and monitored through the SCADA System.

### Cable Supports

Cable tray may be galvanised mild steel for water pump stations.

## PUMP STATIONS

### Security

External cabinets with doors shall have locking hatches at the top and bottom, with a simple “lift-to-unlock” mechanism. House all control equipment in a secure structure, generally adjacent to the pumping station. It could be placed on top of the pumping station, depending on individual site requirements.

External cabinet or building door access shall have door switches fitted and monitored through the SCADA System.

### Design Features

Design the electrical installation to provide:

- Auto and manual operation of the pumps.

- Power supply authority kilowatt-hour metering and where AMR is not possible with addition pulse output.

- Wet-well level sensing to give stop/start control for the two pumps, a "high water" alarm, an “overflow” alarm and an analogue 4-20 volt output. See clause 7.3.2 – Wet-well for information on start and stop levels. The high water alarm should operate at the incoming sewer soffit level.

- Supervisory Control and Data Acquisition (SCADA) functions to communicate via communications link to a base station. Refer to clause 16 – SCADA.

- One single-phase socket and one three phase 20-amp socket, both for very intermittent use.

- Lighting in the control cabinet.

- Ensure the plant fully resets and restarts itself after power surges, blackouts and brown outs.

- Specify high efficiency electric motors from reputable manufacturers. Report the motor efficiency prior to ordering any such equipment.

- Detail smoke detectors above switchboards in all switchrooms and alarm through the SCADA, except for installations of less than 50 kW total connected load.

- If there is an aerial pole or a vent pole on-site within a three metre radius (top view) of the wet-well, detail a LED light near the top of the pole pointing towards the wet-well. Specify an LED light rated at a minimum 4000 lumens, cool white and housed in a security cage to protect from vandalism. Locate its manual switch inside the cabinet.

- Wire the equipment throughout with 250/440 volt cable. Identify the cable termination with suitable permanent markers and mark all outgoing terminals and links with identification symbols. Specify marine grade aluminium cable trays.

- Specify sealing of the cable ducts between the wet-well and electrical control cabinet. Specify sealing material that is easy to remove and replace to prevent pests and odour passing through from the wet-well to the cabinet. Size ducts to pass the pumps’ plugs from the wet-well to the control cabinet without disconnecting the plug from the cable or the cable from the pump, where plugs can be used.

- Inform the CCC power account manager at Meridian as soon as a site with a new or reinstalled power meter is ready to be load tested, preferably during planning but as early as possible. The account manager will arrange for the meter calibration to be checked and will advise Council of the correct multiplier and ensure billing is set-up.

### Three phase generator inlet plug

Fit all stations that do not have permanently installed generators with a three-phase generator inlet plug. Plugs shall generally be mounted on the switchboard, provide a 100mm diameter wall penetration and new polycarbonate access box on the station wall for the entry of portable generator cables. Use a Mennekes 1454A 125A 5 pin plug.

# GENERAL INSTALLATION & TECHNICAL REQUIREMENTS

## GENERAL

This section is for the design of Electrical Equipment Installation.

- Electrical Equipment includes but is not limited to;

- HV switchgear and transformers

- Switch boards, distribution boards, motor load centres

- Control panels, marshalling panels, junction boxes

- Cables and cable support systems

- Lighting

- General power outlets

- Instruments

- Solar panels and power supplies

- Radio and other communication equipment

- Only new materials shall be used in construction.

- No materials used in the construction of the above shall be inflammable, hydroscopic and subject to deterioration which may compromise the safety of the equipment.

## RATINGS

### Low Voltage Equipment

Equipment supplied shall deliver rated output under the stated service conditions.

- Rated voltage	230Vac / 400Vac +10% to -6%

- Insulation voltage	500V

- Frequency		47.5 - 52.5Hz

- Impulse withstand voltage (wave 1.2/50s)	6.0kV

Such equipment shall be suitable for connection to either of the following supplies, applicable:

- 400VAC, 3 phase, 3 wire, 50Hz.

- 400VAC, 3 phase, 4 wire, 50Hz.

- 230VAC, 1 phase, 2 wire, 50 Hz.

- 12VDC (Being phased out, only use for existing systems using 12VDC)

- 24VDC

### 11kV High Voltage Equipment

Equipment supplied for connection to high voltage AC systems (nominal system voltage 11kV) shall have the following (minimum) ratings:

- Rated voltage			12kV

- Frequency				50Hz

- Impulse withstand voltage		75/85kV

- Power frequency withstand voltage	28/32kV

The equipment shall be suitable for connection to an 11,000VAC, 3 phase, 3 wire, 50Hz supply.

All high voltage design and installation shall be carried out by an approved Orion contractor. Contact Orion for a list of approved contractors.

## STANDARDS AND REGULATIONS

This Specification shall be read in conjunction with the latest edition of the following Standards or Regulations, which are deemed to form a part of this Specification. In the event of this Specification being at variance with any provision of these Standards, the requirements of this Specification take precedence over the provisions of the Standard.

Reference to any Standard or Regulation shall mean the current issue of the Standard or Regulation and include any amendments thereto or any Standard or Regulation in substitution therefore.

All materials, equipment and workmanship shall comply with the Standards or Regulations detailed in Section A, Clause 2.0 and the following to the extent that they are applicable:

- AS/NZS 2053.1:2001	Conduits and fittings for electrical installations

- NZS 6401:2003Electric cables PVC insulated for working voltage up to and including 600/1000V

- AS/NZS 2293	Emergency evacuation lighting for buildings

- AS/NZS 2373:2003	Electric cables - Twisted pair for control and protection circuits

- AS/NZS 3008.1.2:2010	Electrical installations - Selection of cables - Cables for alternating voltages up to and including 0.6/1 kV

- AS/NZS 5000.1:1999	Electric cables - Polymeric insulated - For working voltages up to and including 0.6/1 kV

- NZECP 35:1993	New Zealand Electrical Code of Practice for Power Systems Earthing

Standards or Regulations other than those listed above and in Section A, Clause 2.0 may also be applicable. In any case all materials and equipment shall comply with an appropriate national (preferably AS/NZS or NZS) or international Standard, and wiring practices shall comply with all applicable New Zealand Acts, Standards, Regulations, Codes, etc.

## CABLES

### Low Voltage Cables

Red-sheathed cables shall only be used for fire circuits.

Where abbreviations of cable types are given, they shall have the following meanings:

- Al		Aluminium conductor.

- Cu		Copper conductor - Unless otherwise stated all conductors shall be 			plain annealed stranded copper.

- MIMS		Mineral insulated, metal sheathed.

- MIMS/PVC 	Mineral insulated, metal sheathed, PVC covered.

- PILC 		Paper insulated, lead covered

- PVC/PVC 	Polyvinyl chloride insulated and sheathed.

- TPS		Polyvinyl chloride insulated, tough plastic sheathed, to NZS 6401.

- XLPE/PVC 	Cross-linked polyethylene insulated, PVC sheathed, to AS/NZS 3198.

- ATA		Aluminium tape armoured.

- AWA		Aluminium wire armoured.

- STA		Steel tape armoured.

- SWA		Steel wire armoured.

- COAX 		Coaxial cable.

- FLEX		Flexible cord or cable.

- NS		Neutral screened cable.

### Conductors

The minimum size for conductors of cables for lighting circuits shall be 1.5mm2 and 2.5mm2 for conductors of cables for socket outlets. All conductors shall be copper.

The minimum size for conductors of cables for any other circuits (with the exception of instrumentation or data circuits) shall be 2.5mm2. All conductors shall be copper.

Larger conductor sizes (cables) shall be used where the loading, voltage drop, situation, etc, dictates. Aluminium or other conductors may be considered, but in general copper is preferred.

All conductors of 1.5mm2 and above shall be stranded.

### Instrument Cables

Instrument cable shields shall be electrically continuous.  When two lengths of shielded cable are connected together (at a terminal block(s)) an additional terminal block shall be used for connecting the shields.

Shields shall be isolated and insulated except at their selected grounding point. At any point of termination, the shield shall not be stripped back any further than necessary. Shields shall not be used as part of the signal circuit.

Analogue signal circuits shall be grounded at one common point. Digital signal circuits shall be either ungrounded, or grounded only at the power supply.

### Installation

The following electrical installation requirements apply:

- All cables shall be installed in accordance with the manufacturer's recommendations so as to minimise failure under normal use, and any abnormal conditions that may reasonably be anticipated, including electrical fault conditions.

- Analogue and digital data cables and LV DC cables shall be physically segregated from all LV and MV AC power and control cables. A separation of 500 mm or more is desirable, but may be reduced to 300 mm for short distances.

- Care shall be taken to prevent cuts or abrasion damage to cable sheaths. Dry lubricant shall be applied to cables during pulling in to prevent welding or scuffing of cable sheaths. No cable shall (at any time) be bent to less than its minimum recommended bending radius.

- Cables shall not be installed where they may be subject to damage due to a subsequent work (such as nailing of linings and the like).

- Cables shall not be embedded directly in concrete or plaster unless knock outs are allowed for. Where it is necessary to run cable through block walls or concrete slabs and the like, any such cable shall be enclosed within PVC conduit.

- Plastic sheathed cables shall not be run in any situation where timbers have been treated with tar oil, creosote or allied products.

- Single core cables forming part of a three-phase system shall be rigidly held in trefoil formation by approved cable clamps. Such cable installations shall be capable of resisting the forces arising from any fault current that may flow in any conductor(s) without significant disruption to the cable formation.

- When parallel conductors are installed, they shall be of equal length and shall follow substantially identical routes. Trefoil groups of parallel conductors shall each comprise one conductor of each phase. The circuit configuration chosen shall be one of the configurations recommended in Appendix B of the AS/NZS 3008.1.2.

- Cable entries to equipment shall be made using appropriate glands, sleeves, or bushes. The degree of protection provided by the equipment enclosure shall not be reduced by the cable penetration(s).

- Cabling to equipment that is likely to move and/or vibrate during normal operation (generators, motors and the like) shall be installed with cable slack or loops that allow for the vibration and movement. In severe cases, the fixed cabling shall terminate in a junction box and the final connections completed with flexible cable.

- All cables shall be protected where they pass through any openings, gaps, holes, etc, by ensuring that surrounding surfaces are smooth and free of sharp edges. Where necessary holes shall be bushed with close fitting plastic bushes

- Cable entries to buildings shall be vermin-proof and shall be sealed to prevent ingress of gases and water.

- Where cables pass through fire rated walls or floors an appropriate fire barrier or fire rated sealing compound shall be used in the following (or equivalent) manner.

- Seal the penetration with PYROSAFE SVT universal bulkhead system, packing any gaps with FYRFYBA ceramic fibre.

- Small penetrations may be sealed with Fire Research foaming sealant.

- Cables shall not be jointed without the (prior) written approval of the CCC. If permitted, joints shall be accessible and made using feed through terminals in proprietary junction boxes, with proprietary jointing kits to the approval of the CCC.

- Cables shall be neatly arranged on cable trays, ladder or in trunking. Twisting, unnecessary crossovers, bunching, excessive slack or tightness shall be avoided and where cables join or leave cable trays and the like, unnecessary crossovers and tangling shall be avoided.

- TPS wiring shall be concealed. Where this is not possible, the CCC shall approve the cable route.

- Where cables are supported on catenary wires, not more than five cables shall be bunched together on any one catenary wire. Cables shall be securely clipped or tied to catenary wires using proprietary clips or ties.

- Vertical cable rises exceeding 6 metres shall have loops or offsets to avoid differential movement between cable cores and the sheath. Provision shall be made for longitudinal expansion occurring in long lengths of MIMS cables.

- All cables shall have durable, waterproof labels (with unique circuit identification) fixed to them at both ends.

- After installation but before connection, all cables are to be tested for insulation resistance using a 500V tester for 230V circuits and a 1000V tester for 400V circuits. The results of the tests shall be recorded and supplied to the CCC.

## CABLE SUPPORT AND PROTECTION SYSTEMS

### General

The following requirements apply:

- Cable support systems shall be installed in accordance with the manufacturer's recommendations so as to minimise failure under normal use, and any abnormal conditions that may reasonably be anticipated.

- They shall be straight and, to the greatest extent possible, either horizontal or vertical and parallel with building lines. The intent is to produce a tidy installation.

- Joints and accessories shall fit closely and shall be correctly matched.

- Care shall be taken to avoid corrosion (due to contact between dissimilar metals) at fixings and joints. Fixings and fastenings shall be of a material appropriate to the parts being fixed, the loads imposed and the locations involved. Bolts, screws, nuts, washers and other fixing components shall 316 STAINLESS STEEL ONLY.

- Cable support systems shall be complete with matching proprietary bonds, ties, reducers, expansion joints and jointing accessories which shall be employed as appropriate at junctions, changes of level, changes of direction, and changes of size.

- Cable trays and trunking shall be installed as required. Cable trays and trunking shall be filled to a maximum of 67% of their capacity.

### Cable Ladder

Cable ladder shall be fabricated from extruded aluminium sections intended for the purpose.

### Cable Tray

Cable tray shall be fabricated from aluminium sheet.  All trays shall be perforated or slotted to permit airflow and drainage of liquids.

### Cable Trunking and Ducting

Vertical cable trunking shall be fitted with insulated cable supports to support cables at a maximum of 2.5m intervals.

Cable ducts shall be un-plasticized PVC sewer or drainage pipe (100 mm diameter or larger) complying with NZS 7649.

All fixing devices shall be of 316 stainless steel.

### Conduit

Conduits shall be manufactured from PVC and comply with the relevant parts of NZS 2053.

The minimum size of conduit shall be 20 mm and unless otherwise specified all conduits shall be one size larger than required by regulation for the number of conductors to be drawn in.

Conduit for any circuit shall be erected, completed, and swabbed out before any cable is drawn in.

Conduit shall be provided with minimum of 12 mm of cover where embedded in concrete or plaster.

Conduit runs shall be concealed where possible and installed with correctly sized saddle.

Conduits shall be installed either truly vertical or horizontal as appropriate. All runs shall be installed in a neat and tidy manner.

Install suitable draw wires where necessary.

Conduits that penetrate walls or floors of fire resisting construction shall be treated in the following or equivalent approved manner:

Seal all PVC conduit penetrations with fire stop collars.

Seal all steel conduit penetrations with PYROSAFE SVT universal bulkhead system and pack any gaps with FYREFYBA ceramic fibre.

For small penetrations with gaps less than 10 mm, seal with fire resistant foaming sealant.

### Catenary Wires

Catenary wires shall be galvanised steel of 2.5 mm diameter (minimum), securely fixed to at each end and supported at intermediate points as required. Catenary wires shall support cables clear of all structures, services and other equipment.

Turnbuckles of a suitable size to permit future adjustment shall be provided.

Separate Catenary wires shall be employed for mains voltage electrical services and for telecommunication, signalling, or data cables. Maintain a minimum distance of 50 mm between catenaries, or 150 mm between mains and other Catenary wires.

## CABLE JOINTING

Cable joints shall only be permitted with the (prior) written approval of the CCC.

All joints and terminations shall comply with the cable manufacturer's recommendations. Joints shall be carried out using:

- Proprietary jointing kits

- Prefabricated junction boxes

- Underground jointing chambers

- Termination pillars

- Compound filled boxes.

Cables shall be supported so that no weight or stress is transferred to the joint. The method of supporting the joint shall be to the (prior) written approval of the CCC.

Only workers experienced in all aspects of the proposed jointing work shall make the joint. A CCC representative may witness the work, and if (in his opinion) the work is unsatisfactory, may require remedial work on all other joints made in a similar manner.

Proprietary bimetallic links or lugs shall be employed where cables of different conductor materials are to be jointed. All components and materials used in a cable joint shall be selected to avoid corrosion due to contact between dissimilar metals.

The enclosure of any completed joint shall be compatible with the location of the joint and in particular shall prevent inadvertent contact with line conductors or the ingress of moisture, vermin or other harmful substances. The use of self-adhesive tape as the sole means of insulating and sealing a joint is not acceptable.

## CABLE TERMINATIONS

### Cable Glands

Armoured cable terminations shall be fitted with appropriate metal cable glands that shall grip the cable securely and seal on the outer sheath of the cable. The glands shall be complete with matching lock nuts and shall include provision for securely bonding the cable armour to earth.

PVC/PVC, XLPE/PVC and NS cable terminations shall be fitted with suitable sealing glands. These shall grip the cable securely and seal on the cable sheath.

Cables run in hazardous areas shall be fitted with the appropriated ‘Exe’,’Exd’ and ‘Exn’ gland.

### Cable Terminations

Cable terminations shall be made with correctly sized crimp or compression lugs, fitted according to manufacturer's instructions and recommendations using proprietary crimping tools or presses with correctly sized dies.

Torque lug terminations may be made with prior approval and providing the staff carrying out the terminations have specific training regarding the system being used.

Terminals shall not support the weight of cables, and cable terminations shall not be under mechanical stress.

Aluminium conductors shall be terminated using only proprietary bimetallic lugs or links.

All conductors shall be terminated sequentially and (for multi-core control cables) unused conductors shall be terminated so that the sequence is unbroken.

## UNDERGROUND CABLING

### Excavation

Underground cable installation shall include all necessary clearing, excavating, disposal of spoils, temporary supports, baling, pumping, the provision of bedding material, cable laying, protection, backfilling, marking and reinstatement.

Prior to the commencement of excavation the locations of all existing services near the proposed cable route shall be marked. Any existing facilities that are damaged during the course of the work shall be repaired and reinstated to the CCC’s approval.

### Cable Laying

Cables shall be laid in compliance with the requirements of the NZS Wiring Rules (AS/NZS 3000), NZECP 28 and Orion Technical Specification NW72.22.01.

Cables shall be bedded in clean sand with minimum depth of bedding of 50 mm below the cable and minimum cover of sand above the cable of 50 mm. The minimum depth of cable shall mean the perpendicular depth from final finished surface level to the top of the buried cables.

Conduits or ducts shall be provided at the depth(s) shown on the Drawings. Long radius sweeps or bends shall be used for all changes of direction.  Elbows will not be accepted. Install draw wire into all ducts.

A PVC cable marker strip shall be placed (during backfilling) along the full-buried length of cables at the depth shown on the Drawings. This shall be coloured orange for all cables in excess of extra low voltage. Other appropriate colours shall be employed for signal, data and telecommunications cables.

Underground cable joints shall be avoided wherever possible. Where unavoidable, underground cable joints shall be permitted only with the (prior) written approval of the CCC.

All exposed ends of underground cables shall be capped and sealed until properly terminated, to prevent the ingress of moisture.

A loop or slack section of cable shall be left at each side of a road or traffic way to allow for settlement of the road without stretching the cable.

Plaques shall be provided to identify the points at which buried cables enter the ground. These shall be securely fixed to the structures or external walls of buildings from which the cables enter the ground.

### Backfilling

Backfilling material shall be free of stones, debris, rubbish, etc., and shall be placed, and thoroughly compacted in 200 mm (loose) layers. The surface shall be made good so as to match the original adjacent surface(s) in accordance with CSS: Parts 1-7.

The CCC may inspect Cable joints and installation and Trenches shall not be backfilled until the CCC has given approval.

## CABLE MARKING

All cable and cable cores including marked multicore cables shall be marked with the cable designation and wire number as shown on the cable schedules and device circuit / wiring diagrams.

Markings should be made at each end of the cable and at each termination.

Cable shall be marked on each side of any termination, inside any cabinet or junction box and at any field termination.

The marling system shall be attached by an approved method such cable ties and clear housings threaded onto the cable.

## LUMINAIRES

Indoor Luminaries shall not be installed until the building is weatherproof.

Where luminaries are to be recessed into building work, openings shall be correctly sized and provision made for maintenance access if required.

Luminaries’ erected in rows shall be geometrically straight and at the same level except if otherwise shown on the drawings.

Luminaires shall be cast aluminium, plastic, polycarbonate.  No outside fitting shall be of ferrous material.

## GENERAL PURPOSE OUTLETS

### Socket Outlets

Socket outlets in domestic or commercial situations shall be mounted at a height of 0.30m above finished floor level, or 0.20m above benches. In industrial situations (factories, switch rooms, plant rooms and the like) they shall be mounted 1.4m above finished floor level in.

Mounting shall be directly to walls or in flush boxes or white polycarbonate mounting blocks as applicable. Where perimeter trunking is installed, socket outlets shall be mounted in the top section.

Three phase switched socket outlets shall be surface mounted.

### Fixed Outlets

Fixed outlets shall be installed for permanently connected equipment such as hot water cylinders, auto-doors, roller shutter doors, hand dryers, etc, and shall be mounted 1.40m above finished floor level, or 0.50m above benches.

Single phase fixed outlets shall be white polycarbonate, complete with isolator.

### Outlet Boxes

In timber-framed walls, switch and socket outlet boxes shall be fixed to dwangs, noggins or studs to provide the necessary support.

Where boxes are in block work or in concrete, steel galvanised boxes shall be used. They shall be sealed to prevent the ingress of cement slurry and securely fixed to prevent movement during concreting. They shall be examined (as soon as possible) after concreting, and cleaned out and protected against corrosion as necessary.

### Special Purpose Outlets

A label stating the purpose for which the outlet is intended shall clearly and permanently identify each special purpose outlet.

Outlets which supply at any voltage or frequency other than 230V, 50Hz, shall have pin configurations which will not accept the standard 10A, 230V “crows foot” (AS/NZS 3112) plug most commonly used in New Zealand.

## VARIABLE SPEED OR FREQUENCY DRIVES (VSD)

Installation of cabling shall be to the manufacturers recommendations.  Generally mains cables shall be shielded. Output cables shall be specially designed multiple screened cables such as Olex Varolex, General Cables ‘Kleen Screen, Triangle EU series or similar product.

Control input cables shall be shielded and control output cable to relays may be unshielded.

Power output cabling shall be laid a minimum of 300 mm from any other cable including the mains input cable.

Motor cable earthing cable shall be connected to a solid earth point at both ends of the cable.

## SWITCHBOARDS & MCCS

Switchboards and MCCs shall be levelled and installed with all vertical surfaces at ninety degrees to the horizontal plane.

Care shall be taken to ensure that mechanical damage does not occur during unpacking and installation. Particular care should be taken to ensure that floor trenches are bridged so that the switchboard or MCC cannot fall in during installation manoeuvres.

Switchboard shall be located to enable ease of cable installation to achieve recommended cable bending radii.

Cable access to the switchgear shall be via aluminium earthed gland plates 5 mm thick. All cables, where practicable, shall be glanded with the correct compression gland. All cable entry point shall be sealed to prevent ingress of vermin and insects.

## VALVE ACTUATORS

Valve actuators will be provided as part of the Mechanical works. All materials to electrically connect, control and convey cabling are part of the Electrical contract.

Actuators should be equipped with the following:

- 3 Phase motor (24V/48V DC may be appropriate in particular applications)

- 24v dc controls

- Open and close limit to terminals

- Open and Close Torque limits to terminals

- Command to Open and Close terminations

- Valve fault change-over relay contacts to terminals

Selected actuators will have position feedback and analogue positioners.

Where actuators are mounted in hazardous areas they shall be connected with the appropriate Ex glands.

## MOTORS

Pump motors shall be 3 phase for pumps 3kW or above.

Motors shall be high efficiency IE3 to IEC 60034-30:2008.

# SWITCHBOARDS AND CONTROL PANELS

## GENERAL

Electrical Switchgear includes but is not limited to;

- Main Switchboards

- Main Power Distribution Centres

- Motor Load Centres

- Motor Control Centres

- Distribution Boards

- Control Panels

- Marshalling Boxes

- Junction Boxes

Only new materials shall be used in construction.

No materials used in the construction of the above shall be inflammable, hydroscopic and subject to deterioration which may compromise the safety of the equipment.

Access to operator controls – pushbuttons, switches, isolators, etc – shall be by secure access. Secure access may be by site security such as security fences and locked gates, an outer weatherproof and vandalproof enclosure such as provided for roadside pump stations or inside a secure room or building.

Operator controls shall be provided in an otherwise dead front panel, without direct access or exposure to terminals, terminal covers, contactors, etc with the exception of their operating panels designed to protrude through the front of a masking panel.

Switchgear operator panels shall be logically laid out and labelled. Internal components shall be appropriately protected from accidental touch and the whole unit shall form a neat and functional unit.

Switchgear shall not be installed underground.

### Switchgear Standards

Switchgear shall be 3 phase, 4 wire with MEN earthing.

All equipment installed shall adhere to the relevant AS/NZS, BS, NZS, NZECPs or IEC standard covering that particular product. In no circumstances shall products or fabricated equipment be installed that is not manufactured to acceptable standard types as quoted in the New Zealand Electricity Regulations and AS/NZS 3000

The following Common standards for this type of work are:

- AS/NZS 3439.1:2002		Low Voltage Switchgear & Control Assemblies

- AS/NZS 3439.3:2002		Low Voltage Switchgear & Control Assemblies

- AS/NZS 3100:2009	Approval and test specification – General Equipment requirements for electrical equipment

- AS/NZS 3760:2010	In-service safety inspection and testing of electrical equipment

- AS/NZS 60947.6.2:2004	Low voltage switchgear and control gear

- AS60529:2003			Degrees of protection provided by enclosures.

- NZS 4203:1992			Seismic Loadings

### Exceptions and Deviations

The contractor shall list in his tender all exceptions and deviations from the requirements of this document including any alternative materials or equipment layouts.

The contractor shall provide the following information with the tender;

- Switchgear Layout

- Weight and dimensions

- List of proposed equipment that differs from specified equipment

## TECHNICAL SPECIFICATION

### Switchgear Ratings

Switchgear ratings shall be suitable for at least 125% of the maximum demand.

### Cabinet Construction

The following general statements apply where switchgear is designed by the contractor or sub-contractors.

- Generally all equipment cabinets shall be manufactured from metal.

- Main panels are generally floor mounted.

- Small wall or field mount panels may be made from a non-metal material.

- Small control panels and distribution boards are generally wall mounted.

- Switchgear shall be Type Tested Assemblies(TTA) or Partially Type Tested Assemblies(PTTA).

- Where a special cabinet base is required it shall be a welded steel ‘I’ section or channel, galvanized and painted. It shall be supplied with appropriate clamps . Base shall have provision for insertion of 50 mm diameter pipes through the width of the base to assist lifting with fabric strops.

- Where required, cabinets shall have anti-condensation heater installed complete with a thermostat.

- An exhaust fan and thermostat shall be installed where temperatures are capable of reaching 40°C. Dedicated exhaust ducting shall be provided for equipment capable of generating exhaust temperatures in excess of 45°C. Air conditioning units may be used in lieu of forced ventilation in some cases.

- Ventilation design shall be supported by heat calculations including solar gain where this may be an issue.

- Cabinets shall be provided with lighting in large control cabinets and be activated by a door mounted microswitch.

- The switchgear IP rating shall be suitable for the environment where it is installed.

- Design shall include for segregation of voltages where possible including separate cabinets and ducting to segregate 400/230v ac from 24/12v dc. circuits.

- A Name plate label shall be attached to each main item with engraved text as shown below:

- Manufacturer and contact details

- Serial Number

- Voltage ,Frequency and Current Rating

- Form of Segregation ( Form xx)

- Form of Protection (IPxx)

- Form of construction per AS/NZS 3439 to be agreed with the Capital Program Group Electrical Engineer or as consistent with the CCC provided Standard Design for the type installation.

- All cabinets Doors shall be labelled indicating cell function.

- All metalwork shall be painted.  Finishing shall include degreasing, etch priming, undercoating and 2 coats of final colour. Final colour is dependant of type of metalwork used if Type Tested equipment is used. PTTA metalwork shall be Ripple Cream.

- All metalwork shall be bonded using earth bounding cables.

- Cable glanding plates shall be Aluminium.

- Equipment Gear Plates shall be painted mild steel or industrial Formica.

- Access to Bus Bar chambers shall be though removable panels secured with fixings requiring a tool to remove them.

- All Bus Bar and other access panels shall be easily accessible without isolating the switchgear.  All panels shall be suitably labelled identifying the danger of removing such panels.

- All live metal work shall be suitably shrouded to avoid accidental touch by operators carrying out routine inspection or maintenance work.

- Switchgear metal work shall be designed to allow expansion in length and ease of replacement or modification of cabinet configuration.

- Cabinets shall be laid out to ensure a logical flow from mains voltage device to low voltage devices.

- All doors shall open in the same direction where practicable and be capable of having key locks or latches fitted without changing the door.

- Door openings shall allow the withdrawal of any component inside the cabinet without the removal of other components inside that cabinet.

- All terminals for all devices shall be wired to terminals, excepting small light and power circuits wired directly to miniature circuit breakers; these do not count as spare space.

- All cores for all cables shall be wired to terminals; these do not count as spare space.

- Provide for 20% spare space for all elements.

- Allow to supply a box of 5 spare fuses for each size of glass fuse fitted.

- 24Vdc controls are preferred over 230Vac for improved safety.

- Where switching is carried out at low voltage all contact surfaces shall be gold plated.

### Switchgear Equipment and Installation

The following general statements apply where switchgear is designed by the contractor or sub-contractors.

- Where bus bars are installed they shall comply with the Form of Separation form 3b/4A

- Bars shall have colour coding to identify Phases.

- All bus bar mounting shall comply with a type test rating and certification must be provided at time of tender.

- All holes shall be de-burred and joints filed flat.

- Bus Bar connections shall be secured with constant pressure washers.

- All copper bars shall hard drawn high conductivity copper specifically manufactured for this purpose.

- Equipment shall be laid out to achieve the best use of the space while maintaining a logical layout and flow.

- All equipment shall be Din rail mounted where possible.

- Cable trunking shall be open slot type, closed slot will not be accepted. Trunking will be mounted horizontally and vertically to achieve a logical flow of cabling between

- Components and trunking spacing shall allow adequate space for cable numbering and attachment of cable ferrules.

- Components attached to the gearplate directly shall be by screws in the threaded holes, blind rivet nuts, or bushes. Use only slotted, posi-drive or Philips headed screws. Hex head drive self tappers are not acceptable. Pop riveting is only acceptable to attach PVC trunking systems and DIN Rail.

- All components shall be labelled with the name as shown on schematic diagrams. Self-adhesive and engraved labels are acceptable attached to trunking where there it is impractical to attach to gearplate.

- Mains voltage and low voltage relays shall have different base configurations. 230v control relays shall be round base pin configuration while low voltage bases shall be rectangular.

- All field wiring shall be terminated in terminal blocks mounted on DIN rails. All terminations shall be labelled as per the number shown on the drawings.

### Switchgear Equipment Wiring and Cabling

Wiring shall be carried out in a neat and systematic manner and shall not be possible for any cables or wires to contact sharp or rough edges that may damage sheath or wire insulation.

Wiring shall be contained within closed slot trunking  open slot  trunking will be rejected.

Control cabling inside trunking shall occupy up to 50% of the capacity of the ducting.

All control wiring conductors up to 4mm² shall have Starfix crimp ferrules or similar.

Conductors of PVC insulated panel wiring (other than instrumentation, communications and data circuits) shall be flexible and adequately rated for the circuit loading. In any case conductors will have a minimum cross sectional area of 0.75mm².

Segregation or shielding shall be provided between instrumentation, communications, data, 230VAC, 400VAC, 24VDC and 12VDC circuits and associated terminals.

All terminals for incoming/outgoing circuits for control, data and communications shall be mounted in accessible positions that are also convenient for cable termination.

Cable jointing inside trunking is not permitted. All jointing shall be carried out at terminal blocks.

Solder joints and solder tinned cable ends into terminals are not permitted.

No more than two conductors shall be terminated in any one side of any terminal. Each wire shall be labeled. Whenever possible shorting straps or combs shall be used to bridge identical terminals. Terminal bridging strips shall be insulated or covered.

Wiring to doors shall be anchored at the panel side and be of sufficient length to enable the door to swing fully open without strain on the wiring.

All cables, wires and conductors shall be labelled, with both an overall cable label and individual core ferrules.

Cable colour coding shall be as follows;

- 3Ph/1Ph	Red/White/Blue

- 230v control	White Appliance wire

- Neutral		Black

- Earth		Green/Yellow

- RTU  inputs       Orange 1.0 mm Appliance wire

- RTU outputs	Purple 1.0 mm Appliance wire

- PLC Inputs	Orange 1.0 mm Appliance wire

- PLC Outputs	Purple 1.0 mm Appliance wire

- 110V ac	Yellow

- 12v DC Pos 	Red

- 12v DC Neg	Grey

- 24v DC Pos	Pink

- 24v DC neg	Grey-common with 12v Neg

- 24VAC Phase	Brown

- 24VAC return	Brown

- 4-20mA 	Pos – White/red, Neg- Black

## MOTOR STARTERS

### General

Detail soft starters if variable speed drives are not used. Ensure variable speed drives don’t “hunt” between pumps.

Specify pump motor controls with the ability to ramp the start and stop times to prevent high and low pressures on start-up and shut down. Set the ramp rates from the following conditions excluding under power failure, unless surge transient analysis dictates alternative rates:

- Determine the pump’s minimum flow and the corresponding minimum operating RPM.

- Ensure the pump ramps up to the minimum operating speed at 10% of the total frequency range/sec (5 Hz/sec).

- Limit the rate of change above the minimum operating speed to 2% of the total frequency range/sec (1.0 Hz/sec) when accelerating or decelerating.

- On shut down, the ramp rate below the minimum operating speed should be approximately 10% of the total frequency range/sec (5Hz/sec).

Confirm any alternative rates are acceptable with the equipment supplier

### Direct on Line

Note Orion Network code bans DOL starter for motors over 4kW unless agreed with them.

Direct on line starters shall be configured to include the following equipment;

Lockable Isolator

- Fuses or MCB

- 24v DC Contactor

- Adjustable electronic Overload

- Manual/off/auto selector switch

- 24v DC Control relays

- Ammeter

Or a combination isolator / circuit breaker system.

Control shall be as follows;

- Manual – motor runs as soon as ‘Man’ is selected or by pushbutton on the control panel.

- Off – no operation in Man or Auto.

- Auto – Motor starts on a command from PLC or SCADA.

### Soft Starters

Soft starter shall be configured to include the following equipment;

- Lockable Isolator

- Bypass contactor

- Manual/off/auto selector switch

- 24vDC Control relays

- Ammeter (4-20mA)

- Door mounted Starter control panel

- IP 20 for mounting inside switchboards and IP 54 for wall mounting.

Control shall be as for DOL.

Fault Configuration

Starters shall be configured to stop on a Mechanical fault input (external trip) and display a fault showing that the fault has been generated from an external source such as a no-flow or water low level alarm contact. The starter shall also have an output configured to indicate a ‘run’ state and another to indicate an ‘Electrical’ fault.

Outputs

The starter shall be configured to give a 4-20mA output proportion to motor current to drive a front panel mounted ammeter. This may also need to be an input to SCADA.

### Variable Speed Drives

Variable Speed Drives shall be configured to include the following equipment;

- Lockable Isolator

- Manual/off/auto selector switch

- 24v DC Control relays

- Door mounted Ammeter (not required where HMI used in pumping stations)

- Controller Inside control card (CI) (where required)

- Door mounted Starter control panel

- Maximum Transient Current 165% for 2 sec/ 150% for 60 seconds.

- IP 20 for mounting inside switchboards and IP 54 for wall mounting.

- Manual Speed Control Potentiometer (preferable to VFD panel speed control.)

Intelligent motor starter ports on such starters may be required to directly interface with the plant communications system via Ethernet communications.

Intelligent modular rack mounted or individual Telemecanique 'Integral' motor starters are acceptable for motors less than 4kW. The proprietary Modular bus bar mounting system is acceptable for use in Form 4 or 3b switchboards provided adequate ventilation and only Telemecanique accessories are used.

Control shall be as follows;

- Manual – motor runs as soon as ‘Man’ is selected or by pushbutton on the LCCD panel, speed control via Potentiometer (or panel).

- Off – no operation in Man or Auto.

- Auto – Motor starts on a command from PLC or SCADA. Speed control via automation system.

Fault Configuration

Starters shall be configured to stop on a Mechanical fault input (external trip) and display a fault showing that the fault has been generated from an external source such as a no-flow or water low level alarm contact. The starter shall also have an output configured to indicate a ‘run’ state and another to indicate an ‘Electrical’ fault.

Outputs

The starter shall be configured to give a 4-20mA output proportion to motor current to drive a front panel mounted ammeter or integral in the VSD display. This may also need to be an input to SCADA

An output for drive speed may be used direct to SCADA where required,

## VENTILATION AND AIR CONDITIONING

All panels containing heat producing devices shall be equipped with ventilation to ensure equipment is not subjected to temperatures above 40ºC.  Where cooling air is drawn in from outside attention must be made to the air quality.  Filtering of air shall take place where the ambient level of H2S exceeds 1ppm and electronic equipment is to be installed.

## FACTORY TESTING

Type Test Certificates shall be available for inspection by the Engineer if requested but should be supplied in the Operations and Maintenance Manual.

Factory Acceptance Testing shall be carried out by the contractor in the presence of the Engineer. However routine testing shall be carried out before the official Factory Test.

Testing shall be carried out in accordance with a written test procedure. A completed copy shall be provided to the Engineer before the start of testing.

Routine Testing shall include, but not be confined to, the following;

### Power Off

- Mechanical test to ensure all fixings and fitting are secure and bolts torqued where necessary. Doors open and close freely and all internal equipment is accessible and secured in the correct manner.

- Doors and equipment are able to be locked where required.

- Door interlocks with MCCSs, fuse switches and isolators is effective and interlocks are defeatable.

- Layout check to ensure the panel layouts on and inside the panels are as per construction drawings.

- All connections on power and control circuits are tight and all wiring is protected.

- The ratings of the switchgear is as specified.

- A point to point test has been carried out on all power and control wiring.

- All wiring, internal and door mounted equipment is labelled.

- On a unit with Bus Bars, a HV test as specified has been carried out and results recorded.

- The requirements of metering are as specified.

- The equipment is as specified or approved as an alternative.

- Cable sizes, colours and installation are as specified.

- Earthing is continuous and of the correct size and is labeled as required.

### Power On

Power On testing shall only be carried out with all circuit breakers, isolators, Fuse Switches and fuse terminals in the open position. All equipment shall be turned off and all automatic devices and switches turned to OFF.

Power On testing is carried out to ensure that all relevant equipment is supplied by the correct voltage supply.  Any damage cause to equipment that is caused by incorrect wiring shall be renewed at the cost of the contractor.

The Contractor shall systematically liven circuits to check that power supply outputs are correct, that any non mains powered equipment has the correct supply and to enable any programmable devices to the set up.

Once Power On testing has been completed all devices shall again be isolated.

### Factory Acceptance Test

Factory Acceptance Testing is carried out in the presence of the Engineer or his representative.  The contractor shall supply all certification, marked up As Built drawings and completed test sheets.

He shall supply all test equipment and demonstrate the function of the switchgear as required.  At the completion of testing the Engineer will present the contractor with a list of defects or sign the test sheet.

At the completion of testing the contractor shall set all devises to OFF and package the switchgear ready for delivery.  A set of marked up As Built drawings shall accompany the switchgear.

## DELIVERY

At the completion of testing the contractor shall set all devices to OFF and package the switchgear ready for delivery. A set of marked up As Built drawings shall accompany the switchgear.

The wrapped switchgear shall be labelled as follows;

- Delivery address

- Contact person and phone number on site

Switchgear shall be packaged to suit the delivery and off-loading method.

## APPROVALS

All design drawings shall be approved for construction by at least one of the following

- the Capital Program Group Electrical Engineer

- the Plant Manager

- the Operations Manager

# INSTRUMENTATION

## PRELIMINARY

This specification is for the Supply and Installation of Instrumentation.

## GENERAL

This specification includes for the supply, installation, cabling, labelling, setting up and commissioning of any instrument for measuring plant parameters installed within the plant.

It does not include for the integration of the instrument in the automation system or the inclusion of the instrument output into the SCADA system. It does include for connection to the nearest Network PLC to the instrument.

## DESIGN AND SELECTION

The Process Engineer (PE) will produce a P&ID showing the location of the instrument in the process. The PE will also produce a Functional Description of the instrument for the SCADA Engineer and filing within the Councils Asset management System.

The instrument will be selected by the following criteria;

- Known brand

- Compatibility with other plant instrumentation

- Robustness and durability

- Field wiring accessibility

- IP Rating and or hazardous area rating

- Suitability for the task

- Mechanical construction

- Reliability

- Repeatability

- % Error and accuracy

- Mounting system

- Proven measurement technology

- Industry standard outputs and network communications compatibility.

- Local display and operation

- Programming and local trending capability

- Ease of calibration and self-diagnostics.

- Communications protocol support

- Programmable features such as engineering units displayed

While all of these features are not applicable to all instrumentation they are to be taken into account where applicable when selecting new instrumentation.

## MOUNTING

Field instruments shall be mounted as specified by the manufacturer in an accessible location for installation and maintenance. Instruments shall not be mounted on removable items such as hand rails, vibrating equipment without suitable damping or cable support systems. Instruments shall be mounted in a safe position removed from hazardous, hot, corrosive and high positions where possible. Where this is not possible consideration should be given to the supply and installation of remote transmitters located in ‘safe’ areas.

Consideration should be given to the location of the instrument to see that it is accessible for calibration, servicing and maintenance without providing special devises to access it.

## STANDARDS

Supplied instrumentation shall comply with the relevant standards related to the type of measurement being carried out.  The Engineer shall be aware of what the relevant standards are for the specific instrument being supplied.

Standard Signals

| Parameter | Protocol | Output | Power supply | Notes |
| --- | --- | --- | --- | --- |
| Level | HART | 4-20mA | 24v DC or loop | HART where available |
| Flow | HART | 4-20mA | 24v DC or loop | HART where available, flow pulse and reverse flow indications |
| Pressure | HART | 4-20mA | 24v DC or loop | HART where available |
| Temperature |  | 4-20mA | 24v DC or loop |  |
| Proximity | N/A |  | 24vDC |  |

Where it is not possible to use 24DC a 230v RCD protected circuit may be used.

## FLOW METERS

### General

The installations must follow the manufacturers installation guidelines allowing for appropriate clear pipe upstream and downstream. Where no data is provided then 5 diameters upstream and 3 diameters down stream shall be provided.

Under normal circumstances, flow meters will be buried direct in the location directed by the Engineer with upstream/downstream clear pipework in accordance with the manufacturer’s specifications.

The flow sensor will be installed in the pipeline complete with earthing rings. The sensor earthing shall be bonded to the transmitter in the switchboard (by others) by bringing an additional 6mm2 earth cable back alongside the signal cable.

The flow sensor will be wrapped in ‘denso’ tape (600), followed by ‘denso’ PVC overwrap tape (931), ensuring that the body, terminal box, flanges, and bolts are completely covered.

The void around the sensor will be back filled with a packing sand mixture.

If the sensor location is subject to heavy traffic, then a form of ‘U’ shaped concrete box culvert will be installed above the sensor to avoid any external weight on the coil housing.

The flow sensor installation will be verified and signed off by an Independent Verifier approved by both Christchurch City Council and Environment Canterbury.

Following installation the flow meter accuracy is to be verified while buried by utilising the flow meter manufacturer's proprietary verification tools and software packages

### Design Duty

The design maximum flow rate for the pumping station/each of the wells is + m3/hour.  The actual flow rate will vary from + m3/hour to maximum flow depending on demand.

The pipework either side of the flow meter will be designed for the maximum station capacity of + m3/hour and is expected to be 250 mm or 300 mm diameter.

### Magnetic Flow Meter

The flow meter(s) shall have prior type approval by the Christchurch City Council Assets Management Team for use on Christchurch City Council Wastewater and Water supply pumping stations. The minimum requirements for the flow meter are as follows:

- Electromagnetic type.

- Supplied with remote head complete with wall mount kit displaying:

- Flow rate in m3/hr - analogue.

- Flow total in m3 – backlit lcd, non-resettable. Read via HART communications

- Flow range 0 - + m3/hr (max flow + 25%)

- External connections required for SCADA are:

- 4-20 mA (rate) with HART superimposed over.

- Pulsed output (total) – 5 kHz pulses at flow of 1.2 x flow limit x m3/hr rounded to nearest 100. (Shall be capable of 5 kHz pulses minimum) for pumped wells only. For artesian wells 1 pulse/m3

- One resettable relay (indicating a faulty meter)

- Flow meter accuracy to be verified following installation and while buried by utilising the flow meter manufacturer's proprietary verification tools and software packages. A verification certificate shall be supplied with each meter.

- HART Foundation registered

- Signal converter to be programmed for Empty Pipe and Reverse Flow Detection

- Sensor sized to suit pipework (Clause 12.2) or smaller if required to meet accuracy requirements at low flow.

- Flanged to AS 4087 PN 16 (check pressure rating below).

- Lining shall be EPDM or hard rubber.

- Sensor protection rating to IP68.

- Signal converter protection rating to IP65

- Supply voltage 24 VDC.

- Unit accuracy to be +1% or better over flow range + m3/hr to + m3/hr. A calibration certificate shall be supplied with each meter to verify its accuracy.

- Check max flow velocity range is less than 3 m/s..

- Pressure rating greater of 16 bar or 1.5 x maximum operating pressure bar minimum.

- Supplied complete with 30m min of interconnecting cable terminated and sealed to IP68 at the sensor

## EARTHING

Earthing shall be carried out strictly in accordance with the manufacturer’s recommendations. A separate instrument earth is to be installed to which all instruments, instrument screened cables and instrument cabinets are to be connected. The instrument earth shall be bonded to the installation main earth with one 16mm² single core cable as a minimum

## CALIBRATION CERTIFICATES

All instruments installed at the plant shall have a factory calibration certificate confirming instrument specifications.  Instruments shall be re-calibrated at the discretion of the plant instrument technicians.

## DOCUMENTATION

All new instruments shall be supplied with relevant software CD’s and instruction manuals to enable onsite programming, data uplifting and downloading, parameter setting and diagnostic facilities. Summary test sheets shall be provided in addition to manufacturers configuration datasheets. Examples are included in the appendicies.

Asset Equipment templates are to be filled out and submitted to council for all new or replaced instrumentation.  Refer TRIM 14/141308 911 Asset Management - CWW - Station Asset Templates

# AUTOMATION

## GLOSSARY OF TERMS

- SCADA		Supervisory Control And Data Acquisition software package

- PLC		Programmable Logic Controller (also known as an RTU)

- RTU		Remote Telemetry Unit (also known as a PLC)

- HMI		Human Machine Interface

## GENERAL

It shall be carefully noted that the specification details set out here are mandatory and shall NOT be varied without the vendor having sought and received the WRITTEN agreement of the CCC SCADA Engineer.

CCC considers that computerised systems shall not be relied upon for personnel safety interlocking. As such all safety related interlocks shall be either external to the automation systems, or part of a certified safety system such as ASi safe safety bus. Status of interlocks shall however be included in PLC and HMI systems as appropriate.

Any item that does not meet the site standard for automation equipment and practices shall not be used.

### Functional Descriptions (FD)

A Functional Description (FD) document must be produced which enables CCC to have a full working understanding of how the automation system operates under all normal and abnormal conditions. The Functional description captures the user requirements to describe the automation system that is to be provided, how it will control the process and all interactions with the operator.

Functionality must be thoroughly tested during factory acceptance test (FAT) by simulation or other means by the System Integrator before site functional commissioning and acceptance testing can occur. This may be undertaken against a dedicated Test Acceptance Specification (TAS) outlining the various individual tests to be performed or against a more detailed set of functional descriptions commonly referred to as a level 2 FD. A level 2 FD is essentially the integrators software detailed design specification (SDDS) and is sufficiently detailed for the programmer to code against.

The upkeep and Integrity of the FD is the Contractors responsibility until the plant has been handed over.

The Functional Description document is to be treated with the same importance as that of the PLC code. It is in fact the master controls document as it is the cement between the Plant, PLC and SCADA.

The CCC have developed generic User Requirements Specifications (URS) for both Water & Wastewater Pumping stations to assist Integrators in their development of a Functional Description and to drive standardisation.  A template for documenting the software detailed design Functional Descriptions is freely available and its use is encouraged by Contractors tasked with providing functional descriptions or making changes to existing functional descriptions.

- TRIM 09/367127  CCC - FD Template.

- TRIM : 15/615036   CCC - Two Pump Wastewater Station Variable Speed Drive Control - User Requirements Specification

- TRIM : 13/523632 CCC - Two Pump Wastewater Station Soft Starter Control - User Requirements Specification

- 15/626813 CCC - Water Supply Station - User Requirements Specification

### System and Supporting Documentation

- All supporting documents must be supplied in electronic form in the Microsoft 20xx format or later and in the case of drawings, aside from a pdf version the contractor should supply the source AutoCAD or Visio version that is compatible with the current version used by the CCC.

- The Medium used to supply these documents should be CD or DVD.

### Training

- Comprehensive training shall be provided at operational, technical and system design levels for all systems provided. A training plan shall be provided prior to commissioning and shall be completed before commissioning can be considered to be complete. Training is to be a separate activity at the completion of other commissioning activities.

### Support

- Tenderers are to specify in their Tender the level of support that can be expected after handover.

### Site Procedures

- After the project has been handed over, it is the responsibility of the contractor to ensure compliance with all CCC procedures including software and functional description changes, and backups.

- All work must be done with the prior knowledge/permission of the relevant CCC site representative.

### Site Participation

- Key site personnel are to be involved as an integral part of the development team to ensure CCC requirements are met.

## TAG NAMES AND CONVENTION

### General

The Council operates a standard for plant and equipment tagging at the Wastewater Treatment Plant.  Refer “CWW Tagging Convention”, (TRIM:ELEC06/6074).

The Councils Asset Register, Operator10, PLC, SCADA and P&ID drawings all use the same core element of the overall tag to facilitate cross-referencing. The Councils tagging convention must be adopted and adhered to by consultants, contractors and other approved service providers undertaking work at the wastewater treatment plant.

### PLC Structure

It is the Contractors responsibility to ensure that his PLC documentation methods and standards are approved by CCC prior to any work being commenced. This will avoid any rework from the contractor at his expense. Where applicable examples can be supplied to assist the contractor

As a general rule device descriptors in PLC’s/RTU’s should include as a minimum the following:

- The Tag name (Where applicable; as per CWW Tagging Convention )

- A clear description of the device

- Any special operating range for the device eg: 50 To + 50 Degrees.

Whenever possible analogue inputs and analogue outputs must have their raw values and Engineering values added to their description/comment fields.

In order to facilitate easier reading of the descriptors, words must be PROPER Cased

## PROGRAMMABLE LOGIC CONTROLLER (PLC) & REMOTE TELEMETRY UNITS (RTU)

### General

All data points in any PLC/RTU shall have a related Tag and an Address comment/description related to the data point’s duty. The PLC/RTU internal tagging systems are related directly to the Function Description and the Plant Tagging System (refer CWW Tagging Convention, TRIM File: ELEC07/716).

### PLC Software

The CCC has standardised on the use of Schneider PLC’s programmed using Unity Pro software at the Christchurch City Wastewater Treatment Plant (CCWwTP).

The Unity Pro software is IEC 61131-3 compliant and utilises Derived Function Blocks (DFBs).

### RTU Software

The CCC has standardised on the use of Yokogawa Stardom RTU’s which are programmed using the Yokogawa IEC 61131-3 compliant Logic Designer software.

Older legacy RTU’s that are still in operation utilise similar non IEC 61131-3 compliant programming packages.

### User Defined Data Types and Derived Function Blocks

User defined data types (UDT) and Derived Function Blocks (DFB) are used extensively in software development to reduce the overall time taken to code both the PLC/RTU and HMI software applications. The council has a library of re-usable software blocks that it prefers to use on automation project work.

DFBs are re-usable blocks of code which use structured data elements in the same way as the ArchestrA SCADA graphical objects use them and as such there is normally a corresponding ArchestrA object for each DFB. This allows seamless integration between the PLC/RTU, site HMI and the base SCADA system.

Once developed these DFBs are used to create DFB instances for each device. DFB’  libraries are available for both PLC and RTU to assist the Integrator writing software to deliver the functionality described in the FD’s.

The Contractor should request from the CCC responsible Engineer the latest version of the councils software libraries before undertaking software development.

If for any reason a UDT or DFB requires change or a new one is required, permission must be received from the CCC asset management team before any changes are made.

### PLC/RTU Hardware

The following sections describe the minimum requirements for PLC and RTU hardware.

General

- All I/O and field devices related to process control or selections shall be connected to the PLC/RTU.

- No PLC/RTU shall cause unrelated process plant to shutdown due to inappropriate field connectivity.

- All hardware shall be installed in accordance with the manufacturer’s specification supplemented by CCC specific requirements detailed in this section.

- I/O and associated equipment shall not be installed in locations that contain voltages in excess of extra low voltage.

- The standard control voltage for digital I/O is 24V DC for new installations. In some rare instances existing site requirements may require the use of other voltages such as 240 VAC.

- PLC/RTU I/O systems can be Local or Remote. Racks containing I/O that are anything greater than 3m from the logic processor would be considered to be remote I/O.

- Remote I/O systems are acceptable.

- At project completion there must be at least 30% free memory capacity.

- The minimum chassis size for PLC systems shall be 10 slots. (unless agreed otherwise).

- At project completion an area must be left for the next larger size chassis to be installed. For example if a 16 slot chassis is installed, an area must be left to enable replacement with the next size.

- The grouping and layout of I/O modules shall follow the following format whenever possible,

- Communications and specialist I/O modules

- Analogue Input Modules

- Analogue Output Modules

- Digital Input Modules

- Digital Output Modules

- All processor and I/O chassis shall be separately grounded with 6 mm-conduit wire back to local earth bus bar. This bus bar shall be grounded back to the UPS feed distribution board using 10-mm conduit wire.

- The PLC/RTU shall be capable of obtaining scan times for all PID loops of less than 100msec, and digital of less than 60ms, when the plant is fully operational.

Analogue I/O

- 4-20mA I/O modules shall be used for analogue signals and should be connected in differential mode whenever possible. (unless agreed otherwise).

- For temperatures, approved RTD modules will be considered

- If “SMART” digital instrumentation is offered then complete details of operation, configuration, maintenance and interfacing to the automation system shall be supplied. If operational access to the instrument systems is via a dedicated network/highway then full software and operating details are to be approved by CCC.

Marshalling Terminals

- Loomed I/O swing arms to marshalling terminals for field wiring shall be used for all high density analogue and digital I/O.

- Marshalling terminals shall be ‘cage clamp’ type.

Digital and Analogue I/O

- Marshalling terminals shall be individually fused per output with indication that the fuse has been activated (ruptured).

- Digital input marshalling terminals may be fused per module.

- Analogue output and input marshalling terminals shall provide the ability to test the loop value without the need of interrupting the circuit.

### Uninterruptible Power Supply

- As a minimum the UPS must supply all SCADA/HMI, PLC primary chassis, and active network equipment and critical instrumentation.

- Provide an external service / bypass switch for the UPS that allows the UPS to be removed from service without loss of power to the equipment supplied by the UPS.

### Power Supplies 24V DC

- All 24V DC power supplies primary shall be at minimum power conditioned feed, to avoid brown out power failure condition occurring.

- Amp meter, voltmeter and fault indication shall be supplied with the power supply units unless agreed otherwise with the CCC responsible engineer.

- Analogue Power Supply 24V DC

- A dedicated central redundant analogue 24V DC power supply shall be used for each major process area. The power supply shall be linear.

- Digital Power Supply 24V DC

- A dedicated central redundant digital 24V DC power supply shall be used for each major process area. The power supply shall be linear.

### Communications

This section only serves to identify the basic communications requirements for PLC’s. For a complete description of the councils networking requirements refer to section 9 “Communications”

General

- All PLCs shall support a 10BaseT, 10BaseFL, 100BaseT or 100BaseFX Ethernet communications port.

- All PLCs shall support a RS422, RS485, or RS232 serial communications port.

Cabling

- All communications cabling must be at least 500mm from any power or signal cable.

- Dedicated stainless steel or high impact plastic conduit or stainless steel trunking shall be provided for all communication cabling in process areas. In non-process areas high impact plastic conduit is acceptable.

- The cable and termination components shall be in accordance with manufacturer specifications.

- Termination points shall be easily accessible, with no cable joining.

- The cable shall be clearly labelled at termination points stating the source node followed by destination node.

Programming Terminal Connection Points

- There shall be at least one programming terminal connection point on any communications network.

- All programming terminal connections shall be dedicated.

- Each programming terminal connection point shall be designated a nodal address supplied by CCC.

- Remote or local programming functionality shall be provided in locations approved by CCC.

### Field I/O

General

All field equipment, cubicles, wiring, installation, testing and commissioning shall be carried out according to the manufacturer’s specifications and Sections 3 and 4 of the CWWP Generic specification.

Labelling

- All I/O modules shall be marked with the I/O address on the front of the module and on the tag inside. In the case of processors these shall carry the allocated name, Asset register tag, addresses etc. In the case of other modules they shall be marked in a similar manner to support their function and identification.

- Field devices shall be labelled with their appropriate tag. The tags are to be made of engraved or stamped stainless steel or other approved system.

System Control I/O Requirements

- Each plant component (eg pumps, valves and solenoids) that is automatically controlled by the system shall be able to be operated manually from a SCADA or HMI station.

- Appropriate control logic shall exist to ensure that manual operation must not cause danger to personnel or plant.

- Where drive field isolators are fitted these shall provide feedback to the PLC.

- Each VFD isolator shall provide isolator feedback to the VFD.

- Each VFD controlled by a PLC shall provide run feedback to the PLC that is controlling it.

- Drives and key equipment identified by the CCC Responsible Engineer are required to be connected to a Ethernet network that allows motor phase current and motor thermal model feedback to the PLC.

- Each process valve controlled from a PLC digital output shall provide feedback (PLC input signals) from de-energised (non-active, closed on normally closed valve) and energised (activated, open on normally closed valve) positions.

- Where fault overrides are configured and operated via the SCADA system or HMI, then these shall be notified and automatically reset on de-selection.

- The use of communications networks to control valves and drives is acceptable.

### PLC Software

All memory points used must have symbols and address comments allocated.

Standard Automation Routines

CCC has developed and is still developing a set of standard automation routines applicable to its processing facilities. These routines are accompanied by supporting documentation that will be released on the appointment of an approved System Integrator.

Deviation from these standard routines will only be allowed when approved in writing by the CCC Responsible Engineer.

Redundant Logic & Tags

No redundant logic or tags shall be left in a processor after the completion of a project.

Approved System Integrators

Systems Integrators not identified under the approved Integrators list must be approved in writing by the CCC Assets Management.  System Integrators must be able to demonstrate an understanding of:

- Developing PLC code in the standard code format.

- Readability between standard CCC functional description and PLC code must be demonstrated.

- Show an ability to interface the standard code to the respective SCADA and HMI systems.

- Show the use of text messaging for devices and selection faults to the SCADA and HMI systems.

- Demonstrate an ability to simulate the PLC code against functional descriptions.

- Demonstrate ability to deliver quality documentation including but not limited to functional descriptions, manuals, testing and commissioning procedures.

A probationary period for the system integrator will require monitoring by CCC.

Modification to Existing Programs

CCC shall approve any modifications prior to commencement of any works.

Version Control & Backups

Following completion and handover of a project, all CCC procedures for software changes, function description changes and backup procedures shall be followed.

Network Integrity Checking

Network integrity checks shall be performed between each PLC and its peers using a ‘heartbeat’ system. This mechanism shall be monitored for failure with routines implemented to handle failures via appropriate alarms and graphical displays on the relevant SCADA and HMI systems.

Industrial switches that provide hooks into SCADA systems via OPC and Modbus plus for purposes of monitoring and reporting network failures and loadings shall be configured to provide appropriate alarms and graphical displays on the relevant SCADA and HMI systems.

Critical Interlocking

Critical interlocking is defined as interlocking between control systems to ensure that no personnel injury or damage to equipment will occur in the event of a device failure.

Interlocking shall be wired to discrete I/O or employ the use of certified safety bus networks to ensure that they operate in a fail-safe manner.

Process Control Loops (PID)

- No PID control loops shall have their input and output elements (eg process variable (PV) and control variable (CV)) wired to different control systems or operated across a non-I/O network.

- The setting of Set-point values, output values, ramp values and mode of control for a PID loop is to be done in a separate program file for each PID control loop. This program file shall be named with the loop tag eg “PID_Tag_Description”.

- The use of a common PID sub-routine or user defined function block is encouraged and to be used by all PID controllers. The common PID routine shall contain the code for change of mode from PLC to operator mode, set-point tracking, output tracking, controller status etc.

### Testing

Simulation:

- Total system simulation during factory acceptance test must be complete and comprehensive to ensure that commissioning times are minimised.

- The use of simulation software packages or simulation software written in PLC code is acceptable to emulate the actual process actions and test the PLC code, HMI and SCADA systems.

- Testing shall be against the Functional Descriptions (FD) and or a set of purposely written set of test procedures.

I/O Testing:

- I/O wiring shall be “continuity checked” prior to I/O any functional checking to ensure integrity of the physical wiring and termination.

- Component operational checks for all field devices and drives shall be done via the HMI and SCADA systems to ensure that I/O is fully checked through the complete control system before automatic programs/sequences are run.

- It is required that the supplier shall have approved by CCC, adequate procedures that will document the compliance and completion of such checking.

## DOCUMENTATION

The following documentation shall be provided for documentation of PLC/RTU, and HMI software code.

- Functional Descriptions

- PLC/RTU data-table layout.

- PLC/RTU and I/O Rack layouts.

- PLC I/O Schedule.

- I/O and network schedules for each enclosure.

- Module dip switch settings.

The following are to be kept up to date in the PLC/RTU and provided on a supporting document.

- PLC to PLC communications tables.

- HMI to PLC Communications and Vice Versa.

- Comments for each rung/block/structured test routine shall be provided.

- I/O network saved configurations.

- I/O tag listing with descriptions.

# COMMUNICATIONS

## GENERAL

Use Ethernet communications for all plant control networks.

Use of other communications networks such as Fieldbus, ASi, DeviceNet, CANbus, ControlNet and Profibus require written approval of the CCC Engineer.

Any new network equipment or cabling that is required to connect into the existing site automation architecture shall be approved by the CCC Responsible Engineer.

## PLC/RTU TO CONTROL DEVICES

Communications between a PLC/RTU processor and its I/O, including remote I/O, Variable Speed Drives, Soft starters shall use a dedicated Ethernet network that is independent of other Ethernet Networks. The level of independence required is such that no other communications traffic is able to affect the traffic loading or availability of the I/O network.

## PLC/RTU TO SCADA, PLC/RTU AND HMI

Communications between PLC/RTU, SCADA and HMI devices shall be on a dedicated Ethernet network that is secured from other networks. The level of security is such that only specifically permitted devices are allowed to communicate over the network.

## SCADA TO SCADA

Communications between SCADA I/O Servers, SCADA Application, Historian and SCADA client terminals shall be on a domain managed network contained to the degree practical to permit approved business connections, local SCADA client connections and remote VPN connection SCADA client connections.

### SCADA to Plant Historian, Information Server and Corporate Systems Communications

This is via a dedicated router/switch and firewall so that local network traffic is contained as much as possible within the domain.

## CCC INTRANET TO SITE CONTROL NETWORK

The Site control network connects through the firewall, router and APN/PABX to the CC WAN.

### Office PC to SCADA Communications

The viewing of dynamic plant data is to be achieved by using either web based thin clients or via a session on the SCADA terminal server.

### Office PC to Information Server Communications

Historical Event Data analysis and running of reports is achieved through the CCC’s existing corporate network.

## ETHERNET COMMUNICATION

### General

This specification covers the supply, installation, testing, commissioning and documentation of the complete Ethernet network, which must enable any device to be connected on any CCC site.

Note: In addition to this section and other related sections all work shall also comply with the AS/NZS 3080. This is based on the International Standard ISO/IEC 11801 – Information Technology – Generic telecommunications cabling for commercial customer premises. If required explanations for terms and abbreviations can be found in The Glossary of Terms sections of AS/NZS 3080, AS/NZS 3085.1.

Any new network equipment or cabling that is required to connect into the existing site shall be approved by CCC.

Note: This specification is for Automation and Central Networks only and is not intended to be used for general admin (MIS) network construction – approval for MIS network associated work must be approved by the CCC IM&CT Department (however the cabinets and cables may be shared for monetary reasons).

### Specification

The specification covers more specifically:

- The provision of Communications (RJ45 8 wire) Outlets (CO) and individual 8 wire Unshielded Twisted Pair (UTP) cables from every CO back to a Distributor enabling termination of these cables.

- The provision of Communications Equipment Cross Connects (Data) and patching facilities at the Distributor.

- The connections of active computer network hardware to the cabling system.

- The commissioning and testing of cabling and active hardware.

- The connections to the existing communications system.

- The maintenance and integrity of the existing communications system.

- The documentation of the complete installation or update of the existing communications system.

### Documents Referred To

The work carried out by the Communications Contractor shall comply in all respects with this specification. The current issue relevant to New Zealand and International Communications Standards in particular to:

- Cabling for commercial premises and subsequent amendments.

- AS/NZS 3085.1 Telecommunications Installations – Administration of Telecommunications Cabling Systems.

- Industrial Safety Code Regulations.

- Relevant Specifications for Connections to Telecommunications Carrier

- Networks.

### Communication Protocols

A single connection to the corporate WAN network shall be achieved via a dedicated network router. Only CCC approved Ethernet Communication Equipment shall be used to optimise the network traffic.

### Communications Design Responsibilities

The CCC shall approve the following design criteria prior to the commencement of any works:

- Bracket and support detailed design.

- Communications wiring diagrams of all equipment, showing all interconnections between equipment to enable the necessary wiring to be undertaken.

- Details of all equipment necessary to meet the engineering specification and performance indicated.

- Capacity, and redundancy of the communications outlets, hardware, distributors etc.

- Capacity, location and design of the communications conduit or trunking system where used in lieu of multi-conduit installation. The contractor shall be responsible for ensuring mechanical protection for the existing communications services during construction.

## COMMUNICATION CABLING

### General

This work generally comprises the installation of structured cabling as indicated on the Design Plan.

### Specification

- Ethernet backbone cables must be appropriately dimensioned to meet the stated requirements marked up on the Design Plan.

- Termination, jumpering and patching facilities for the structured communications cabling system.

- Patch cord (stranded cables), and jumpers (solid core cables).

- Liaison with CCC for cut-over of the cabling and connection to the LAN, telephone system etc.

- Integrated Structured Horizontal Cabling from the communications enclosure.  Distribution to communications outlets (locations marked up on the Design Plan reference).

- Dual (assumed unless otherwise shown on drawings) RJ45 Communications Outlets(CO) mounted in faceplates to match the electrical faceplates in colour and style.

## ENCLOSURES

### Structured Cabling System

- Shall be compliant with AS/NZS 3080 in all respects.

- The Copper Structured Horizontal Cabling system shall perform to at least Class D 100 ohm balanced cable (solid core) requirements (Category 5E cabling and components) with no fixed link (from the Distributor to the Communications Outlet) being electrically greater than 90m (allowing for the twist in the cable).

- Optical Fibre Cables shall be multi-mode, graded-index optical fibre with nominal 62,5/125μm-core/cladding diameter. Fibres shall be terminated in either ST or SC connectors. Unjacketed fibre cables shall be terminated in Optical Fibre cable trays or boxes for protection. The fibre installed must be appropriate to the physical environment the cable is being installed in as recommended by the manufacturer.

- Carry a system warranty for at least 15 years.

- Provide full labelling of outlets and frames to CCC specifications.

- Provide full documentation of all work performed to enable ongoing administration of the cabling system.

### Patch Leads

- Whenever possible patch leads should adhere to the colour conventions identified in Table 1 below but where this is not possible as in the case with many industrial applications, STP patch cables are only available in white (light grey) and so these should be clearly identified as follows:-

- For patch leads, it is not critical to identify the patch lead per-se but it is important to identify the devices/ports it connects to. Generally the primary switch ID would be used for the base cable ID rather than area.

- The "/" is the separator between the device tagname (per tagging standards) and the allocated port. In the case of a PLC, the port number would be "slot #.port #".
For patch panels, the "PPnn" comes from the Electrical standards example.

Patch lead examples:

Example 1 - Patch lead between PLC & switch:
Generator 2 panel houses PLC07 (905.1 PQ007) and associated IO layer switch (905.1 NQ006.04). Connection between these devices within the cabinet would be STP patch lead from PLC NOE card in slot 2 to Connexium switch port 1.
Label would be banded blue with patch cable ID 826.2 DJ 001 (alt id could be 905.x to suit site if schedule exists)
Device 1 number on label 905.1 PQ007/2.1
Device 2 number on label 905.1 NQ006.04/1 

Example 2 - Patch lead between switch and panel mounted device (VSD)
Connection between these devices within the cabinet would be STP patch lead from Connexium switch port x to VSD Ethernet card port 1.
Label would be banded blue with patch cable ID 826.2 DJ 002
Device 1 number on label 905.1 NQ006.04/2 
Device 2 number on label 826.0 DQ001/1

Example 3 - Patch lead between switch and panel mounted patch point
Connection between these devices within the cabinet would be STP patch lead from Connexium switch port x to panel patch point 1.
Label would be banded blue with patch cable ID 826.2 DJ 003
Device 1 number on label 905.1 NQ006.04/8 
Device 2 number on label 905.1 CUxxx PP01

Example 4 - fixed cabling from panel patch point to network panel patch panel
Connection between these cabinet would be STP cable.
Label would be banded blue with patch cable ID 826.2 DJ 004
Device 1 number on label 905.1 CUxxx PP01 
Device 2 number on label 905.1 CUyyy PP01/5 (5th socket on patch panel 1)

Table -1  Patch Leads

| PRIMARY USE | COLOUR |
| --- | --- |
| Crossover | Red |
| Administration | Beige |
| Management (iLo) | Grey |
| Voice/Video | Green |
| Wireless | Purple |
| SCADA and Ethernet HMI’s | Yellow |
| PLC and RTU | Blue |
| PLC to PLC (Peer to Peer) | Black |
| KVM Extenders | White |
| Fibre | Orange |

### Communications Outlets

- All CO faceplates shall be flush mounted on lined surfaces (Flush Boxes) and mounted either vertically or horizontally to match power outlets.

- Faceplates shall be level at a matching height above floor to power outlets and be at least 50mm (usually stud width) away from them.

- Where faceplates cannot be flush mounted they shall be mounted on suitable surface mounting accessories.

### Cable Reticulation Techniques

- Install Ethernet cabling In accordance with the recommendations of the manufacturer so that the warranty is in no way compromised.

- On cable trays or ladder within building risers and communications enclosure or where more than 12 cables run together in ceiling and service spaces.

- Hung from steel plastic coated catenary tensioned cables in ceiling spaces and in accessible under floor areas for less than 12 cables.

- Ensure that cable trays, catenaries and cables generally are installed in straight lines square or parallel to building features such as walls (internal and external) where possible, ie not run diagonally especially across other services.

- No horizontally run cable shall be unsupported for more than 500 mm in ceiling spaces or under floors. Cables shall be suitably secured where not on trays, ladders or catenaries.

- Cables shall be concealed where practical.

- Cables must be installed to ensure minimum-bending radius stipulated by manufacturer is not exceeded.

- Where cables cannot be concealed, they shall be run in surface mounted trunking or conduit appropriate to the location with 50% spare capacity. Trunking and conduit shall be run parallel and square to building features both vertically and horizontally.

- Run cables with a clear separation distance of 500mm from electrical cables. Where cables cross electrical cables they must be at right angles to the electrical cable and be separated by a physical barrier by at least 500 mm.

- Cables installed in trays, trunking or on catenaries shall be securely fixed at 300 mm intervals with cable ties.

- Bond all steel, metal trunking, trays and catenaries to the Main Building Electrical Earth with a minimum of 4mm2 bond wire (any bonding shall comply with the requirements of AS/NZS 3000).

- Where trunking is used ensure that the correct manufacturers fittings (Glands, bends, flexible couplings etc) are used, and ensure that inspection joints/pull boxes are used. Distances between inspection joints/pull boxes should be no more than 15m apart.

- A draw cord must also be left in any trunking or conduit for further use.

- Dedicated stainless steel trunking or conduit shall be provided for all communication cabling run within the confines of a manufacturing plant. This trunking or conduit shall be at least 500 mm from any power or signal cables.

- Only data cables shall be run in trunking or catenary wires – power, fire cables etc are strictly prohibited from being run or cable tied to data cable.

- Install cables in spaces free from protrusion of screws and similar fasteners or where prone to mechanical damage. Remove all sharp edges and allow slack in the cable run.

- All cables shall be installed together free of twists and able to be traced without removing other cables.

- Provide adequate support at the top of all cabling vertically installed, ensuring that the weight of cables is supported at a maximum distance of 300 mm.

- Do not route cabling into horizontal ducting using sharp bends in contravention of cable manufacturer’s specified minimum bending radius.

### Naming Conventions for Fibre

The labelling of fibre cables is set out in Table 2 below, this example label tells us the duty, type, site unique fibre Number, core count, fibre installed date, the patch panel its terminated in, the Patch Panel location and the fibres destination.

- Fibre # - this is a unique 6 digit sequential number giving a fibre run its identity.

- Cable Type – the type of cable it is.

- Core Count – the size of the fibre (number of cores).

- Date – the date of installation.

- Patch Panel # - the patch panel (Comms cabinet) to which the fibre is terminated.

- Location – a simplified description of the patch panels geographical location ie RAS (Return Activated Sludge Building) followed by the source of the fibre ie SVR (Server Room).

AE M 0123 12 012306 PP01 RAS/ SVR

Table 2  Fibre labelling examples

| LABEL ELEMENT | EXAMPLE | OPTIONS |
| --- | --- | --- |
| Duty | AE | A=Administration E=Engineering AE= Admin+Eng |
| Type of fibre | M | M=Multi mode S=Single mode |
| Site Unique Fibre # | 0123 | 4 digit sequential number identifying the fibre cable |
| Core Count | 12 | Number of cores |
| Installation Date | 012306 | MMDDYY |
| Patch Panel # | PP01 | Letters PP + 2 digit number identifying patch panel cabinet |
| Location | RAS/ SVR | Destination/Source |

Labelling Requirements:

- Label all Communications Outlets and Patch Panels to ensure that each Outlet and equivalent patch panel termination have the same number.

- Label all Voice and Data Patch Panels using appropriate numbering schemes.

- Label all optical fibre terminations.

- Separately identify and label all distributors and cabinets.

- All trunking, conduit and catenary wires must be labelled “Data Cabling” at least every 6m using a good quality high visibility label.

### Commissioning and Testing

- Test the horizontal cabling fixed installation from both ends using a suitable scanner to Class D or as specified by CCC. Provide a copy of the test report showing compliance.

- Each installed fibre shall also be tested using an optical fibre power meter/or alternative from both ends and results recorded for attenuation loss at 850 and 1300 nf wavelength over the backbone length to meet the maximum loss requirements for such cables in AS/NZS 3080.

- Commission and test all active data equipment to be connected.

## DOCUMENTATION

The following documentation shall be provided for documentation of communications networks.

- Network connection diagram

- Network device port schedule

Note: Updates to existing Network Port Schedules are to be provided where applicable.

# SCADA

## GENERAL

- The Human Machine Interface (HMI) shall wherever possible use Ethernet TCP/IP as the physical connection to the communications network.

- Over a logical grouping of PLC’s there shall be a SCADA system consisting of a primary server, a backup server and client computers as may be necessary.

- SCADA/HMI systems shall not be used for logic control of the plant. There must be no background applications, which monitor plant status and then drive bits or registers or I/O in the PLC.

- The HMI shall not hold interlock logic for selection inhibits, this shall be provided in the PLC.

- The SCADA/HMI must have the following minimum performance criteria:

- Times to update points in the SCADA/HMI Database using high speed or wired Ethernet (TCP/IP) < 2 second

- Screen Display Build Time shall be < 3 seconds

- Trends must be displayed in < 15 seconds

- All HMI software systems shall have an unlimited tag license unless written approval is provided by CCC responsible engineer.

- Where SCADA/HMI licensing is based on number of displays an unlimited license shall be purchased.

## REMOTE SUPPORT

- CCC has a standard policy of no direct connection via modem to site networks.

- Any external connections must be approved by the CCC IM&CT Services Department.

- This will generally take the form of a Virtual Private Network (VPN) connection.

## HARDWARE

### Computer & Communications Enclosures

- All computers shall be housed in a dedicated computer enclosure on an individual shelf or with individual rack mounting kit.

- All computer and communications enclosures must have a hinged and glazed front door, hinged rear access and must be temperature controlled with positive pressure filtered fans, must be mounted on a plinth.

- All computer and communications enclosures must offer a minimum of 45 x 19” RU and 900 mm deep.

- All computer and communications enclosures must be powder coated.

- Unobstructed access to the front and rear of the enclosure must be provided. Transportable or roller enclosures are not acceptable.

- All computer and communications enclosures must be supplied with an integral Vertical Power Rail with a minimum of 10 x 10A outlets suitable for the locale of installation.

- All computer and communications enclosures must be lockable.

- All communications enclosures must allow management jumper bars for patch leads approximately every 3U.

### Control Desk Layout

- Control desk layouts must allow unobstructed access to SCADA/HMI monitors, keyboards and mice.

- Keyboard/video/mouse extender receivers shall be located out of sight but be easily accessible. Keyboard, video, mouse and power cables shall be routed through plastic portals inserted into the desk as necessary.

- Control room lighting must adhere to OSH requirements.

### Keyboard/Video/Mouse Extenders

Computer Server hardware will be remotely mounted from monitors and associated keyboards and mice, therefore signal-boosting devices may be required.

The use of a single twisted pair cable (minimum of CAT-5e) between a transmitter and receiver is preferred.

## SOFTWARE

### General

The Wonderware InTouch/ArchestrA package is the Councils current choice of SCADA system and any additional automation works should be integrated into the current SCADA system in accordance with the Councils current SCADA User Requirements specification object definitions.  Furthermore, any additional SCADA graphics/trends, alarms and reports must be documented within the existing SCADA User and Engineering Manuals as appropriate.

### Operating System

The following operating systems are acceptable to CCC:

- Microsoft Windows 20xx Server (for primary and backup servers)

- Microsoft Windows 20xx for client computers

### Graphical Interface Standards

When ever possible graphic elements should adhere to the colour conventions and symbol representations identified within the SCADA User Manual.

### System Redundancy

The system shall be a “hot” primary/backup server configuration. Role transition from the Primary to Backup server must be notified to the operator via an alarm, supported by logging of an event to file.

Role transition from the Primary to Backup server due to a failure with the Primary server must require no operator intervention.

### Historical Archiving

Archiving of data will be to the existing SCADA Historian.

As a general rule the following tags shall be configured to historically archive.

- Analogue inputs and outputs.

- PID process variables control variables and set points.

- PID mode of operation (ie auto, manual, set output).

- Drive load currents (%), drive kW, drive speed, drive speed reference, drive thermal load.

- Field device status (running, stopped, In/Out Service etc).

- Alarms

- Operator commands

Note:

(1) for sites communicating via radio or low speed communications networks the rules for archiving will be more selective and dead-bands will be coarser to optimise bandwidth utilisation.

(2) for projects requiring large amounts of additional archiving it may be necessary to provide additional storage capacity within the current Historian Servers. Estimates for hard disk storage should be notified to the councils SCADA Engineer so that where necessary additional hard disk capacity can be made available. Costs associated with providing additional capacity may be charged to the project.

### Trending

- All tags configured to historically archive shall be trended and all trended tags shall also be historically archived.

- A maximum of eight tags are to be assigned to a trend display.

- Each tag in a display must be assigned a unique colour.

- It shall be possible for trends to be retrieved within operator specified date and time ranges.

- Trends shall be able to be displayed on multiple client computers at one time while retaining individual control of time ranges and scale.

### Alarms

The schedule of Alarm Priorities are:

- Critical (P1), Rang 1-249, Animation Colour = Red

- Urgent (P2), Range 250-500, Animation Colour = Red

- Non Urgent/standard ( P3), Range 501 – 749, Animation Colour = Orange

- Events (P4), Range 750 -999, Animation Colour = Blue

The schedule of Alarm Paging Classes, as managed by SCADAPhone – the alarm paging system, are:

- Christchurch

- BP Lyttelton

- BP Akaroa

- Communications

- SCADA System

- RTU System

An alarm point shall be continuously scanned by the SCADA. If an alarm is to be configured with an acknowledge flag in the HMI/SCADA, then this flag shall also be scanned continuously.

The common acknowledge flag shall be set when the alarm is acknowledged from the HMI/SCADA.

Individual valve and motor/pump alarms may be required to latch.

Latching alarms require the intervention of the operators to reset the particular alarm. Note: hardwired trip related alarms for motors/pumps may require the intervention of the plant Engineer to physically reset the hardwired trip before the operator can attempt a reset from the HMI or SCADA system.

### Status Text Messaging

Status messages shall be displayed within the ‘Status Window’ to provide information concerning the current operation of any sequences.

The messages shall be stored either natively, in a CSV file or in a relational database.

### Reporting

Reports are created using either Microsoft SQL Server Reporting Services or the Active Factory Plug-in for Excel. In both cases the reports may then be published to the Wonderware Information Server (WIS) where they are viewed using a standard web browser. Note: domain access rights/privileges will determine the reports made available to individual users. Refer TRIM File: 10/502351 section 8 CCC Water Supply SCADA URS for further details of available reports.

Where no existing report exists within the SCADA system these must be created and must provide the same look and feel as existing SCADA reports.

Any new automation systems must meet the following general requirements.

- Each major processing plant and energy services plant shall report data relating to the processing or production rate of the plant, i.e. m3/hr, kg/hr, kW etc.

- If CCC has elected not to purchase the necessary instruments for these measurements then the PLC shall contain logic that determines each of the current consumption rates.

- These rates shall be determined by allocating a ratio of the metered value to the individual plants according to feedback from the plant and sound engineering principles.

- All these product flow rates and utilities consumption rates shall be totalised to provide the following:

- Running totals for the day, week, month and year

- Totals for each day of week

- Previous week, month, year totals

- There may be specific project requirements for Plant performance reporting. These shall be detailed in the Specifications section of the tender documents.

Note: for production rates it is very important that the data point reflects the “Product Rate” at all times, i.e. is zero when plant is shutdown.

## DOCUMENTATION

Where existing documents do not exist then any new documents provided must adhere to the following requirements:-

- How to start-up and shutdown the system.

- Which displays are used to control certain areas of the plant.

- How displays are linked together.

- How to access process selections and trend displays.

- Which displays are used to view alarm groupings.

- All HMI project files.

- Hard and soft copies of any macros, scripts or custom developed source code (ie. Visual Basic, C++). A CDROM containing all text messaging databases as at completion.

- A CDROM or DVD containing a Device Tag Database cross-referencing where the tag has been used. Each tag shall be unique and shall have a clear description related to the duty of the tag.

- All schematics and manuals detailing the system configuration and layout must be provided to CCC.

# GENERATOR AND DIESEL ENGINES

## GENERAL

Detail an alternator manufactured in accordance with Rotating electrical machines that meets the following requirements:

- Enclosure: screen protected drip-proof

- Prime Rating

- Voltage regulation: inherent ±2%, no load to full load at 0.8 to unity power factor at any voltage within the range setting

- Voltage variation 400-430 volts

- Earthing: multiple earth neutral system. The neutral point to be brought out to a terminal

- Frequency: 50 cycles per second

- Phases: 3 phase 4 wire with switching in active conductors only

- Power factor: 0.8

- Rated voltage: 415 volts

- Excitation: the alternator shall be self-exciting with PMG

- Radio interference: shall be in accordance with the Radiocommunications Regulations

Directly couple the alternator to the engine by means of a flexible coupling.

Specify a unit capable of powering the largest pump, or enough pumps to allow for the pumping of the Maximum Flow, plus all auxiliary equipment (ventilation fans, battery chargers, lighting etc).

Specify a generator capable of starting and running the pump sets from stand still and zero delivery pressure and that is continuously rated to run at the rated output for several days at a time. Generators should also be rated to allow for the effects of the harmonic load content for a station utilizing variable speed drives or other wave-chopping devices. The harmonic loading can account for up to 25% of a set’s rating.

Specify a governor capable of maintaining a steady speed within the limits specified in Reciprocating internal combustion engines. Performance for class A1 governing .

Consider the effect of the air temperature within the building on the engine air intake after prolonged diesel runs.

Vent the exhaust at a height above the roofline conforming to ECAN requirements. Refer to the Ecan Pollution Prevention Guide http://tools.ecan.govt.nz/eppg/. Detail a vermin proof exhaust pipe weather protection cap - not a counter balanced type.

Ensure servicing points such as water and oil levels etc are readily visible and accessible.

## CONTROLS AND CHANGEOVER

Specify a “Deep Sea”, engine management system:

- Generators used for exporting shall have a Deep Sea 8620 enhanced model controller.

- Generator controllers used on non-export stations shall use a Deep Sea 7420 model controller.

Both units should be programmed to energise the output shown on the generic drawing when the control mode is NOT IN AUTO. Generic drawings are:

- Sockburn Pump Station

Detail all control equipment in appropriate enclosures ensuring it is visible without the need to open doors, hatches etc.

Design controls that make three attempts at starting with cranking periods of up to 15 seconds, each with an equal rest period between. In the event of the unit failing to start after the last attempt, specify that the controls lock out and energise the remote alarm.

Changeover shall be provided by motorised MCCB or ACB as appropriate for the size. Do not use Schneider communicating coils. Opening shall be provided by 230Vac No-Volt release with 3 second delay. Closing shall use the corresponding supply voltage, generator 230Vac for Generator CB, transformer 230Vac for Mains CB. Interlocks preventing parallel operation may be fitted for non-paralleling units however the design shall make allowance for later removal of any interlocks provided in an Auto Mains Fail only installation.

### Instrumentation, Protection and Control

Configure the SCADA radio transmission unit (PLC/RTU) logic to start the engine as required.

Engine protection devices linked to a common SCADA alarm shall include:

- Over temperature

- Low oil pressure

- Over speed

- Low coolant flow

- Low coolant level

Local indicators shall include engine running, voltage, current, frequency and faults and of faults in the battery charger.

Provide the following indications:

- Hour meter

- Engine water temperature gauge

- Lubricating oil pressure gauge

- Lubricating oil temperature gauge

- Tachometer

- Boost gauge when engine is not naturally aspirated

Locate all meters and gauges to avoid vibration damage.

Specify voltage-free contacts to give the following indication to the SCADA system:

- Fail safe common diesel alarm (low oil pressure, high temperature, over speed, low engine tank water, fail to start) [Contacts open for alarm]

- Fail safe charger fault. [Contacts open for fault]

- Alternator on [Contacts closed for on]

- Diesel running [Contacts closed for running]

Specify the supply of an analogue signal to the SCADA that is proportional to the kilowatts being produced. This is from Generator MCCB metering trip unit.

### Starting

The method of starting control shall be selectable between auto and manual. Starting equipment shall be rated for a minimum of 10 starts per hour.

Provide an Auto/Amp SCADA temperature compensated power supply/battery charger if the unit does not have a factory fitted charger. Include a fitted battery:

- of at least the capacity of the manufacturer’s recommendation,

- of the largest physical size that will fit the manufacturers battery cradle, and

- with the highest Cold Cranking Amps (CCA) rating for its physical size (CCA varies even with physical size).

## COOLING SYSTEM

Cooling is normally by way of a water-to-air radiator. Special circumstances must apply before Council will accept a water-to-water heat exchanger.

Allow for radiant cooling to the air within the building. Incorporate forced ventilation of the building if required for prolonged diesel runs under full power with the building doors and/or windows closed (see clause 6.6 - Penetrations and watertightness). Consider the conflict between ventilation and noise control when designing this system. Compliance with TA noise plan is required.

Fit the engine cooling system with a low wattage heater and thermostat suitable for operation on 230-volt mains supply and adequate to maintain an engine temperature of approximately 25°C.

When using a water-to-water heat exchanger:

- The cooling system may utilise approximately 14°C water from the reticulated supply.

- Establish a minimum safe quantity of raw water and permanently set this using a flow control valve. The flow control valve must allow the raw water supply to be controlled independently from any pressure changes that would otherwise affect the flow rate i.e. it MUST be pressure compensated.

- Detail a solenoid valve to enable raw water flow only when the diesel is running.

- Mount a pocket type thermometer in an obvious, easily seen position in the raw water discharge to allow monitoring of the discharge temperature.

- Discharge cooling water to a sewer unless this option is totally impractical. Limit the discharge temperature to 20°C if the water is discharged to a waterway. Ensure Resource Consent compliance with allowable flows and temperatures for any discharge to a waterway.

- Detail an RPZ (Reduced Pressure Zone) valve fitted to the cooling system additional to the RPZ required in clause 15.5 – Water Supply, to prevent backflow of potentially contaminated water into the pump station water supply.

- If raw water is not dumped to waste, detail a double wall plate heat exchanger (e.g. Alfa Laval M6-MDFM) to prevent possible contamination of the reticulated supply.

## FUEL SYSTEM

Provide diesel storage using a standard sized tank capable of supplying the engine for 72 hours at the maximum load that is capable of being applied by the installation. This may be well below the maximum engine/generator’s full capacity. Note that some engines use high fuel flows and the fuel tank as injector/pump cooling and the tank minimum capacity may be considerable.

Tank capacity should be sized to provide 15% of the above required fuel volume as maximum free board. Detail the fuel intake from the tank to the diesel generators 100mm above the bottom of the tank, to allow any impurities to settle at the tank bottom.

Provide good access for refuelling, volume indicators and Council’s preference for aboveground storage when designing the fuel storage. Integration (inside) the main building will be considered only if beneficial and complying with the Hazardous Substances and New Organisms Act.

Ensure diesel storage is located at the following distances from the boundary (as adapted from Table 4, Schedule 4 of the Summary of Approvals of Substances transferred under the Hazardous Substances (Dangerous Goods and Scheduled Toxic Substances) Transfer Notice 2004 (As Amended)):

| Tank Capacity (L) | Distance from high intensity land use (m)* | Distance from low intensity land use (m) |
| --- | --- | --- |
| <600 | 0 | 0 |
| 1,000 | 1.5 | 0 |
| 2,500 | 2 | 0 |
| 5,000 | 3 | 2 |
| *Includes residential land uses, and high use roads |  |  |

There may be a requirement to obtain resource consent for the storage tank if the site is:

- within 20m of a river, a bore, a wetland boundary; or

- within a 1 in 20 year flood plain; or

- where the depth to unconfined or semi-confined groundwater is less than 30m; or

- within 100m of an active fault and the land is over a semi-confined or unconfined aquifer.

- within 1000m of a community groundwater bore.

A double skinned tank should not require additional secondary containment. A stationary container test certificate is required for tanks with a capacity greater than 500 litres.

Provide automatic fuel shut off in case of fire. Provide a black dipstick to facilitate easy level readings.

Ducting to any buried fuel line shall indicate leaks from a telltale or similar. Provide containment of any leak to prevent ground contamination. Provide twin wall PE (Dura pipe). Underground piping has pressure valve on pipe terminations to allow for pressure testing the interstitial space within the pipe. Include in manuals for annual testing. Do not drain to in-ground sumps.

Do not use galvanized steel or sheet metal tanks, pipes or fittings in any diesel fuel storage, delivery, or fuel system. Do not use copper pipe except where the manufacturer has factory fitted it to the engine. Connections to copper pipe shall use a suitable flexible hose that will not cause work hardening and subsequent brittleness of the copper pipe.

## NOISE LEVELS

Design the generator whether used for emergency purposes only or not, its acoustic enclosure and the building combined to limit noise to the level at the property boundary to comply with the City Plan rules in clause 1.3.3 Noise Standards for all zones outside the Central City or the Banks Peninsula District Plan rules in chapter 33 Noise and Environment Canterbury noise control standards.

Detail service and maintenance access and incorporate acoustically controlled inlet and outlet air louvres in the acoustic enclosure, which could be of a proprietary design.

Specify a residential grade engine silencer and insulate the exhaust pipework, cladding it to at least 3 metres above floor height.

## DOCUMENTATION

Documentation shall include a shortened section describing the basic manual procedures required to test run and to, on attendance to a faulted site, identify the standard procedure for identifying and clearing faults.