# 3 PART SPECIFICATION

##### PRODUCT NAME	  BPS 1 AMP SERIES HARD WIRED POWER SUPPLY

| PART 1 |  |
| --- | --- |
| System Description Basic use Limitations | The Securitron Magnalock Corporation BPS 12-1 and BPS 24-1 One Amp Regulated Adjustable Linear Class 2 DC Power Supplies The BPS-12 and BPS-24 are one Amp units that incorporate a fused AC input and a regulated DC output. A 2.5 Amp current limiting the automatic breaker protects the stand-by batteries from driving into a short circuit. In the event of a DC short, the supply's regulator will go into thermal cutoff, switching off the power. The power supply enclosure is sized large enough to include at least two optional four amp-hour batteries and the unit can charge up to a 20 AH pack (batteries mounted externally). The BPS Series incorporates integral battery charging capability which keeps the sealed lead acid gel/cell at full charge for instantaneous stand-by power in case of line voltage failure. All models in the series are Class 2 rated by UL which means that output wiring need not be run in conduit. |
| References | UL DRQH.E178848 UL FWAX.SA6635 UL ALVY.BP7041 ULC FWAX7.SA6635 ULC EHX7.BP7041 California State Fire Marshall: 3774-0923:102 and 3774-0923:103 City of New York, Dept. of Buildings: MEA251-95E and MEA254-95E City of Cleveland-Board of Building Standards and Building Appeals: S-5-89 US Veteran's Administration: M.P.3 Part III US Department of Defense Listed. ISO 9001. |
| Warranty | SECURITRON MAGNALOCK CORPORATION warrants that it will replace at customer’s request, at any time for any reason, products manufactured and branded by SECURITRON. SECURITRON will use its best efforts to ship a replacement product by next day air freight at no cost to the customer within 24 hours of SECURITRON’s receipt of the product from customer. If the customer has an account with SECURITRON or a valid credit card, the customer may order an advance replacement product, whereby SECURITRON will charge the customer’s account for the price of the product plus next day air freight, and will credit back to the customer the full amount of the charge, including outbound freight, upon SECURITRON’s receipt of the original product from the customer. SECURITRON’s sole and exclusive liability, and customer’s sole remedy, is limited to the replacement of the SECURITRON product when delivered to SECURITRON’s facility (freight and insurance charges prepaid by customer). The replacement, at SECURITRON’s sole option, may be the identical item or a newer unit which serves as a functional replacement. In the event that the product type has become obsolete in SECURITRON’s product line, this MAGNACARE warranty will not apply. This MAGNACARE warranty also does not apply to custom, built to order, or non-catalog items, items made by others (such as batteries), returns for payment, distributor stock reductions, returns seeking replacement with anything other than the identical product, or products installed outside of the United States or Canada. This MAGNACARE warranty also does not apply to removal or installation costs. SECURITRON will not be liable to the purchaser, the customer or anyone else for incidental or consequential damages arising from any defect in, or malfunction of, its products. SECURITRON does not assume any responsibility for damage or injury to person or property due to improper care, storage, handling, abuse, misuse, or an act of God. EXCEPT AS STATED ABOVE, SECURITRON MAKES NO WARRANTIES, EITHER EXPRESS OR IMPLIED, AS TO ANY MATTER WHATSOEVER, INCLUDING WITHOUT LIMITATION THE CONDITION OF ITS PRODUCTS, THEIR MERCHANTABILITY OR FITNESS FOR ANY PARTICULAR PURPOSE. |
| PART 2 |  |
| Manufactured Units Composition Materials | 12 VDC Capacity 24 VDC Capacity Outputs Cabinet Size BPS-12-1 1A BPS-24-1 1A 1 12 x 9 x 4 inches |
| Accessories | Optional CC-8 "slave" board to add eight additional class 2 outputs. |
| Finishes | N/A Part 3 |
| PART 3 |  |
| Installation | Please refer to instruction manual (Securitron part number: 500-10100) Instruction manual can also be found on our website: www.securitron.com |

### POWER SUPPLY 24 VDC:

The power supply shall be produced by an ISO 9001 certified manufacturer.  The power supply shall furnish regulated 24 VDC and shall be U.L. class 2 listed. 1, 4 or  8 separate output circuit breakers shall be provided to divide the load, LED’S shall monitor zone status (voltage no voltage) and slide switches shall be provided to connect or disconnect the load from power.  The power supply shall have the internal capability of charging optional 24 VDC sealed lead acid backup batteries in addition to the operating the DC load.  The power supply shall be supplied complete requiring only 120VAC to the fused input and shall be supplied in an enclosure. The power supply shall be provided with emergency release terminals that allow the release of all devices upon activation of the fire alarm system.

Securitron model BPS-24 series power supply.

### POWER SUPPLY 12 VDC:

The power supply shall be produced by an ISO 9001 certified manufacturer.  The power supply shall furnish regulated 12 VDC and shall be U.L. class 2 listed. 1, 4 or 8 separate output circuit breakers shall be provided to divide the load, LED’S shall monitor zone status (voltage no voltage) and slide switches shall be provided to connect or disconnect the load from power.  The power supply shall have the internal capability of charging optional 12 VDC sealed lead acid backup batteries in addition to the operating the DC load.  The power supply shall be supplied complete requiring only 120VAC to the fused input and shall be supplied in an enclosure. The power supply shall be provided with emergency release terminals that allow the release of all devices upon activation of the fire alarm system.

Securitron model BPS-12 series power supply.

Rev 11-15-01

# Text boxes

SECURITRON SPECIFICATION

BPS 12-1 and BPS 24-1 ONE AMP REGULATED ADJUSTABLE LINEAR CLASS 2 DC POWER SUPPLY