本文档下载自文档下载网，内容可能不完整，您可以点击以下网址继续阅读或下载：

http://www.51wendang.com/doc/437ec10ed908de0667a81455

开利冷冻机

AQUAFORCE&#174;30XW150-400

-Cooled Liquid Chillers

, Start-Up, Operation, Service

Troubleshooting

CONSIDERATIONS. . . . . . . . . . . . . . . . . . . . . . 2GENERAL. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 3-9Conventions Used in This Manual. . . . . . . . . . . . . . . . 3Display Module Usage . . . . . . . . . . . . . . . . . . . . . . . . . . . 3 TOUCH PILOT  DISPLAY

NAVIGATOR  DISPLAY MODULE

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 9-18

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 9General

Base Board (MBB). . . . . . . . . . . . . . . . . . . . . . . . . . 9Compressor Protection Module (CPM) . . . . . . . . . . 10Electronic Expansion Valve (EXV) Board . . . . . . . . 13Minimum Load Valve (MLV)/Condenser Board. . . 15Enable-Off-Remote Contact Switch (SW1). . . . . . . 16http://www.51wendang.com/doc/437ec10ed908de0667a81455Emergency On/Off Switch (SW2) . . . . . . . . . . . . . . . . 16Energy Management Module (EMM). . . . . . . . . . . . . 16Local Equipment Network. . . . . . . . . . . . . . . . . . . . . . . 17Board Addresses. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 17Touch Pilot Display. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 17Control Module Communication. . . . . . . . . . . . . . . . . 17 REDLED GREEN LED YELLOW LED

Comfort Network&#174; (CCN) Interface. . . . . . . 18Remote Alarm and Alert Relays . . . . . . . . . . . . . . . . . 18CONFIGURATION . . . . . . . . . . . . . . . . . . . . . . . . . . . . 18-46Touch Pilot Operation Configuration Tables. . . . . 18Machine Control Methods. . . . . . . . . . . . . . . . . . . . . . . 20Machine On/Off Control . . . . . . . . . . . . . . . . . . . . . . . . . 20 TOUCH PILOT MACHINE CONTROL

NAVIGATOR DISPLAY MACHINE CONTROL

Fluhttp://www.51wendang.com/doc/437ec10ed908de0667a81455id Control Option. . . . . . . . . . . . . . . . . . . 25Cooling Set Point Selection . . . . . . . . . . . . . . . . . . . . . 25 SET POINT OCCUPANCY

Set Point Selection . . . . . . . . . . . . . . . . . . . . . 27Chilled Water Fluid Type Selection . . . . . . . . . . . . . . 27 FRESH WATER

BRINE OR GLYCOL OPERATION

Pump Control. . . . . . . . . . . . . . . . . . . . . . . . . . . . 28 COOLER PUMP CONTROL CONFIRGURATIONSMachine Start Delay. . . . . . . . . . . . . . . . . . . . . . . . . . . . . 29Circuit/Compressor Staging and Loading . . . . . . . 29 CIRCUIT/COMPRESSOR STAGING CIRCUIT/COMPRESSOR LOADING

Load Control. . . . . . . . . . . . . . . . . . . . . . . . . . 30Dual Chiller Control . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 30 DUAL CHILLER CONTROL FOR PARALLEL APPLICATIONS

DUAL CHILLER PUMP CONTROL FOR PARALLEL CHILLER APPLICATIONS

DUAL CHILLEhttp://www.51wendang.com/doc/437ec10ed908de0667a81455R CONTROL FOR SERIES APPLICATIONS

DUAL CHILLER PUMP CONTROL FOR SERIES CHILLER APPLICATIONS

Loading . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 35Temperature Reset. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 35 RETURN WATER RESET

SPACE TEMPERATURE RESET 4-20 mA TEMPERATURE RESET

Limit . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 39 SWITCH CONTROLLED DEMAND LIMIT

EXTERNALLY POWERED CAPACITY BASED DEMAND LIMIT

EXTERNALLY POWERED CURRENT BASED DEMAND LIMIT

CCN LOADSHED CONTROLLED DEMAND LIMITIce Storage Operation. . . . . . . . . . . . . . . . . . . . . . . . . . . 40Broadcast Configuration . . . . . . . . . . . . . . . . . . . . . . . . 40 ACTIVATE

BROADCAST ACKNOWLEDGER

Control . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 42 ALARM ROUhttp://www.51wendang.com/doc/437ec10ed908de0667a81455TING CONTROL ALARM EQUIPMENT PRIORITY

COMMUNICATION FAILURE RETRY TIME RE-ALARM TIME

ALARM SYSTEM NAME

Saving Time Configuration. . . . . . . . . . . . . 42Capacity Control Overrides . . . . . . . . . . . . . . . . . . . . . 42Head Pressure Control. . . . . . . . . . . . . . . . . . . . . . . . . . 45 LOW CONDENSER FLUID TEMPERATURE HEAD PRESSURE CONTROL OPTION

-START-UP. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 46System Check. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 46START-UP. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 46-56Actual Start-Up. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 46Operating Limitations. . . . . . . . . . . . . . . . . . . . . . . . . . . 46 TEMPERATURES VOLTAGE

MINIMUM FLUID LOOP VOLUME FLOW RATE REQUIREMENTS

. . . . . . . . . . . . . . . . . . http://www.51wendang.com/doc/437ec10ed908de0667a81455. . . . . . . . . . . . . . . . 56-63Sequence of Operation. . . . . . . . . . . . . . . . . . . . . . . . . . 56Dual Chiller Sequence of Operation. . . . . . . . . . . . . 56 PUMPOPERATION

Modes. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 56Sensors. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 58 THERMISTORS TRANSDUCERS

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 63-71Economizer Assembly . . . . . . . . . . . . . . . . . . . . . . . . . . 63Electronic Expansion Valve (EXV). . . . . . . . . . . . . . . 63 MAIN EXV CONTROL

ECONOMIZER EXV CONTROL

EXV TROUBLESHOOTING PROCEDURE

Assembly. . . . . . . . . . . . . . . . . . . . . . . . . . 65 COMPRESSOR OIL SYSTEM

reserves the right to discontinue, or change at any time, specifications or designs without notice and without ihttp://www.51wendang.com/doc/437ec10ed908de0667a81455ncurring obligations.

No. 04-53300062-01Printed in U.S.A.Form 30XW-2TPg 17-10

[此处图片未下载成功]

Replaces: 30XW-1T

(cont)

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .68 SUCTION SERVICE VALVE LOW FLUID TEMPERATURE

LOSS OF FLUID FLOW PROTECTION TUBE PLUGGING RETUBING

TIGHTENING COOLER HEAD BOLTS

INSPECTING/CLEANING HEAT EXHANGERS WATER TREATMENT

CircuitCHILLED WATER FLOW SWITCH

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .70 LEAK TESTING

DevicesREFRIGERANT CHARGE

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .70 COMPRESSOR PROTECTIONRelief DevicesCOOLER PROTECTION

PRESSURE RELIEF V . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .ALVES

MAINTENANCE. . . . . . . . . . . . . . . . . . . . http://www.51wendang.com/doc/437ec10ed908de0667a81455. . . . . . . . . . . . . .71Recommended Maintenance Schedule . . . . . . . . . .71TROUBLESHOOTING. . . . . . . . . . . . . . . . . . . . . . . . . 71-88Alarms and Alerts DIAGNOSTIC ALARM CODES AND POSSIBLE  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .71Service TestCAUSES

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .86APPENDIX A — TOUCH PILOT

TABLES . . . . . . . . . . . . . . . . . . . . . . . . . . 89-107APPENDIX B — NAVIGATOR  DISPLAY

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 108-120APPENDIX C — CCN TABLES . . . . . . . . . . . . . . 121-135APPENDIX D — 30XW150-400 CPM

SWITCH ADDRESSES. . . . . . . . . . . . . . . . 136-138APPENDIX E — PIPING AND

. . . . . . . . . . . . . . . . . . . . . .139, 140APPENDIX F — GLOBAL TIME SCHEDULECONFIGURATION FOR i-Vu&#174; DEVICE AND CSMCONTROLLER  . . . . .http://www.51wendang.com/doc/437ec10ed908de0667a81455 . . . . . . . . . . . . . . . . . . . . . . 141-143APPENDIX G — MAINTENANCE SUMMARY

LOG SHEETS . . . . . . . . . . . . . . . . . . . . . . . 144-147INDEX . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .148START-UP CHECKLIST

30XW LIQUID CHILLERS . . . . . . . .CL-1 to CL-7

CONSIDERATIONS

due to system pressures, electrical components, andInstalling, starting up, and servicing this equipment can beequipment location. Only trained, qualified installers and ser-vice technicians should install, start up, and service this equip-ment. When working on this equipment, observe precautions inthe literature, on tags, stickers, and labels attached to the equip-ment, and any other safety precautions that apply. Follow allsafety codes. Wear safety glasses and work gloves. Use care inhandling, rigging, and setting this equipment, and in handlingall electrical cohttp://www.51wendang.com/doc/437ec10ed908de0667a81455mponents.

[此处图片未下载成功]

Electrical shock can cause personal injury and death. Shutoff all power to this equipment during installation and ser-vice. There may be more than one disconnect switch. Tagall disconnect locations to alert others not to restore poweruntil work is completed.

[此处图片未下载成功]

DO NOT VENT refrigerant relief valves within a building.Outlet from relief valves must be vented in accordancewith the latest edition of ANSI/ASHRAE (AmericanNational Standards Institute/American Society of Heating,

[此处图片未下载成功]

Refrigerating and Air Conditioning Engineers) 15 (SafetyCode for Mechanical Refrigeration). The accumulation ofrefrigerant in an enclosed space can displace oxygen andcause asphyxiation. Provide adequate ventilation in

[此处图片未下载成功]

enclosed or low overhead areas. Inhalation of high concen-trations of vapor is harmful and may cause http://www.51wendang.com/doc/437ec10ed908de0667a81455heart irregulari-ties, unconsciousness or death. Misuse can be fatal. Vis heavier than air and reduces the amount of oxygen avail-apor

[此处图片未下载成功]

able for breathing. Product causes eye and skin irritation.

[此处图片未下载成功]

Decomposition products are hazardous.

NOT attempt to unbraze factory joints when servicingthis equipment. Compressor oil is flammable and there isno way to detect how much oil may be in any of the refrig-erant lines. Cut lines with a tubing cutter as required whenperforming service. Use a pan to catch any oil that maycome out of the lines and as a gage for how much oil to addto system. DO NOT re-use compressor oil.

unit uses a microprocessor-based electronic controlsystem. Do not use jumpers or other tools to short outcomponents, or to bypass or otherwise depart from rec-ommended procedures. Any short-to-ground of the con-trol board or http://www.51wendang.com/doc/437ec10ed908de0667a81455accompanying wiring may destroy theelectronic modules or electrical components.

prevent potential damage to heat exchanger tubes,always run fluid through heat exchanger when adding orremoving refrigerant charge. Use appropriate antifreezesolutions in evaporator and condenser fluid loops to pre-vent the freezing of heat exchangers or interconnecting pip-ing when the equipment is exposed to temperatures below32 F (0&#176; C). Proof of flow switch is factory installed on allmodels. Do NOT remove power from this chiller duringwinter shut down periods without taking precaution toremove all water from heat exchangers. Failure to properlyprotect the system from freezing may constitute abuse andmay void warranty.

require specific rotation. Swap any twoincoming power conductors to correct compressor rotation.Do not change factory-installed power wiring at circuitbreakers, comtactors, http://www.51wendang.com/doc/437ec10ed908de0667a81455or compressors.

and troubleshooting information for the 30XW150-400This publication contains controls, operation, start-up, ser-water-cooled liquid chillers with electronic controls. The30XW chillers are equipped with electronic expansion valves. The AquaForceComfortLink  controls and&#174;offer two different user interface devices, the Touch Pilot  30XW chillersdisplay and the Navigator   display.

Used in This Manual — ing conventions for discussing configuration points for theThe follow-Navigator module and Touch Pilot display will be used in thismanual.

names for the Touch Pilot display will be shown innames for the Navigator module will be shown in . See Appendix A for a complete list of point names. ItemSee Appendix B for the complete path name preceding the itembold http://www.51wendang.com. The point and item names in Appendices A and B willbe listed in alhttp://www.51wendang.com/doc/437ec10ed908de0667a81455phabetical order and the path name for each willbe written with the mode name first, then any sub-modes, eachseparated by an arrow symbol (  .

path name will show the user how to navigate through theNavigator module or the Touch Pilot display to reach the desired

[此处图片未下载成功]

[此处图片未下载成功]

item on the screen. The arrow symbol in the path name representspressing  to move into the next level of the menu struc-screen for the Touch Pilot display.

after the point name after an equals sign. If the valueWhen a value is included as part of the point name, it will berepresents a configuration setting, an explanation will beshown in parentheses after the value. The Touch Pilot namewill be shown first with the Navigator name following. As anexample,

(Staged Loading Sequence = 1, LLCS = Circuit A leads).Press the  and

[此处图片未下载成功]

keys simultaneously onthe point name or value. http://www.51wendang.com/doc/437ec10ed908de0667a81455The expanded description is shown in the

[此处图片未下载成功]

Navigator display tables (Appendix B) but will not be shown withthe path names in text. The Touch Pilot display will show an ex-panded description of the point name. To view the expanded point

[此处图片未下载成功]

name for the Touch Pilot display go to Appendix A.

(Carrier Comfort Network

[此处图片未下载成功]

The Touch Pilot display configures the unit via the CCN&#174;pendix C of this manual.

[此处图片未下载成功]

) Tables, which are located in Ap-Display Module Usage

PILOT DISPLAY — The Touch Pilot display is thestandard user interface for the AquaForce 30XW chillers with

[此处图片未下载成功]

the LCD (liquid crystal display) touch screen for display and userComfortLink control system. The display includes a large

[此处图片未下载成功]

configuration, a Start/Stop button, and an Alarm Indicator LED(light-emitting http://www.51wendang.com/doc/437ec10ed908de0667a81455diode). See Fig. 1.

[此处图片未下载成功]

Carrier Comfort NetworkThe Touch Pilot display can be used to access various&#174;

[此处图片未下载成功]

circumstances, contact your Carrier representative.

. For operation under thesedisplays on the touch screen. The Touch Pilot display uses theOperation of the Touch Pilot display is driven from the

[此处图片未下载成功]

following screen “buttons” to allow the user to operate the dis-play and navigate within and between screens.

[此处图片未下载成功]

“BACK” returns to the next higher screen in thehierarchy.

TOUCHSCREEN

-STOPBUTTON

. 1 — Touch Pilot  Display

“HOME” displays the Default Group Display screen

[此处图片未下载成功]

configured display of up to 9 points on each of 8 screens. Thisfor Touch Pilot display. The Default Screen is a user-allows for quick access to various, frequhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ently viewed points,

[此处图片未下载成功]

without navigating through the Main Menu structure. This but-ton is available at all menu levels and returns the user to thefirst Default Group Display screen.

[此处图片未下载成功]

“MAIN MENU” displays the Main Menu screen. Thispossible, of all points supported by the controller. This includes

[此处图片未下载成功]

allows access for viewing and configuration, where

such as set point and operational configuration. Thisbutton is available at all menu levels and returns the user to theMain Menu screen.

[此处图片未下载成功]

“PREVIOUS” moves the user to the next earliertype.

[此处图片未下载成功]

screen in a group of sequential screens of the same

“NEXT” advances the user to the next screen in agroup of sequential screens of the same type.

“OK” agrees with, or says “yes” to a prompt and per-

[此处图片未下载成功]

forms the approprihttp://www.51wendang.com/doc/437ec10ed908de0667a81455ate processing.“NO” rejects, or says “no” to a prompt and performsthe appropriate processing.

[此处图片未下载成功]

“CANCEL” terminates an ongoing action and returnsto the current screen without any other processing.“CLEAR DAdialog box. This button is used to clear incorrect data.TA” clears the data value in a data entry“RESET DAdialog box.

” zeros the data value in a data entry“ADD” adds the active point to a Group Displayscreen.

[此处图片未下载成功]

“REMOVE” deletes a point from a Group Displayscreen.

“INCREASE” modifies the value of a field within itsview up by one item.

limits or “SCROLL UP” shifts the screen

“DECREASE” modifies the value of a field within itsview down by one item.

limits or “SCROLL DOWN” shifts the screen

“PAGE DOWN” will replace the items currently ontable or list has more data than will fit on the screen.

screen with the next ghttp://www.51wendang.com/doc/437ec10ed908de0667a81455roup of items if the current

“PAGE UP” will replace the items currently on thetable or list has more data than will fit on the screen.

with the previous group of items if the current

“FORCE” begins the process of forcing or overridingthe value of a point.

“AUTO” begins the process of removing a force from

[此处图片未下载成功]

a point.

“MODIFY” begins the process of modifying a config-uration value.

“ALARM INDICAnew alarm condition occurs. The alarm indicator lightTOR LIGHT” activates when aactivated until it is manually reset using the Reset button on theLED, located on the right side of the display, remains

menu.

[此处图片未下载成功]

“START/STOP BUTTON” enables the user to startor stop the chiller from the Touch Pilot  display.page 16 for additional information.

Enable-Off-Remote Contact Switch (SW1) on

[此处图片未下载成功]

Passwordhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 dialog box will be displayed for field input of the

[此处图片未下载成功]

Several items are password protected. When required, apassword. The default password is 3333. The password can bechanged if desired.

[此处图片未下载成功]

(initiates communication) to the Main Base Board. The TouchPilot display then shows that controller’s default Group Dis-

[此处图片未下载成功]

play screen. See Fig. 2. This is a user-configured display screenwith up to 9 points on 8 separate screens. For more informationon adding or removing points from the Group Display screen,see the Group Display Screens section on page 7.

will be displayed with expanded information. In the exam-Touch any of the screen point buttons and Point Data Dialogple shown, the CTRL_PNT button in the bottom left cornerwas selected. See Fig. 2 and 3.To exit the box, press .

is the Group Display screen. To access the MainMenu, press the http://www.51wendang.com/doc/437ec10ed908de0667a81455 button. The screen shown in Fig. 4 will bedisplayed. Selecting a button will display the screens associat-ed with that category. The user can also access the login screenfrom the Main Menu if needed.

on the screen. When a button is selected, either a sub-menu or a list of point names and values will be shown. Sub-menus will display a list of associated point names. See Fig. 5for the Touch Pilot menu structure.

the display is the table name. The line and total line counterIf the list of point names and values are shown, the top lineis displayed in the upper right corner of the display. Selectingan item will cause a Point Data dialog box to appear.

— The Setup Menu screen, shown inMenu. This configuration allows the user to configure the basicoperation and look of the display. Table 1 summarizes the Set-up Menu functions.

-XAXQXW

. 2 — Group Display ScreenFig. 3 — Point Data Dialog Box://www.51wendang.com/doc/437ec10ed908de0667a81455par. 4 — Main Menu Display

[此处图片未下载成功]

Fig. 6 — Setup Menu Display

1 — Setup Menu

MENU BUTTONREGIONAL

button specifies the time and date format and the base unit of measure. Time display can be configured as

[此处图片未下载成功]

12-hour AM/PM setting or as a 24-hour setting. The date can be formatted in one of 3 settings, MM-DD-YYYY (Month-Day-Year),  DD-MM-YYYY (Day-Month-Year), or YYYY-MM-DD (Year-Month-Day). Units of measure can be either US (English) or Metric (SI).

button selects the active language and font of the display. Available languages are English and Spanish (Espanol). If a preferred language is not available, additional software for the Main Base Board (MBB) and the Touch Pilot  dis-play are required. Contact your Carrier representative for instructions and software.

button adjusts the LCD contrhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ast. Press and hold the [MOON] button to increase/darken the contrast or the [STAR] button to decrease/lighten the current contrast.

: Touching the screen anywhere for 5 seconds while powering-up will prompt the user to restore contrast and calibration settings to factory defaults.

button specifies whether backlighting should be kept on at all times or turned off during inactive periods.

button is used to adjust the LCD touch screen calibration. Touch the screen in the circular targets located first in the upper left and then in the lower right corner of the screen to adjust.

button is used to configure the limited and full logged-in access system passwords. In order to change passwords, the user must be logged in with full access to view and change the passwords. All passwords must consist of 4-digits, which can be entered using the numeric keypad. Access levels and associated privilegehttp://www.51wendang.com/doc/437ec10ed908de0667a81455s are as follows:

Logged-in Access - Provides the user with read/write access to all available tables (except service configura-tion tables, where the user will not be permitted to modify point data, and Group Display tables, where the user will not be permitted to add points.) This access level also provides read/write access to all Touch Pilot display setup properties except Display, CCN, and Password.

Logged-in Access - Provides user with read/write access to all available tables for the attached device and all Touch Pilot display properties.

the user does not log in, read-only access to all tables is allowed. The user will be prompted to log in when attempting to access password-required functions.

button is used to view the description data and part number from the Ctlr-ID Table and to specify the Operating Mode. The Operating mode can be configured for Equipment mode or Network mhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ode. For Touch Pilot displays that are standard with the unit, Operating mode should not be changed from Equipment mode. Equipment mode provides

only to the chiller’s MBB via the Local Equipment Network (LEN) Bus. For remote access, a remote Touch Pilot display can be set to Network mode. Network mode provides access to all devices on the CCN (Carrier Comfort Net-work&#174;) bus.

: When changing the operating mode, a power cycle is required in order for the new operating mode to take effect. The user should view and correct the following CCN data: address and baud rate, alarm acknowledger, and broadcast acknowledger designation.

button is used to configure the bus and element numbers and the baud rate of the control on the network.

control hasdetermine when alarms occur. The cohttp://www.51wendang.com/doc/437ec10ed908de0667a81455ntrol is factory config-ured for the proper date and is set for the Eastern Time Zone.The date and time zone must be checked and corrected if nec-essary, to allow the machine to function on an internal timeschedule and to display a proper time and date stamp foralarms. The time and date is displayed on the Group DisplayScreen.

change the Time and Date, press the  Main Menubutton. Select

. On the display, a day and date box

[此处图片未下载成功]

with a time box will be shown. To change the day and date,press the day and date box. A calendar will be displayed. If thecorrect month is displayed, touch the correct date. If the wrong

[此处图片未下载成功]

month is displayed, use the  or

change to the correct

[此处图片未下载成功]

month and select the correct date. The date will highlighted.

accept the change. The previous screen will be

with the correchttp://www.51wendang.com/doc/437ec10ed908de0667a81455ted day and date shown. To correct

[此处图片未下载成功]

[此处图片未下载成功]

the time, use the

[此处图片未下载成功]

or

the left to change the hour. Use

[此处图片未下载成功]

or  on the left to change the minutes. Continuously

the  or

sequence the numbers. The time is

[此处图片未下载成功]

shown in a 24-hour format. To accept the changes, press the

[此处图片未下载成功]

or

. A “Save” dialog box is displayed with the

[此处图片未下载成功]

words, “Do you wish to save changes?” Press  to accept

changes.

show status information along the top of the screensand 9 buttons that display 9 point names and point values thatare chosen by the user. All Group Display screen points areuser configurable. The bottom line of the screen contains navi-gation buttons that can be used to move between the GroupDisplay screens.

://www.51wendang.com/doc/437ec10ed908de0667a81455ardialog box. See Fig. 2 and 3. This box contains buttons thatPressing a point button will show that point’s Point Dataremove the point from the group display and apply or remove aforce (point override). When touching any button in the displayscreen, the button will be outlined to acknowledge input. Theremay be a delay in response to input, but if the button is out-lined, do NOT press any other button until the previous inputhas been processed.

Board), all point buttons will be displayed in inverse vid-If there is a communication failure with the MBB (Maineo and the message in the top left line of the screen.

Failure will be displayedDefault Group Designationthe 8 Group Display screens. This is the default screen of the — The default group is the first ofdisplay. Information on this screen as well as the other 7screens can be user-modified to meet the needs of the site.To Add a Point to a Group Displahttp://www.51wendang.com/doc/437ec10ed908de0667a81455ypress the desired menu button (Status, Setpoint, Service, — From the Main Menu,Maint, or Config) and, if necessary, the sub-menu button toaccess the point to be added. Press the point button to show thesource point’s Point Data dialog box. See Fig. 3. From thePoint Data dialog box, press the ADD button. The display willshow the last Group Display accessed. Use the navigation but-tons to access the destination Group Display. Press an existingpoint button or a blank button to update the highlighted buttonwith the source point’s name. Press to add the highlightedpoint to the group and return to the table display.

Remove a Point from a Group DisplayData Dialog box, press the REMOVE button and follow the — From the Pointprompts. The display will return to the Group Display screenfrom which the point was removed, and the button correspond-ing to the deleted point will be blank and disabled.

DISPLAY MODULE — Thehttp://www.51wendang.com/doc/437ec10ed908de0667a81455 Navigator dis-play module provides a mobile user interface to theComfortLink control system. The display has up and down ar-row keys, an  key, and an  key. These keysstructure. Press the  key until ‘Select a Menu Item’ isthe top 11 mode levels indicated by LEDs on the left side of thedisplay. See Fig. 7. See Table 2 and Appendix B for more de-tails about the display menu structure.

within a mode or sub-mode, a “&gt;” indicates thecurrently selected item on the display screen. Pressing the and  keys simultaneously will put themeaning of all sub-modes, items, and their values can be dis-played. Pressing the  and  keys when thethe Navigator module to its default menu of rotating displayitems (those items in Run Status VIEW). In addition, thepassword will be disabled, requiring that it be entered again be-fore changes can be made to password protected items. Pressthe  key to exit out of the expanded text mode.When a specifichttp://www.51wendang.com/doc/437ec10ed908de0667a81455 item is located, the item name appears onthe left of the display, the value will appear near the middle ofthe display and the units (if any) will appear on the far right ofthe display. Press the  key at a changeable item andto change the value, and confirm the value by pressing the key.

item values or testing outputs is accomplished inthe same manner. Locate and display the desired item. Press so that the item value flashes. Use the arrow keys to key to acceptit. Press the Items in the Configuration and Service Test modes are pass-word protected. The words Enter Password will be displayedwhen required, with 1111 also being displayed. The defaultpassword is 0111. Use the arrow keys to change each numberand press  to accept the digit. Continue with thechanged through CCN operator interface software such asComfortWORKS&#174;, ComfortVIEW  and Service http://www.51wendang.comfortLinkNavigatorCarrier

://www.51wendang.com/doc/437ec10ed908de0667a81455play initiates communication with the Main Base Board.This indicates an initialization period while the Navigator Once communication is established, the default rotating dis-play will be shown. If communication is not established, theNavigator module will display:

software loaded, the display will remain at theIf the Navigator module is connected to a Main Base Boardpowered-up initialization display.

control has atermine when alarms occur. The control is factory configuredfor the proper date and for use in the Eastern Time Zone. Thecontrol must be checked and corrected if necessary. The correcttime is important if the machine is to function on an internaltime schedule and display a proper time and date stamp foralarms. The time and date will be displayed on the default ro-tating display of the Navigator module. The time and date canalso be checked and changed underhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 the Time Clock mode asdescribed below.

EXPANSIONPATH

.MM

of Day

ClockTIME

.XX

change the time, press the arrow key to move to the cor-rect hour and press . The minutes can be changed in asimilar manner.

and changed if necessary.

check or change the date, the following items must beITEMITEM EXPANSIONPATH

of YearTime Clock DATEWWDOMDay of MonthTime ClockDATEXXDAY Day of WeekTime Clock DATEYYYEAR

of Century

ClockDATE

: WW is the current month of the controller, (01=January,

=February, etc.).

is the current day of the month

is the day of the week, (01=Monday, 02-TZZ is the year of the century, (06=2006, 07=2007)

, etc.)(metric). The factory default for the units of measure isEnglish. To change the unit of measure, the following itemmhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ust be changed.

EXPANSIONPATH

Display

DISPOFF – English

– SI (Metric)

, Portugues, and Translated. The “Translated” option isnot supported at this time. The factory default language isEnglish. To change the display language, the following itemmust be changed.

EXPANSION

Selection

DISP

: When the Language Selection (Configuration expansions will immediately change to the new language. TheDISP LANG) variable is changed, all appropriate displayfour letter/digit code will not change. No power-off or controlreset is required when reconfiguring languages.

LED Test mode of the device.

EXPANSIONPATH

Display LEDs

DISP

wihttp://www.51wendang.com/doc/437ec10ed908de0667a81455ll access the TEST point. Pressing willPressing  and  simultaneously allows theAdjust Contrast

- - - -  - - - - - - - - - - - - - - -Use the up or down arrows to adjust the contrast. Thescreen’s contrast will change with the adjustment. Press to accept the change. The Navigator module willEquipment Network) bus.

is set to the highest level. To adjust the backlight of theNavigator module, enter the LED Test mode of the device.

EXPANSIONPATHVALUETESTTest Display LED’sConfiguration Mode DISP

will access the TEST point. Pressing willPressing the up and down arrow keys simultaneously allowsthe user to adjust the display brightness. The display will read:Adjust Brightness

- - - - - - - - - - - - - - - - -

the up or down arrow keys to adjust screen brightness.Press

[此处图片未下载成功]

to accept the change. The Navigator module8

2 — ComfortLink  Nhttp://www.51wendang.com/doc/437ec10ed908de0667a81455avigator  Display Menu Structure

Display(VIEW)Starts/Hours(RUN)CompressorRun Hours(HOUR)CompressorStarts(STRT)Fan Run Hours(FAN)CompressorDisable(CP.UN)PredictiveMaintenance(MAIN)

Versions

(VERS)

[此处图片未下载成功]

SERVICESET

ACoolingGeneralCircuit ADisplayTest ModeTemperaturesPressuresSetpointsInputsOutputsConfiguration(TEST)(UNIT)(PRC.A)(COOL)(GEN.I)(CIR.A)(DISP)Test ModeTemperaturesPressuresSetpointsOutputsConfiguration(QUIC)(CIR.A)(PRC.B)(HEAT)(CIR.B)(UNIT)

BCircuit CMisc. Circuit CServiceTemperaturesPressuresSetpointsOutputsConfigurations(CIR.B)(PRC.C)(MISC)(CIR.C)(SERV)Circuit CGeneralOptionsTemperaturesOutputsConfiguration(CIR.C)(GEN.O)(OPTN)

,Demand Limit,Master/Slave(RSET)

of DayOperatingReset Current(http://www.51wendang.com/doc/437ec10ed908de0667a81455TIME)Control TypeAlarms

(SLCT)(R.ALM)

(DATE)ModesAlarms

(MODE)(ALRM)

1Alarm(SCH1)History

(H.ALM)

2(SCH2)Holidays(HOLI)ServiceMaintenanceConfiguration(MCFG)

ComfortLink  electronic control system that controls andmonitors all operations of the chiller. The control system iscomposed of several components as listed in the following sec-tions. All machines have a Main Base Board (MBB), Touch Pi-lot  module or Navigator  device, electronic expansionvalve board (EXV), auxiliary board, Compressor Protectionboard, Emergency On/Off switch, and an Enable-Off-RemoteContact switch.

ComfortLink control system. It contains the major portionof operating software and controls the operation of the

— The 30XW water-cooled liquid chillers contain

Base Board (MBB) — The MBB is the core of

. See Fig. 8. The MBB continhttp://www.51wendang.com/doc/437ec10ed908de0667a81455uously monitors input/output channel information received from its inputs and fromall other modules. The MBB receives inputs from status andfeedback switches, pressure transducers and thermistors. TheMBB also controls several outputs. Some inputs and outputsthat control the chiller are located on other boards, but aretransmitted to or from the MBB via the internal communica-tions bus. Information is transmitted between modules via a3-wire communication bus or LEN (Local Equipment Net-work). The CCN (Carrier Comfort Network&#174;) bus is also sup-ported. Connections to both LEN and CCN buses are made atTB3. For a complete description of Main Base Board inputsand outputs and their channel identifications, see Table 3.

3 — Main Base Board Inputs and Outputs

/OUTPUT

/O TYPE

MODULE POINT NAME

POINTPinNotationMBB-J1, MBB-J1A,

-J1B

://www.51wendang.com/doc/437ec10ed908de0667a81455r1124 vac12GroundMBB-J9A, MBB-J9B, MBB-J9C, MBBJ9D RS485 Port (D )GRS485 Port (Gnd)-RS485 Port (D-)MBB-J12 RS485 Port (D )GRS485 Port (Gnd)-RS485 Port (D-)MBB-J5B-CH1717

-J4-CH1316AMBB-J5A-CH16A

-J7A-CH65V 5 vdc Ref.SSignalRReturn

-J7C-CH85V 5 vdc Ref.SSignalRReturn

-J6-CH3MBB-J4-CH12MBB-J4-CH14

-J6-CH2MBB-J6-CH1MBB-J6-CH5MBB-J6-CH4MBB-J4-CH15AMBB-J7B-CH7

5 vdc Ref.SignalReturn

-J7D-CH95V 5 vdc Ref.SSignalRReturn

-J4-CH11MBB-J3-CH24MBB-J3-CH25MBB-J2A-CH19MBB-J2A-CH20MBB-J2C-CH225VSR

-J5C-CH18

(24 vac supply)———

Equipment Network———

Communication

———

Water Flow SwitchDemand Limit Switch No. 1Condenser Flow SwitchCircuit A Discharge Pressure Transducer

Limit SW1

Transducer

Flohttp://www.51wendang.com/doc/437ec10ed908de0667a81455w Switch, LOCKLimit Switch 1 Status, DLS1Condenser Flow Switch, CONDDischarge Pressure, DP.A

B Discharge Pressure TransducerDual Chiller LWT ThermistorDual Set Point InputHeat/Cool Switch

Water ThermistorLeaving Water ThermistorCondenser Entering Water

Leaving Water

Chilled Water Pump InterlockCircuit A Suction Pressure Transducer

TransducerDischarge Pressure, DP.B

Set PointHC_SWEWTLWTCEWTCLWTPMPI

k Thermistor

k Thermistor5k Thermistor5k Thermistor5k Thermistor

Temperature, CHWSRemote Setpoint Switch, DUALHeat/Cool Select Contact, HC_SW

Entering Fluid, EWTCooler Leaving Fluid, LWTCondenser Entering Fluid, CEWTCondenser Leaving Fluid, CLWTElectrical Box Interlock, ELEC

TransducerSuction Pressure, SP.A

B Sucthttp://www.51wendang.com/doc/437ec10ed908de0667a81455ion Pressure TransducerUnit StatusAlarm RelayAlert Relay

Pump Relay 1Cooler Pump Relay 2Condenser Pump RelayPump #1 InterlockPump #2 Interlock

Contact-Off-Enable

RALT RPMP1PMP2CPMPPMP_1PMP_2

Transducer

Pressure, SP.BOn/Off Remote Switch, ONOFAlarm Relay Output, ALRMAlert Relay Output, ALRTCooler Pump 1, CPUMP_1Cooler Pump 2, CPUMP_2Condenser Pump, COND_PMPCooler Pump Run Status, PUMP

/O—Input or Output

—Leaving Water Temperature

one CPM per compressor. See Fig. 9. The device controls thecompressor contactors, oil solenoid, and loading/unloading thesolenoid. The CPM also monitors the compressor motor tem-perature, high pressure switch, oil level switch, discharge gastemperature, oil pressure transducer, motor current, MTA(must trip amps) setting and economizer preshttp://www.51wendang.com/doc/437ec10ed908de0667a81455sure transducer(sizes 175-300, 350, 400 only). The CPM responds to com-mands from the MBB (Main Base Board) and sends the MBBthe results of the channels it monitors via the LEN (Local

Protection Module (CPM) — There

Network). The CPM has three DIP switch inputbanks, Switch 1 (S1), Switch 2 (S2), and Switch 3 (S3). TheCPM board DIP switch (S1) configures the board for the typeof starter, the location and type of the current transformers andcontactor failure instructions. See Table 4 for description ofDIP switch 1 (S1) inputs. See Appendix D for DIP switchsettings.

4 — DIP Switch 1 (S1) Inputs

SWITCH POSITION

Configuration

Transformer (CT) Position

, 3

(2), OFF (3)ON (2), OFF (3)OFF (2), ON (3)ON (2), ON (3)

(4), OFF (5), OFF (6)ON (4), OFF (5), OFF (6)OFF http://www.51wendang.com/doc/437ec10ed908de0667a81455(4), ON (5), OFF (6)ON (4), ON (5), OFF (6)OFF (4), OFF (5), ON (6)ON (4), OFF (5), ON (6)OFF (4), ON (5), ON (6)ON (4), ON (5), ON (6)OFFON

—

-the-line StartWye-Delta Start

is located in the main line

is located in the Delta of the motorReserved for future use

; will cause MTA configuration alarm100A/1V CT1100A/0.503V CT2100A/0.16V CT3

; will cause MTA configuration alarmInvalid; will cause MTA configuration alarmInvalid; will cause MTA configuration alarmInvalid; will cause MTA configuration alarmInvalid; will cause MTA configuration alarmAll units should be off

when Shunt Trip is available in the unit

—

Transformer (CT) Selection

, 5, 6

Failure ActionNot Used

CPM board DIP switch S2 setting determines the musttrip amps (MTA) setting. See Appendix D for DIP switch set-tinhttp://www.51wendang.com/doc/437ec10ed908de0667a81455gs. The MTA setting which is calculated using the settingsS2 must match the MTA setting in the software or an MTAalarm will be generated.

below for CPM board DIP switch S3 address informa-tion. See Table 5 for CPM inputs and outputs.

-A DIP Switch 3

:CPM-B DIP Switch 3

:

OFF1OFF

OFF2OFF

OFF3ON

OFF4OFF

[此处图片未下载成功]

11

Table 5 — Compressor Protection Module Inputs and Outputs*

(24 vac supply)

/OUTPUT

—

/O TYPE

—

MODULE POINT NAME

—

POINTPinNotation

-X-J11124 vac12Ground

-X-JP121RS485 Port (D )2RS485 Port (Gnd)3RS485 Port (D-)

-X-J121RS485 Port (D )2RS485 Port (Gnd)3RS485 Port (D-)CPM-X-J7-CH0512

-X-J6-CH06

Level Switch

LS X

X Oil Solenoid, OLS.X://www.51wendang.com/doc/437ec10ed908de0667a81455ar

Trip Amps

(S2)

-Pin DIP Switch

Trip Amps, MTA.X

Equipment Network———

X High Pressure SwitchHPS-XSwitchNot available

Switch S18-Pin DIP SwitchS1 Config Switch, C.SW.X

-X-J9-CH01

X Motor TemperatureMTR-XNTC ThermistorMotor Temperature, CTP.X

-X-J9-CH02

X Discharge Gas TemperatureDGT XNTC ThermistorDischarge Gas Temp, DGT.X

-X-J10B-CH045V

5 vdc refSignalReturn

-X-J10A

5 vdc refSignalReturn

-X-J8-CH01

Pressure TransducerOPT XPressure TransducerOil Pressure, OP.X

V

Pressure Transducer(sizes 175,200,350,400 only)

XPressure TransducerEconomizer Pressure, ECP.X

Current X Phase ACurrent SensorCUR.A

-X-J8-CH02

://www.51wendang.com/doc/437ec10ed908de0667a81455or Current X Phase BCurrent SensorCUR.B

-X-J8-CH3

Current X Phase CCurrent SensorCUR.C

-X-J1-CH07

X 1M ContactorC X 1MContactorCompressor Output, CP.X

-X-J2-CH812

-X-J2-CH912

-X-J2-CH1212

-X-J2-CH131

-X-J2-CH1412

X 2M ContactorC X 2MContactorNot available

X S ContactorC X SContactorNot available

Solenoid XLoad Solenoid XUnload Solenoid X

*“X” denotes the circuit, A or B. See Appendix D for MTA settings.

solenoid-XLoading Solenoid-XUnloading Solenoid-X

Solenoid Output, OLS.XSlide Valve 1 Output, SL1.XSlide Valve 2 Output, SL2.X

Electronic Expansion Valve (EXV) Board —

30XW150-325 units have one EXV board. The30XW350,400 units have one EXV board per circuit.http://www.51wendang.com/doc/437ec10ed908de0667a81455 SeeFig. 10. The board is responsible for monitoring the suction gastemperature and economizer gas temperature thermistors. Theboard also signals the main EXV and economizer EXV(ECEXV) motors to open or close. The electronic expansionvalve board responds to commands from the MBB and sendsthe MBB the results of the channels it monitors via the LEN(Local Equipment Network). See below for DIP switch infor-mation. See Tables 6 and 7 for EXV inputs and outputs.

BOARD 1 (150-400) DIP SWITCHAddress:EXV BOARD 2 (350,400) DIP SWITCHAddress:

ON3

ON6

OFF7

ON8

[此处图片未下载成功]

13

Table 6 — EXV1 Board Inputs and Outputs (30XW150-325)

(24 vac supply)

/OUTPUT

—

/O TYPE

—

MODULE POINT NAME

—

POINTPinNotation

://www.51wendang.com/doc/437ec10ed908de0667a81455A-J1

vac12Ground

-J41RS485 Port (D )2RS485 Port (Gnd)3RS485 Port (D–)

-J3

-J3

-J2A1234

-J2B1234

Equipment Network———

A Suction Gas ThermistorSGTA5k ThermistorCompressor Suction Temp, SGT.A

B Suction Gas ThermistorSGTB5k ThermistorCompressor Suction Temp, SGT.B

A EXVEXV-AStepper MotorEXV Position, EXV.A

B EXV(size 325 only)

-BStepper MotorEXV Position, EXV.B

7 — EXV1,2 Board Inputs and Outputs* (30XW350,400)

(24 vac supply)

/OUTPUT

—

/O TYPE

—

MODULE POINT NAME

—

POINTPinNotation

-J11124 vac12Ground

-J41RS485 Port (D )2RS485 Port (Gnd)3RS485 Port (D–)

-J3

-J3

-J2A1234

-Jhttp://www.51wendang.com/doc/437ec10ed908de0667a814552A1234

Equipment Network——

—

X Suction Gas ThermistorSGT X5k ThermistorCompressor Suction Temp, SGT.X

X Economizer Gas ThermistorECT X5k ThermistorEconomizer Gas Temp, ECT.X

X EXVEXV-XStepper MotorEXV Position, EXV.X

X Economizer EXVECEXV-XStepper MotorCir X Economizer EXV Pos, ECO.X

*“X” denotes the circuit: 1 = Circuit A; 2 = Circuit B.

Minimum Load Valve (MLV) / CondenserBoard — One auxiliary board is optionally installed in each

. See Fig. 11. The auxiliary board contains an analog outputfor head pressure control and discrete outputs for minimumload control. The auxiliary board responds to commands fromthe MBB and sends the MBB the results of the channels itmonitors via the Local Equipment Network (LEN). See below

auxiliary board A, B and C DIP switch addresses. See Table8 for inputs and outputs.

://www.51wendang.com/doc/437ec10ed908de0667a81455[此处图片未下载成功]

AUX BOARD DIP SWITCHAddress:

(24 vac supply)

/OUTPUT

—

/O TYPE

—

MODULE POINT NAME

—

POINTPinNotation

-J1

vac12Ground

-J9

RS485 Port (D )GRS485 Port (Gnd)-RS485Port(D-) RS485 Port (D )GRS485 Port (Gnd)-RS485Port(D-)AUX-CH9 Signal-Ground

-J2-CH3AUX-J2-CH4

Equipment Network———

Head Pressure Control

Signal

Load Valve AMinimum Load Valve B

_AMLV-AMLV-B

-10 VDCSolenoidSolenoid

Press Actuator Pos, SPD.AMinimum Load Valve Circuit A,

.A

Load Valve Circuit B,

.B

Enable-Off-Remote Contact Switch (SW1) —

switch is installed in alhttp://www.51wendang.com/doc/437ec10ed908de0667a81455l units and provides the owner andservice person with a local means of enabling or disabling themachine. It is a 3-position switch and it is used to control thechiller. When switched to the Enable position, the chiller willbe under its own control. When switched to the Off position,the chiller will shut down. When switched to the Remote Con-tact position, a field-installed dry contact can be used to startthe chiller. The contacts must be capable of handling a 24-vac,50-mA load. In the Enable and Remote Contact (dry contactsclosed) positions, the chiller is allowed to operate and respondto the scheduling configuration, CCN configuration, and setpoint data.

units with a Touch Pilot  display, the position of theEnable/Off/Remote contact switch is ignored except when theRemote Mode operating type is selected. Refer to the MachineControl Methods section on page 20 for more details.

Management Module (EMM) — The EMhttp://www.51wendang.com/doc/437ec10ed908de0667a81455M

available as a factory-installed option or as a field-installedaccessory. See Fig. 12. The EMM receives 4 to 20 mA inputsfor the temperature reset, cooling set point and demand limitfunctions. The EMM also receives the switch inputs for thefield-installed second stage 2-step demand limit and ice donefunctions. The EMM communicates the status of all inputswith the MBB, and the MBB adjusts the control point, capacitylimit, and other functions according to the inputs received. SeeTable 9.

[此处图片未下载成功]

Care should be taken when interfacing with other manufac-turer’s control systems due to possible power supply differ-ences, full wave bridge versus half wave rectification,which could lead to equipment damage. The two differentpower supplies cannot be mixed. ComfortLink  controlsuse half wave rectification. A signal isolation device shouldbe utilized if incorporating a full wave bridge rectifier sihttp://www.51wendang.com/doc/437ec10ed908de0667a81455g-nal generating device is used.

[此处图片未下载成功]

Emergency On/Off Switch (SW2) — This switch is

in all units. The Emergency On/Off switch shouldonly be used when it is required to shut the chiller off immedi-ately. Power to all modules is interrupted when this switch isoff and all outputs from these modules will be turned off.

Table 9 — Energy Management Module (EMM) Inputs and Outputs

/OUTPUT4-20 mA Demand Limit4-20 mA Temperature Reset/Cooling SetpointDemand Limit SW2Ice Done

Override Remote Lockout SwitchSPT

% Total CapacityRUN R

[此处图片未下载成功]

SHD RCA_SCB_S

-20 mA Demand Limit

-20 mA Temperature Reset/ Cooling Set pointDemand Limit Step 2Ice Done Switch

Schedule OverrideChiller Lockout

Temperature ThermistorPercent Total Capacity OutputRun Relay

Relay

://www.51wendang.com/doc/437ec10ed908de0667a81455parRun Status for Circuit ARun Status for Circuit B

/O TYPE4-20 mA*4-20 mA*Switch InputSwitch InputSwitch InputSwitch Input10k Thermistor0-10 vdcRelayRelayRelayRelay

MODULE POINT NAMELimit 4-20 mA Signal, DMD

/Setpnt 4-20 mA Signal, RSETSwitch Limit Setpoint 2, DLS2Ice Done Storage Switch, ICE.DOccupied Override Switch, OCCSRemote Interlock Switch, RLOCOptional Space Temp, SPTChiller Capacity Signal, CATORunning Status, RUN

Indicator State, SHUT

A Run Status, Q_RUN_ACompressor B Run Status, Q_RUN_B

POINTEMM-J7B-CH6EMM-J7A-CH5EMM-J4-CH9EMM-J4-CH11AEMM-J4-CH8EMM-J4-CH10EMM-J6-CH2EMM-J8-CH7EMM-J3-CH25EMM-J3-CH24EMM-J2A-CH17EMM-J2A-CH18

* A field-supplied 1/2 watt 250 ohm resistor is required across terminals TB6-1,2 (CH6) and/or TB6-3, 4 (CH5).

Equipment Network — Information is trans-mitted between modules via a 3-wire communicatihttp://www.51wendang.com/doc/437ec10ed908de0667a81455on bus orLEN (Local Equipment Network). External connection to theLEN bus is made at TB3.

Addresses — All boards (except the Main BaseBoard and Energy Management Module Board) have8-position DIP switches.

Pilot  Display — The Touch Pilot display portControl Module Communication

LED — Proper operation of the control boards can bevisually checked by looking at the red status LEDs (light-emitting diodes). When operating correctly, the red statusLEDs will blink in unison at a rate of once every 2 seconds. Ifthe red LEDs are not blinking in unison, verify that correctpower is being supplied to all modules. Be sure that the MainBase Board (MBB) is supplied with the current software. Ifnecessary, reload current software. If the problem still persists,replace the MBB. A red LED that is lit continuously or blink-ing at a rate of once per second or faster indicates that the boardshould be replaced.

://www.51wendang.com/doc/437ec10ed908de0667a81455REEN LED — All boards have a green LEN (SIO) LEDwhich should be blinking whenever power is on. If the LEDsare not blinking as described check LEN connections forconnections are shown in Table 10. Wiring is shown in Fig. 13.

communication errors at the board connectors. Seeinput/output Tables 3-10 for LEN connector designations. A3-wire bus accomplishes communication between modules.These 3 wires run in parallel from module to module. The J9A

on the MBB provides communication directly to theNavigator  display module.YELLOW LED — The MBB has one yellow LED. The

Comfort Network&#174; (CCN) LED will blink during times

network communication.

10 — Touch Pilot  Display Port

(Power)

VAC 24VAC-Earth GroundRS485 Port (D )RS485 Port (GND)RS485 Port (D-)24VAC( )

Port (D )RS485 http://www.51wendang.com/doc/437ec10ed908de0667a81455Port (GND)Unused (no connect)RS485 Port (D-)24VAC(-)

(COM1)

(RJ11)

. 13 — Touch Pilot  Display Wiring

Carrier Comfort Network&#174; (CCN) Interface —

30XW units can be connected to a CCN system, if desired.The communication bus wiring is a shielded, 3-conductor cablewith drain wire and is field supplied and installed. The systemelements are connected to the communication bus in a daisychain arrangement. The positive pin of each system elementcommunication connector must be wired to the positive pins ofthe system elements on either side of it. The negative and sig-nal ground pins of each system element must also be wired inthe same manner. Wiring connections for CCN should be madeat TB3. Consult the CCN Contractor’s Manual for further in-formation. See Fig. 14.

: Conductors and drain wire must be 20 AWG (Ameri-can Wire Gage) minimum stranded, tinned copper. Individhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ualconductors must be insulated with PVC, PVC/nylon, vinyl,Teflon, or polyethylene. An aluminum/polyester 100% foilshield and an outer jacket of PVC, PVC/nylon, chrome vinyl,or Teflon with a minimum operating temperature range of–20 C to 60 C is required. See Table 11 for recommended wiremanufacturers and part numbers.

11 — CCN Communication Bus Wiring

NUMBER

WiringPlenum Wiring

—A21451A483018205884421D6451—M13402M644306130—

.Cut the CCN wire and strip the ends of the red ( ), white

(ground), and black (–) conductors. (Substitute appropri-ate colors for different colored cables.)

.Connect the red wire to ( ) terminal on TB3 of the plug,the white wire to COM terminal, and the black wire to the(–) terminal.

.The RJ14 CCN connector on TB3 can also be used, but isonly intended for temporahttp://www.51wendang.com/doc/437ec10ed908de0667a81455ry connection (for example, alaptop computer running Service Tool).IMPORTANT: A shorted CCN bus cable will preventsome routines from running and may prevent the unitfrom starting. If abnormal conditions occur, discon-nect the CCN bus. If conditions return to normal,check the CCN connector and cable. Run new cable ifnecessary. A short in one section of the bus can causeproblems with all system elements on the bus.

[此处图片未下载成功]

Remote Alarm and Alert Relays  —  The 30XW

can be equipped with a remote alert and remote alarmannunciator contacts. Both relays connected to these contactsmust be rated for a maximum power draw of 10 va sealed,25 va inrush at 24 volts. The alarm relay, indicating that thecomplete unit has been shut down, can be connected to TB5-12and TB5-13. Refer to unit wiring diagrams. For an alert relay,indicating that at least 1 circuit is off due to the alert, a field-supplied and installed rhttp://www.51wendang.com/doc/437ec10ed908de0667a81455elay must be connected between MBB-J3-CH25-3 and TB5-13. The action of the alarm and alert re-lays can be reversed from normally open to normally closed byusing the Reverse Alarms Relay configuration (ReverseAlarms Relay, RV.AL).

is important when connecting to a CCN communicationbus that a color-coding scheme be used for the entire networkto simplify the installation. It is recommended that red be usedfor the signal positive, black for the signal negative, and whitefor the signal ground. Use a similar scheme for cables contain-ing different colored wires.

each system element, the shields of its communicationbus cables must be tied together. If the communication bus isentirely within one building, the resulting continuous shieldmust be connected to a ground at one point only. If the commu-nication bus cable exits from one building and enters another,the shields must be connected to grounds at the lightningsuppresshttp://www.51wendang.com/doc/437ec10ed908de0667a81455or in each building where the cable enters or exits thebuilding (one point per building only). To connect the unit tothe network:

.Turn off power to the control box.

information entered in the following configura-tion tables. These tables are accessible by using Network Ser-vice Tool or ComfortVIEW  software. The tables are theCtrlID (Controller Identification) configuration table and theUSERCONF (User Configuration) table. See Tables 12 and 13.NOTE: Always perform an Upload to obtain the latest config-uration before making configuration table changes.

Pilot  Operation ConfigurationTables — The Touch Pilot display operation is controlled by

Table 12 — Touch Pilot Controller Identification Configuration Table

ID DATA

NameLocal addressBus numberDevice (driver) typePrimary baud rateSecondary baud rateDevice descriptionDevicehttp://www.51wendang.com/doc/437ec10ed908de0667a81455 locationSoftware part numberModel numberSerial number

number

address processing list (primary)Broadcast address processing list (secondary)

NO.

AND RANGE

character Name field1150

= Non-bridge

= Broadcast Acknowledger3840038400

Chiller Display24 character text field(Blank)

character text fieldCESR-131363-01(Blank)(Blank)Version 1.0

-251, 254, 255 enabled241-255 enabled/disablednone

DefaultFixedDefaultOptionalDefaultOptionalFixedFixedFixedFixedDefaultsOptional

applicable

13 — Touch Pilot  User Configuration (USERCONF) Table

always on?Full access passwordLimited access passwordActive languageTime formatDate formatUnits baseContrast controlNetwork modeNetwork shttp://www.51wendang.com/doc/437ec10ed908de0667a81455ettingsAlarm acknowledgerBroadcast acknowledgerEquipment CCN addressBus numberElement numberControl variables

status (Not Used)Equipment start/stop (Not Used)Alarm status (Not Used)Alarm reset (Not Used)

8Namechar 8Namechar 8Namechar 8

USEDNOT USEDNOT USEDNOT USED

0102USMetricManualAutoDisableEnable

USAutoDisable

ALWAYS ON? — This configuration is usedto keep the backlight on continuously or to turn it off after 60seconds with no activity.

Entries: No/Yes (No=0 or Yes=1)Default Value:      NoFULL ACCESS PASSWORD — This configuration is usedto specify the full access pahttp://www.51wendang.com/doc/437ec10ed908de0667a81455ssword. Refer to Table 1, SetupMenu, for additional information on passwords.Allowable Entries:0 through 9999Default Value:3333

LIMITED ACCESS PANEL — This configuration is used  tospecify the limited access password.Allowable Entries:0 through 9999Default Value:2222

LANGUAGE — This configuration is used to spec-ify the display’s active language. All translatable text will bedisplayed in this language.

Entries:0 (English), 1 (alternate, installed by user)Default Value:0

FORMAT — This configuration is used to specify theformat for display of time.

Entries:0 = H:MM AM/PM without leading zero

= HH:MM with leading zero whennecessary

Value: 0

FORMAT — This configuration is used to specify theformat for display of date.

Entries:0 = MM-DD-YYYY with leading zero

necessary

= DD-MM-YYYY with lhttp://www.51wendang.com/doc/437ec10ed908de0667a81455eading zero when necessary2 = YYYY-MM-DD

Value: 0

BASE — This configuration is used to specify the for-mat of the units of measure.Allowable Entries:U.S.

Value: U.S.

CONTROL — This configuration is used to en-able or disable the display’s auto contrast adjustment feature.When enabled, the display’s contrast will be automatically ad-justed as required, based on temperature.Allowable Entries:Manual

(Auto Contrast Adjustment Disabled)Auto

(Auto Contrast Adjustment Enabled)

Value: Auto

display’s operating mode. For additional information on oper-MODE — This configuration is used to set theating mode, refer to cision will be ignored and the mode will default to EquipmentDisplay in the Table Setup Menu. This de-when the display is connected to a device (the LEN Bus).

: A power cycle is required for this decision thttp://www.51wendang.com/doc/437ec10ed908de0667a81455o takeeffect.

Entries:Disable = Equipment Mode

= Network Mode

Value: Disable

ACKNOWLEDGER — This configuration is usedto specify whether the Touch Pilot  display will act as thealarm acknowledger for the CCN. There can be only one alarmacknowledger per CCN. Therefore, if another CCN devicesuch as ComfortVIEW  software, the Autodial Gateway orTeLINK is already set as the alarm acknowledger for the CCNnetwork then this decision should be set to No.

: The display must be in Network mode and connectedto the primary CCN bus and this decision set to acknowledgement to be enabled.Yes for alarmAllowable Entries:No

Value: No

ACKNOWLEDGER — This is used  to indicate whether the Touch Pilot display will act asconfiguration

broadcast acknowledger for its CCN bus. There can be onlyone broadcast acknowledger per CCN bus.

://www.51wendang.com/doc/437ec10ed908de0667a81455parNOTE: The display must be in Network mode and this deci-sion set to Yes for broadcast acknowledgement to be enabled.Allowable Entries:No

Value: No

CCN ADDRESS  —  mode (USERCONF Table’s Network Mode decision is set toWhen in equipmentDisablused to specify the CCN address of the piece of equipment toe), the Bus Number and Element Number decisions arecommunicate with. An Attach or power cycle must beperformed for changes to take effect. These decisions will beignored when the display is connected to the LEN bus or inNetwork mode. In Network mode, specify the bus and elementnumber of the equipment communicate with using the dis-play’s Attach function.

: In Network mode, these configurations will be over-written with the default device address if it is changed throughthe Attach process.

NUMBER — This configuration is used  to specify theEquipment Controller bus number.Alhttp://www.51wendang.com/doc/437ec10ed908de0667a81455lowable Entries: 0 through 239Default Value: 0

NUMBER — This configuration is used to speci-fy the Equipment Controller element number.Allowable Entries: 1 through 239Default Value: 1trol how the machine operates. These variables control theMachine Control Methods — Three variables con-

-Off function, set point operation, and Heat-Cool operation.

On/Off Control — depends on which interface display is used. The control is dif-Machine On/Off controlferent for Touch Pilot  or Navigator  displays. Select thecorrect configuration procedure below based on which inter-face is being used.

PILOT MACHINE CONTROL — Machine On/Offcontrol is determined locally by pushing the Start/Stop buttonon the Touch Pilot display. Pressing this button will cause the

[此处图片未下载成功]

Equipment Start screen to be displayed. See Fig. 15.

. 15 — Equipment Start Screen

Tabhttp://www.51wendang.com/doc/437ec10ed908de0667a81455le 14 summarizes the unit control type and stop or gostatus with regard to the following parameters:

Operating type: this is selected by using the start/stop buttonon the front of the user interface.

Remote start/stop contacts: these contacts are used when theunit is in remote operating type (Remote mode).

CHIL_S_S: this network command variable relates to thechiller start/stop when the unit is in CCN control (CCNmode). When this variable forced to Disable, then the unit isstopped. When this variable is forced to Enable, then theunit runs in accordance with schedule 1.

Start/Stop schedule: occupied or unoccupied status of theunit as determined by the chiller start/stop program (Sched-ule 1).

Master control type: This parameter is used when the unit isthe master unit in a two chiller lead/lag arrangement. Themaster control type determines whether the unit is to becontrolled locally, remotely or http://www.51wendang.com/doc/437ec10ed908de0667a81455through CCN (this parameteris a Service configuration).

CCN emergency shutdown: if this CCN command is acti-vated, it shuts the unit down whatever the active operatingtype.

General alarm: the unit is totally stopped due to failure.Start screen will be displayed. Select Local On. The controlwill ignore the position of Enable/Off/Remote Contact switchand all CCN network force commands, except an EmergencyStop Command. The Run Status variable, indicating the cur-rent status of the machine, will change to RUNNING, DELAYor READY. The Chiller Occupied? variable will change toYES. The Control Type variable indicates the type of control.For this configuration, Control Type will be Local. The Oper-ating Type variable will change to L-On (Local On).

Start screen will be displayed. Select Local Sched-ule. The unit will start and stop according to the schedule de-fined in the Time Schedule menu. Two Internal Timehttp://www.51wendang.com/doc/437ec10ed908de0667a81455 Sched-ules are available and must be field programmed. TimeSchedule 1 is used for single set point On-Off control. Time

OPERATING TYPE

_S_SStart/StopOffOnScheduleModeModeModeVariable

----------------Active---------Active--------Active---Off---Active--------Active-Off-----Active--------Active-------Active-Off

-----Active-------ActiveOff------Active---Active--------Active--------Active---On Cool

----Active-On------Active-------Active-On Cool

-----ActiveOn-

2 is used for Dual Set Point/Occupied-Unoccu-pied set point control. The control will ignore the position of

/Off/Remote Contact switch and all CCN network forcecommands, except the Emergency Stop Command.

Run Status variable will indicate the current status ofthe machine — OFF, RUNNING, DELAY, or READY. TheChiller Occupied? variablehttp://www.51wendang.com/doc/437ec10ed908de0667a81455 will indicate the occupied state ofthe machine according to Time Schedule 1 and will be eitherYES (occupied) or NO (unoccupied). The Control Type vari-able will indicate the type of control. For this configuration,Control Type will be Local. The Operating Type variablewill change to L-Sched (Local Schedule).

schedules consist of 8 user-configurable occupied timeperiods. The control supports time schedules for local control,remote control, and ice building. These time periods can beflagged to be in effect or not in effect on each day of the week.The day begins at 00.00 and ends at 24.00. The machine will bein unoccupied mode unless a scheduled time period is in effect.If an occupied period extends past midnight, the occupiedperiod will automatically end at 24:00 hours (midnight) and thenew occupied period must be programmed to begin at 00:00hours.

the following example, the occupied period starts at 6:00AM, Mondahttp://www.51wendang.com/doc/437ec10ed908de0667a81455y through Friday and 10:00 AM on Saturday andSunday. The occupied time ends at 6:30 PM on Mondaythrough Friday and 2:00 PM on Saturday and Sunday. SeeFig. 16.

: This schedule was designed to illustrate the program-ming of the schedule function and is not intended as arecommended schedule for chiller operation.

the chiller is to be controlled to a single set point, useSchedule 1 (OCCPC01S). This will start and stop the machine.During the unoccupied times, the chiller will be off. If the chill-er is to be controlled to 2 set points, occupied and unoccupied,use Schedule 2 (OCCPC02S). This will cause the chiller tocontrol to an occupied set point and an unoccupied set point.The machine will be able to provide cooling at any time.

configure this option on the Touch Pilot  display seeTable 15.

14 — Touch Pilot  Start/Stop Control

STATUS

/StopCCN

Uhttp://www.51wendang.com/doc/437ec10ed908de0667a81455nitGeneralTYPEScheduleEmergencyControl TypeAlarm

--Active-----Yes-----Local

-Unoccupied--Local

----Remote

-Unoccupied--Remote

----CCN

----CCN

--LocalRemote---RemoteRemoteUnoccupied--RemoteCCN---CCNCCNUnoccupied--CCN--DisabledNoLocal

-OccupiedDisabledNoLocal

-OccupiedDisabledNoRemote

-OccupiedDisabledNoCCN

Fig. 16 — Chiller Schedule ScreenTable 15 — Configuring the Schedule with

Pilot Display

NAME

NO.

1 DOW (MTWTFSSH)210000000Occupied from300:00Occupied to

:00Period 2 DOW (MTWTFSSH)511000000Occupied from607:00Occupied to

:00Period 3 DOW (MTWTFSSH)OCCDEFCS://www.51wendang.com/doc/437ec10ed908de0667a81455nfig800100000Occupied from907:00Occupied to

OCC1P02S

P01S 1021:30Period 4 DOW (MTWTFSSH)11

[此处图片未下载成功]

00011000Occupied from1207:00Occupied to

:00Period 5 DOW (MTWTFSSH)1400000100Occupied from1507:00Occupied to

:00

values. To configure, first change the month (day Start MonthHoli-duration (), then the day (Holiday Start Day), then theholiday in included in one of the Occupied Time Periods of theHoliday Duration) of the holiday period in days. If aschedule, the machine will follow that operating condition forthe holiday. In the following examples, the holidays July 4 andDecember 25-26 are programmed for Holiday 1 and Holiday 2,respectively. To configure these holidays with the Touch Pilotdisplay, see Table 16 and Fig. 16. To configure Holidays withthe Navigator display, check the H (holiday) schedule on theSchedule screen and program in the desired ochttp://www.51wendang.com/doc/437ec10ed908de0667a81455cupied times.Table 16 — Programming Holiday Schedules with

Pilot Display

NAMEPATH

NO.

Start Month17Start Day

_01

Duration (days)

Holiday Start Month112Start Day

_02

Duration (days)

mode (Timed Override Hours) for 1, 2, 3 or 4 hours

a one-time basis. To configure this option for the TouchPilot display:

NAME

.VALUETimed Override HoursOCC1P01S or OCC1P02S

1

: 0 to 4Default: 0

by changing the Timed Override Hours to 0.

configured for a timed override, the override can be can-from 65 to 99 for operation under a CCN global schedule. The30XW chillers can be configured to follow a CCN GlobalTime Schedule broadcast by another system element. TheComfortVIEhttp://www.51wendang.com/doc/437ec10ed908de0667a81455W  Network Manager’s Configure and Modifycommands or the Service Tool’s Modify/Names function mustbe used to change the number of the Occupancy EquipmentPart Table Name (OCC1P01E) to the Global Schedule Num-ber. The Schedule Number can be set from 65 to 99(OCC1P65E to OCC1P99E).

must be changed to configure the unit to broadcast aThe Occupancy Supervisory Part table name (OCC1P01S)Global Time Schedule. The Schedule Number can be set from65 to 99 (OCC1P65S to OCC1P99S). When OCC1PxxS is setto a value greater than 64, an occupancy flag is broadcast overthe CCN every time it transitions from occupied to unoccupiedor vice-versa. By configuring their appropriate Time Scheduledecisions to the same number, other devices on the network canfollow this same schedule. The Enable/Off/Remote Contactmust be in the Enable position or the Remote Contact positionwith the contacts closed for the unit to operate. The Unit RunStatus ((OFF,http://www.51wendang.com/doc/437ec10ed908de0667a81455 RUNNINGSTAT) will indicate the current status of the machineschedule. The unit Occupied status (, STOPPING or DELAY), depending on thecurrent occupied schedule according to the schedule, either NOOCC) will indicate theor YES. The Status Unit Control Type (OFF when the switch is Off. The Status Unit Control Type willCTRL) will be LOCALbe CCN when the Enable/Off/Remote Contact switch input isOn.

global schedules and the i-VuRefer to Appendix F for more detailed instructions regard-&#174; device.

Start screen will be displayed. Select CCN Mode.The unit will be controlled by a CCN command to the ChillerCCNChillervisor, controls the On/Off state of the machine. When Start/Stop variable. An external CCN device, such ascontrolled by a Chillervisor, it is recommended that the Start When SM Lostof a loss of communication with the network, the machine will configuration be set to Yes. In the eventAutostart and be chttp://www.51wendang.com/doc/437ec10ed908de0667a81455ontrolled locally.

. In the event local control is established, be sure thatCareful evaluation of chilled water plant control should beall pumps, valves, and other devices are capable of operatingproperly. The control will ignore the position of Enable/Off/Remote Contact switch. The the current status of the machine — OFF, RUNNINGRun Status variable will indicateor READY, DELAY,The Operating Type. The Control Type variable will change to CCN.

will change to CCN.be enabled using the CCN Mode button.

dual chiller control applications, the slave chiller mustTouch Pilot display. The Equipment Start screen will be dis-played. Select Remote Mode. The unit will be controlled by theEnable/Off/Remote Contact switch (SW1). Switching the En-able/Off/Remote Contact switch to the Enable or RemoteContact position (external contacts closed) will force the unitinto an occupied state. In this mode, all CCN nehttp://www.51wendang.com/doc/437ec10ed908de0667a81455twork force22

commands, except the Emergency Stop Command will beignored. The Run Status variable will indicate the current sta-tus of the machine (OFF, RUNNING, DELAY, or READY),depending on the position of the Remote/Off/Enable Switchclosure. The Chiller Occupied? variable will change to YES.The Control Type variable will change to Remote. The Oper-ating Type variable will change to Remote.

operate the machines in Dual Chiller Mode, one machinemust be designated as the master unit and one machine as theslave unit. On the master unit, press the Start/Stop button on theTouch Pilot display. The Equipment Start screen will be dis-played. Select Master Mode. Failure to start the Master unit inthis manner will cause both machines to operate in local mode.The Master Unit Control can be done locally, remotely orthrough CCN commands per the master/slave configuration(Master Control Type). The control will ignore the posithttp://www.51wendang.com/doc/437ec10ed908de0667a81455ion ofEnable/Off/Remote Contact switch if the Master ControlType is configured for Local Control or CCN Control. TheRun Status variable, Chiller Occupied? variable, and Con-trol Type variable will change based on the Master ControlType configured above and the Machine On/Off Control de-fined above. The Operating Type variable will change toMaster.

will shut down. While the unit is in Local Off, it willremain shut down and ignore all CCN commands as well asthe position of Enable/Off/Remote Contact switch. The RunStatus variable, indicating the current status of the machine,will change to OFF. The Chiller Occupied? variable willchange to NO. The Control Type variable will indicateLocal. The Operating Type variable will change to L-OFF(Local Off).

[此处图片未下载成功]

NAVIGATOR  DISPLAY MACHINE CONTROL — Ma-chine On/Off control with the Navigator display is determinedby the configuration of the Operating Type Contrhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ol (OPER).Options to control the machine locally via a switch, from a lo-cal Time Schedule, or via a Carrier Comfort Network&#174; com-mand are offered. See Table 17.

schedules consist of 8 user-configurable occupied timeperiods. The control supports time schedules for local control,remote control, and ice building. These time periods can beflagged to be in effect or not in effect on each day of the week.The day begins at 00.00 and ends at 24.00. The machine is inunoccupied mode unless a scheduled time period is in effect. Ifan occupied period is to extend past midnight, the occupiedperiod must end at 24:00 hours (midnight) and a new occupiedperiod must be programmed to begin at 00:00 hours.

the following example, a early morning pulldown timeperiod is scheduled for Monday morning from 12:00 AM to3:00 AM. The occupied period starts at 7:00 AM, Mondaythrough Saturday. The occupied time ends at 6:00 PM on Mon-day ahttp://www.51wendang.com/doc/437ec10ed908de0667a81455nd Tuesday, 9:30 PM on Wednesday, 5:00 PM on Thurs-day and Friday, and 12:00 PM on Saturday.

: This schedule was designed to illustrate the program-ming of the schedule function and is not intended as a recom-mended schedule for chiller operation.

. All models are factory configured with Operating TypeControl (OPER) set to SWITCH CTRL (Switch Control).With SWITCH CTRL, switching the Enable/Off/RemoteContact switch to the Enable or Remote Contact position (ex-ternal contacts closed) will put the chiller in an occupied state.The Unit Run Status (STAT) will indicate the current status ofthe machine and will change from OFF to RUNNING orDELAY. The unit Occupied Status (OCC) will change fromNO to YES. The Status Unit Control Type (CTRL) will changefrom LOCAL OFF when the switch is Off to LOCAL ONwhen in the Enable position or in the Remote Contact positionwith external contacts closed.

EXPANSIONPATH

://www.51wendang.com/doc/437ec10ed908de0667a81455OPEROperating Control Operating

SLCT OPERITEM

CTRL

. 17 — Equipment Stop Screen

17 — Navigator Start/Stop Control

CHILLEREMERGENCYREMOTE

/OFF/ENABLEREMOTE ON/OFFTIME SCHEDULE 1START/STOPSTOPALARMLOCKOUT

(OPER)TYPE(CHIL_S_S)(EMSTOP)SWITCH

Off

———EnableRemoteEnableRemote—RemoteRemoteEnableEnable

—Open————Closed—Closed—ClosedClosed——

———————OccupiedOccupiedUnoccupied

————

——————————EnableDisableEnableDisable

——Enable——DisableDisableDisableDisableDisableDisableDisableDisableDisable

———Yes——————————

————Closed—————————

OnLocalSchedule

://www.51wendang.com/doc/437ec10ed908de0667a81455arby the user as long as the Enable/Off/Remote Contact switch isin the Enable or Remote Contact position (external contactsclosed). To operate under this Operating Type Control (must be set to OPERTime Schedules are available and must be field programmed.TIME SCHED (Time Schedule). Two Internal)Time Schedule 1 (control. Time Schedule 2 (SCH1) is used for single set point On-OffOn-Off and Occupied-Unoccupied set point control. TheSCH2) is used for dual set pointcontrol will use the operating schedules as defined under theTime Clock mode in the Navigator display module.

EXPANSIONPATHVALUE

Control TypeOperating

SLCT OPERTIME SCHED

1 (If the chiller is to be controlled to a single set point, usethe machine only. During the unoccupied times, the chiller willSCH1). This type of schedule will start and stopbe off. If the chiller is to be controlled to 2 set points, http://www.51wendang.com/doc/437ec10ed908de0667a81455occupiedand unoccupied, use Schedule 2 (chiller to control to an occupied set point and an unoccupied setSCH2). This will cause thepoint. The machine will be able to provide cooling at any time.play, see Table 18.

configure this option while using the Navigator  dis-enter the month (duration (MON.x), then the day (DAY.x), then theincluded in one of the Occupied Time Periods of the schedule,DUR.x) of the holiday period in days. If a holiday inthe machine will follow that operating condition for theholiday. In the following examples, the holidays July 4 andDecember 25-26 are programmed for Holiday 1 and Holiday 2respectively.

19.

configure this option for the Navigator display, seefrom 65 to 99 for operation under a CCN global schedule. The30XW chillers can be configured to follow a CCN GlobalTime Schedule broadcast by another system element. TheComfortVIEW  Network Manager’s Configure and Modifycommandhttp://www.51wendang.com/doc/437ec10ed908de0667a81455s or the Service Tool’s Modify/Names function mustbe used to change the number of the Occupancy EquipmentPart Table Name (OCC1P01E) to the Global Schedule Num-ber. The Schedule Number can be set from 65 to 99(OCC1P65E to OCC1P99E).

must be changed to configure the unit to broadcast aThe Occupancy Supervisory Part table name (OCC1P01S)Global Time Schedule. The Schedule Number can be set from65 to 99 (OCC1P65S to OCC1P99S). When OCC1PxxS is setto a value greater than 64, an occupancy flag is broadcast overthe CCN every time it transitions from occupied to unoccupiedor vice-versa. By configuring their appropriate Time Scheduledecisions to the same number, other devices on the network canfollow this same schedule. The Enable/Off/Remote Contactmust be in the Enable position or the Remote Contact positionwith the contacts closed for the unit to operate. The Unit RunStatus ((OFF, RUNNINGSTAT) will indicate the current status ohttp://www.51wendang.com/doc/437ec10ed908de0667a81455f the machineschedule. The unit Occupied status (, STOPPING or DELAY), depending on thecurrent occupied schedule according to the schedule, either NOOCC) will indicate theor YES. The Status Unit Control Type (OFF when the switch is Off. The Status Unit Control Type willCTRL) will be LOCALbe CCN when the Enable/Off/Remote Contact switch input isOn.

global schedules and the i-VuRefer to Appendix F for more detailed instructions regard-&#174; device.

18 — Configuring Schedules with

Display

EXPANSIONPATH

.1Occupied Time00:00UNO.1Unoccupied Time03:00MON.1Monday SelectYesTUE.1Tuesday SelectTime

.1Wednesday SelectClock NoTHU.1Thursday SelectClock or Time

PER.1

PER.1

.1Friday SelectNoSAT.1Saturday SelectNoSUN.1Sunday SelectNoHOL.1Holiday SelectNoOCC.2Occupied Time07:00UNO.2Unoccupied Time18:00MON.2Monday SelectYesTUE.2Tueshttp://www.51wendang.com/doc/437ec10ed908de0667a81455day SelectYesWED.2Wednesday SelectClock Time

.2Thursday Selector Time

PER.2

SCH2 PER.2

.2Friday SelectNoSAT.2Saturday SelectNoSUN.2Sunday SelectNoHOL.2Holiday SelectNoOCC.3Occupied Time07:00UNO.3Unoccupied Time21:30MON.3Monday SelectNoTUE.3Tuesday SelectWED.3Wednesday SelectTime

SCH1 PER.3

.3Thursday SelectFRI.3Friday SelectClock or Time

PER.3

.3Saturday SelectNoSUN.3Sunday SelectNoHOL.3Holiday SelectNoOCC.4Occupied Time07:00UNO.4Unoccupied Time17:00MON.4Monday SelectNoTUE.4Tuesday SelectNoWED.4Wednesday SelectClock SCH1Time

.4Thursday SelectFRI.4Friday Select or Time

PER.4

PER.4

.4Saturday SelectNoSUN.4Sunday SelectNoHOL.4Holiday SelectNoOCC.5Occupied Time07:00UNO.5Unoccupied Time12:00MON.5Monday SelectNoTUE.5Tuesday SelectNoWED.5Wednesday SelectClock SCH1Time

PER.5

://www.51wendang.com/doc/437ec10ed908de0667a81455arNoTHU.5Thursday SelectFRI.5Friday SelectClock or Time

PER.5

.5Saturday SelectYesSUN.5Sunday SelectNoHOL.5

Select

19 — Configuring Holiday Schedules

Navigator Display

EXPANSIONPATH

.1Holiday Start MonthDAY.1Holiday Start Day

HOLITime 7

HOL.1

.1Holiday Duration in Day1MON.2Holiday Start MonthDAY.2Holiday Start Day

.2

Duration in Day

HOLITime 12

HOL.2

Remote Contact Switch is in the Enable or Remote Contactposition (external contacts closed.) To operate under thisOperating Control, OPER must be set to CCN CONTROL. Anexternal CCN device, such as Chillervisor, controls the On/Offstate of the machine. When controlled by a Chillervisor, it isrecommended that the Auto Start When SM Lost (set to Yes.

://www.51wendang.com/doc/437ec10ed908de0667a81455rAU.SM) bereviewed. In the event Local Control is established, be sure thatCareful evaluation of Chilled Water Plant control should beall pumps, valves, and other devices are capable of operatingproperly. In the event of a loss of communication with the net-work, the machine will start and be controlled locally. TheCCN device forces the variable CHIL_S_S to control the chill-er. The Unit Run Status (of the machine (OFF, RUNNINGSTAT) will indicate the current statusdepending on the CCN command. The unit Occupied status, STOPPING or DELAY),(CCN command and will be displayed as either NO or YES.OCC) will indicate the current occupied state according to theThe Status Unit Control Type (when the Enable/Off/Remote Contact switch is Off. The StatusCTRL) will be LOCAL OFFUnit Control Type will be CCN when the Enable/Off/RemoteContact switch input is Closed and the CHIL_S_S variable isStop or Start.

be enabled using the CCN CONTROhttp://www.51wendang.com/doc/437ec10ed908de0667a81455L option.

Dual Chiller Control applications, the Slave ChillerITEMITEM EXPANSIONPATH

Control Type

SLCT OPERCCN

.SM

Start when SM Lost

SERV

for the chilled water fluid set point is controlling to theEntering Fluid Control Option — The factory de-

water temperature. An option to configure the machinefor entering water control is available. The control operationremains the same except the control point is focused on theentering water temperature, rather than the leaving water tem-perature when configured.

configure this option for the Touch Pilot  display:

NAMEPATHLINE NO.VALUE

Fluid Control

= Leaving Water ControlYes = Entering Water Control

configure this option for the Navigator  display:://www.51wendang.com/doc/437ec10ed908de0667a81455par

EXPANSIONPATH

Water Control

= Leaving Water ControlYWater Control

= Entering controlling the Leaving Chilled Water Set Point are offered andCooling Set Point Selection — Several options for

configured by the Cooling Set Point Select (lectSetpoint Se-lect, Ice Mode Enable discussed later in this book, and Heat, SP.SE) variable. In addition to the Cooling Set Point Se-Cool Select (role in determining the set point of the machine. All units areHeat/Cool Select, HC.SE) variables also have ashipped from the factory with the Heat Cool Select set to 0. (confirmed for the individual set points. Limits for the set pointsEntering Fluid ControlAll default set points are based on Leaving Water Control, EWTO) set to No. Values must beare listed in the configurations noted below.

20A. To configure these options for the Navihttp://www.51wendang.com/doc/437ec10ed908de0667a81455gator dis-To configure these options for the Touch Pilot display, seeplay, see Table 20B.

20A — Cooling Set Point Selection

Touch Pilot Display

NAMEPATHLINE NO.VALUE

Setpoint 1Setpoint2Range: 14 to 70 F

(–10.0 to 21.1 C)Default: 44 F (6.6 C)

Setpoint 2Setpoint3Range: 14 to 70 F

(–10.0 to 21.1 C)Default: 44 F (6.6 C)

Ice Setpoint

Range: -20 to 32 F

(–28.9 to 0 C)

: 44 F (6.6 C)

20B — Cooling Set Point Selection

Navigator Display

EXPANSION

.1Cooling Setpoint 1Setpoints COOLRange: 14 to 70 F (–10.0 to 21.1 C)Default: 44 F (6.6 C)CSP.2Cooling Setpoint 2Setpoints COOLRange: 14 to 70 F (–10.0 to 21.1 C)Default: 44 F (6.6 C)CSP.3

[此处图片未下载成功]

Ice Setpoint

COOL

: -20 to 32 Fhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 (–28.9 to 0 C)

: 44 F (6.6 C)

set point. These values depend on the Cooler Fluid TypeIn all cases, there are limits on what values are allowed forand the Brine Freeze Set point, discussed later. See Table 21.

21 — Configuration Set Point Limits

POINT LIMITS(COOLER FLUID TYPE, FLUD)COOLER FLUID TYPE 1, Water2, BrineMinimum *38 F (3.3 C)14 F (–10.0 C)

F (15.5 C)

*The minimum set point for Medium Tis related to the Brine Freeze Point. The set point is limited to be noemperature Brine applicationsless than the Brine Freeze Point  5&#176; F (2.8&#176; C).

options: Set Point Occupancy, Set Point 1, Set Point 2,The Setpoint Select configuration can be set to five different4-20 mA Input, and Dual Switch.

duty application (below 40 F [4.4 C] LCWT) forchiller normally requires factory modification. Contact aCarrier Reprhttp://www.51wendang.com/doc/437ec10ed908de0667a81455esentative for details regarding specificapplications. Operation below 40 F (4.4 C) LCWT with-out modification can result in compressor failure.SET POINT OCCUPANCY — Set default configuration for the Setpoint Select variable. WhenPoint Occupancy is theSetpoint Select ((Setpoint Occ), the unit’s active set point is based on CoolingSetpoint Select, SP.SE) is configured to 0Set Point 1 (period while operating under Time Schedule 1 (Cooling Setpoint 1, CSP.1) during the occupiedTime Schedule 2 (SCH1based on Cooling Set Point 1 (SCH2) is in use, the unit’s active set point is). If theing the occupied period and Cooling Set Point 2 (Cooling Setpoint 1, CSP.1) dur-point 2and 23.

, CSP.2) during the unoccupied period. See Tables 22Cooling Set-To configure this option while using a Touch Pilot display:

NAMEPATHLINE NO.VALUE

select

(Setpoint Occupied)

configured correctlhttp://www.51wendang.com/doc/437ec10ed908de0667a81455y, Setpoint Select (To change this value, a Control Point Force must be applied.SP.SE) will indicate Auto.

Select,To configure this option while using a Navigator display:

EXPANSIONPATHVALUE

.SE

SelectOperating ModesSLCT

Occ

Table 22 — Cooling Set Point Selection Touch Pilot  Parameters

POINT CONFIGURATION (Setpoint Select)

MODE ENABLE (ice_cnfg)

(Auto)

———NO

(Setp Sw)

SET POINT INPUT (SETP_SW)

————————OpenClosedOpenClosedClosed

DONE INPUT

(ICE_SW)

——OpenClosed———————OpenClosed

SCHEDULE 2OccupiedUnoccupiedUnoccupiedUnoccupiedOccupied

————————

SET POINTCooling Setpoint 1Cooling Setpoint 2Cooling Ice SetpointCooling Setpoint 2Cooling Setpoint 1Cooling Setpoint 1Cooling Setpoint 24 to 20 mA InputCoolinhttp://www.51wendang.com/doc/437ec10ed908de0667a81455g Setpoint 1Cooling Setpoint 2Cooling Setpoint 1Cooling Ice SetpointCooling Setpoint 2

(Setp 1)2 (Setp 2)3 (4-20 mA)

23 — Cooling Set Point Selection Navigator  Parameters

STATUS

Method

(OPER)

/Cool Select (HC.SE)

(SP.SE)Setpoint OccSetpoint OccSetpoint OccSetpoint 1Setpoint 24-20mA Setp

———

Setp Sw

——

ModeEnable (ICE.M)

——Enable———EnableEnable————

Done(ICE.D)——Open———OpenClosed————

SetpointSwitch (DUAL)

——————ClosedClosedOpenClosed——

(SP.OC)OccupiedUnoccupiedUnoccupied

———————OccupiedUnoccupied

SET POINTCSP.1CSP.2CSP.3CSP.1CSP.24_20mACSP.3CSP.2CSP.1CSP.2CSP.1CSP.2

Select, SP.SE)Setpoint 1), the unit’s active set point isbased on Cooling Set Point 1 (Cooling Setpoint 1, CSP.1).Thttp://www.51wendang.com/doc/437ec10ed908de0667a81455o configure this option with the Touch Pilot display:

NAMESetpoint Select

GENUNIT

.

(Set Point 1)

configure this option with the Navigator display:

EXPANSIONPATHVALUE

.SESetpoint SelectOperating ModesSLCTSetpoint 2

change this value, a Control Point Force must be applied.

configured correctly, Setpoint Control will indicateSetp 1.

configure this option with the Navigator  display:

EXPANSIONPATHVALUESP.SESetpoint SelectOperating Modes SLCTSetpoint 1

Select, SP.SE)based on Cooling Set Point 2 (Cooling Setpoint 2, CSP.2).To configure this option with the Touch Pilot  display:

NAMESetpoint Select

NO.25

(Set Point 2)

Select,point is based on an field supplied, external 4 to 20 mA signhttp://www.51wendang.com/doc/437ec10ed908de0667a81455alinput to the Energy Management Module (EMM). Care shouldbe taken when interfacing with other manufacturer’s controlsystems, due to power supply differences of full wave bridgeversus half wave rectification. The two different power sup-plies cannot be mixed. ComfortLink  controls use half waverectification. A signal isolation device should be utilized if afull wave bridge signal generating device is used.

following equation is used to control the set point. SeeFig. 18.

Set Point = 10   70(mA – 4)/16 (deg F)Celsius Set Point = –12.2   38.9(mA – 4)/16 (deg C)

configure this option while using a Touch Pilot display:

NAMESetpoint Select

.

(4-20 mA Input)

change this value, a Control Point Force must be applied.

configured correctly, Setpoint Control (Status GENUNIT) will indicate Setp 2.

://www.51wendang.com/doc/437ec10ed908de0667a81455arTo change this value, a Control Point Force must be applied.When configured correctly, Setpoint Control will indicate4-20 mA.

To configure this option while using a Navigator display:

EXPANSIONPATHVALUE

.SESetpoint SelectOperating Modes SLCT4-20 mA Setp

24A — Heating Set Point Selection

Touch Pilot Display

NAMEHeating Setpoint 1

NO.17

: 80 to 140 F (26.7 to 60 C)

: 100 F (37.8 C)Range: 80 to 140 F (26.7 to 60 C)

: 100 F (37.8 C)

Select,point is based on Cooling Set Point 1 (Cooling Setpoint 1,CSP.1) when the Dual Set Point switch contact is open andCooling Set Point 2 (Cooling Setpoint 2, CSP.2) when it isclosed.

configure this option while using a Touch Pilot display:

NAMESetpoint Select

GENUNIT://www.51wendang.com/doc/437ec10ed908de0667a81455NO.25

(Dual

Switch)

Setpoint 2Setpoint18

24B — Heating Set Point Selection

Navigator Display

EXPANSION

[此处图片未下载成功]

Setpoints HEATSetpoints

[此处图片未下载成功]

HEAT

: 80 to 140 F (26.7 to 60 C)

: 100 F (37.8 C)Range: 80 to 140 F (26.7 to 60 C)

: 100 F (37.8 C)

.1Heating Setpoint 1

change this value, a Control Point Force must be applied.When configured correctly, Setpoint Control will indicateSetp Sw.

configure this option while using a Navigator display:

EXPANSION

Modes SLCT

.SESetpoint Select

Setp Sw

.2Heating Setpoint 2

Set Point Selection — Several options for

XW chillers operating as heat machines exhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ist for controllingthe Leaving Condenser Water Set Point and are configured bythe Set Point Select (Setpoint Select, SP.SE) variable. In addi-tion, the Heat Cool Select (Heat/Cool Select, HC.SE) variablealso has a role in determining the set point of the machine. Allunits are shipped from the factory with the Heat Cool Select setto 0.

default set points are based on Leaving Water Control(Entering Fluid Control, EWTO) set to No. Values must beconfirmed for the individual set points. Limits for the set pointsare listed in the configurations noted below.

configure these options for the Touch Pilot display, seeTable 24A. To configure these options for the Navigator dis-play, see Table 24B.

Setpoint Select configuration can be set to five differentcontrol options: Set Point Occupancy, Set Point 1, Set Point 2,4-20 mA Input, and Dual Switch.

Heat Cool Select configuration can be set to fhttp://www.51wendang.com/doc/437ec10ed908de0667a81455our differ-ent control options:  Cooling, Heating, Automatic Changeover,and Heat/Cool Switch.  Use of the Heat/Cool Switch option re-quires field installed wiring to Main Base Board input channel14. Refer to page 9.

30XW chiller operation in either high condensing orheat machine modes require that field-supplied thermalinsulation be installed on compressor discharge lines, oillines, condenser external surfaces and optional minimumload valve lines up to the solenoid valve body. Tubing andheat exchanger surfaces will be hot and the insulation isrequired to prevent burns from accidental contact.

Water Fluid Type Selection — The chilled

fluid must be configured. The fluid type must be config-ured to obtain the proper leaving water set point control range

and freeze protection. The Cooler Fluid Type (Type, FLUD) can be set to water or brine.

FluidFRESH WATER — Cohttp://www.51wendang.com/doc/437ec10ed908de0667a81455nfigure the unit for Cooler Fluid Type(glycol installed in the chilled water loop. The factory defaultCooler Fluid Type, FLUD) to water for units without brine orfluid type is fresh water. Use this option for fresh water sys-tems. This will allow for a water temperature set point of 38 to60 F (3.3 to 15.5 C). With water as the selection, the FreezePoint is fixed at 34 F (1.1 C).

configure this option with the Touch Pilot display:

.VALUECooler

TypeMain Menu Service SERVICE1

= WaterTo configure this option with the Navigator display:

EXPANSIONPATH

Fluid Type

OR GLYCOL OPERATION — Configure for Cooler Fluid Type (brine or glycol chilled water loops. This option will allow for aCooler Fluid Type, FLUDthe unit  ) to brine forset point temperature ranghttp://www.51wendang.com/doc/437ec10ed908de0667a81455e of 14 to 60 F (–10.0 to 15.5 C).Before configuring this selection, confirm that a suitable anti-freeze has been added and is at a sufficient concentration toprotect the loop. Additionally, the Brine Freeze Set Point(protection operation. Set the Brine Freeze Set Point to the burstBrine Freeze Setpoint, LOSP) must be set for proper freezeprotection provided by the glycol concentration. This valuewill be Freeze Point for the fluid.

configure this option with the Touch Pilot display:

NAMEPATH

NO.VALUECooler Fluid Type

Main Menu

SERVICE112=Brine

Freeze Setpoint

Main Menu

SERVICE1

onfluid concentration

configure this option with the Navigator display:

EXPANSIONPATHVALUEFLUDCooler Fluid TypeConfigurationSERVBrineLOSPBrine Freeze SetpointConfiguration SERVDependent on

concentratiohttp://www.51wendang.com/doc/437ec10ed908de0667a81455n

Pump Control — that the cooler pump control be utilized unless the chilled waterIt is required for all chillers

runs continuously or the chilled water system contains asuitable concentration of antifreeze solution. When the CoolerPumps Sequence is configured, the cooler pump output will beenergized when the chiller enters an &quot;ON&quot; mode. The coolerpump output is also energized when certain alarms are generat-ed. The cooler pump output should be used as an override tothe external pump control if cooler pump control is not utilized.The cooler pump output is energized if a PFreeze Protection alarm is generated, which provides addition-.01 Water Exchangeral freeze protection if the system is not protected with a suitableantifreeze solution.

control. Cooler Pumps Sequence is the variable thatThe 30XW units can be configured for external coolermust be confirmed in the field. Proper configurathttp://www.51wendang.com/doc/437ec10ed908de0667a81455ion of thecooler pump control is required to provide reliable chiller oper-ation. The factory default setting for Cooler Pumps Sequence is0 (No Pump). The configuration settings for Cooler Pumps Se-quence are 1 (1 pump only) for single pump control and 2 (2pumps auto). Configuration settings 3 (PMP 1 Manual) and 4(PMP 2 Manual) are for dual pump control only.

will start the pump. If a flow failure is detected, the unit

the Cooler Pumps Sequence (PUMP) is set to 1, the con-will shut down and must be manually reset. If the CoolerPumps Sequence (lead pump and automatically alternate the operation of thePUMP) is set to 2, the control will start thepumps to even the wear. If a flow failure is detected, the unitwill shut down and the lag pump will attempt to start. If flow isestablished within the Unit Off to On Delay (unit will restart automatically.

) period theCooler Pumps Sequence (Two manual control ophttp://www.51wendang.com/doc/437ec10ed908de0667a81455tions are also available. When thewill always operate. If a flow failure is detected, the unit willPUMP) is set to 3, Cooler Pump 1shut down and must be manually reset. When the CoolerPumps Sequence (ways operate. If a flow failure is detected, the unit will shutPUMP) is set to 4, Cooler Pump 2 will al-down and must be manually reset.

), closure of both the chilled water flow switch (CWFS) andFor all Cooler Pumps Sequence (PUMP) settings (includingthe chilled water pump interlock contact (connected acrossTB5 terminals 1 and 2) are required. In addition, for CoolerPumps Sequence settings of auxiliary contacts for Pump 1 and Pump 2 (wired in parallel)PUMP = 1, 2, 3, 4, normally openmust be connected to the violet and pink wires located in theharness from the MBB-J5C-CH18 connector. The wires in theharness are marked &quot;PMP1-13&quot; and &quot;PMP1-14&quot;. See the fieldwiring diagram in the 30XW Installation Instructions.://www.51wendang.com/doc/437ec10ed908de0667a81455arwater flow switch/interlock does not close within theRegardless of the cooler pump control option selected, if theUnit Off to On Delay period after the unit is enabled and in anON mode, alarm Pwhich will trigger this alarm include:

.91 will be generated. Other conditions Cooler pump interlock is open for at least 15 seconds during chiller operation.

chiller in Master/Slave Control pump interlock does not close after 1 minute of the pump start command.

pump control is enabled and the chilled water flowswitch/interlock is closed for more than 2 minutes followinga command to shut down the pump.

setting (The last alarm criterion can be disabled. If the cooler pumpNO, the control will ignore the pump interlock input if theFlow Checked if C Pmp Off, P.LOC) is set tocooler pump output is OFF.

the pumps to maintain the bearing lubrication and seal in-The ComfortLink  conthttp://www.51wendang.com/doc/437ec10ed908de0667a81455rols have the ability to periodicallytegrity. If Pump Sticking Protection (tionpump will be started once each day for 2 seconds. If the unit, PM.PS) is set to YES, and if the unit is off at 2:00 PM, aPump Sticking Protec-has 2 pumps, Pump 1 will be started on even days (such as day2, 4, or 6 of the month); Pump 2 will be started on odd days.The default for this option is PM.PS=NO.

is issued.

pump will continue to run for 60 seconds after an offCOOLER PUMP CONTROL CONFIGURATIONS

NAMEPATH

NO.VALUECooler Pumps Sequence

Config USER

(No Pump Control)

display:

configure cooler pump control options with the Naviga-ITEMITEM EXPANSIONPATH

Pumps Sequence

OPTN

Pump

DISPLAY NAMEPATH

NO.VALUECooler Pumps SequenceMain

Config USERhttp://www.51wendang.com/doc/437ec10ed908de0667a8145581 (Single

Control)Pump Sticking ProtectionMain

Config USER15Default = NoNo = DisabledYes = EnabledFlow Checked Default = Yif C Pump Off

Config USER

= DisabledesYes = Enabled

display:

configure cooler pump control options with the Naviga-ITEMITEM EXPANSIONPATH

Pumps SequenceConfiguration OPTN1 Pump OnlyPM.PSPeriodic Pump Default = NoStart

OPTNNo = DisabledYes = EnabledP.LOC

Checked if Pmp Off

OPTN

= YNo = DisabledesYes = Enabled

NAMEPATH

NO.VALUE

Pumps 2 (2 Pumps Automatic)Sequence Main Menu

USER

(Pump 1 Manual)4 (Pump 2 Manual)Pump Auto Rotation Delay Main Menu

USER

Default = 48 hoursPump Sticking Default = NoProtection Main Menu

USER15No = DisabledYes = http://www.51wendang.com/doc/437ec10ed908de0667a81455EnabledFlow Checked Default = Yif C Pump Off

Main Menu

USER

= DisabledesYes = Enabled

display:

configure cooler pump control options with the Naviga-ITEMITEM EXPANSIONPATH

Pumps 2 Pumps AutoSequenceConfiguration OPTNPMP1 ManualPMP2 ManualROT.PPump Rotation Delay

OPTNDefault = 48 hoursPM.PSPeriodic Pump Default = NoStart

OPTNNo = DisabledYes = EnabledP.LOC

Checked Default = Yif Pmp Off

OPTN

= DisabledesYes = Enabled

Start Delay — the machine is also available. This parameter is useful in keep-An option to delay the start of

multiple machines from starting at the same time in case ofa power failure. The parameter has a factory default of1 minute. This parameter also has a role in the timing for achilled water flow switch alarm. The flow swithttp://www.51wendang.com/doc/437ec10ed908de0667a81455ch status is notchecked until the delay time has elapsed.

configure this option with the Touch Pilot display:

NAMEPATH

NO.VALUE

Off to On Delay

Main Menu

USER

= 1 Minute

configure this option with the Navigator display:

EXPANSIONPATH

Off Time

OPTN

= 1 Minute

/Compressor Staging and Loading —

AquaForce&#174;circuit. As a result, circuit and compressor staging are the

XW chillers employ one compressor persame. The control has several control option parameters to loadthe compressors. The circuit/compressor start can be config-ured as well as the loading of each circuit/compressor.

/COMPRESSOR STAGING — The control can beconfigured to decide which circuit/compressor starts first, byconfiguring Lead/Lag Cihttp://www.51wendang.com/doc/437ec10ed908de0667a81455rcuit Select (SequenceAutomatic Lead-Lag, Circuit A Leads or Circuit B Leads. The, LLCS). Three options for this variable are allowed:Circuit Loadingfactory default is Automatic Lead-Lag.

starts. When enabled, the control will determineThe automatic lead-lag function determines which circuit/which circuit/compressor starts to even the wear of the com-pressor. The compressor wear factor (combination of starts andrun hours) is used to determine which compressor starts.

Wear Factor = (Compressor Starts) pressor Run Hours)

0.1 (Com-factor is the circuit that starts first.

circuit/compressor with the lowest compressor wearcan also be configured with the same variable.

starting a particular circuit/compressor first is desired, thatTo configure this option with the Touch Pilot display:

NAMEPATH

NO.VALUE

(Automatic Lead-lag)Circuit Loading 1http://www.51wendang.com/doc/437ec10ed908de0667a81455 (Circuit A Leads)Sequence

Menu

USER

(Circuit B Leads)Default = 0

(Automatic Lead-lag)

configure this option with the Navigator display:

EXPANSIONPATHVALUE

: Automatic, LLCS

/Lag Circuit Select

Configuration

A Leads, OPTN

B Leads, Cir C Leads

– Automatic

/COMPRESSOR LOADING — The be configured to stage the circuit/compressors. The Loadingcontrol canSequence Select (determines  how the control will perform loading. The configu-Staged Loading Sequence, LOAD) settingration can be set to Equal or Staged.

fully unloaded.  As additional capacity is required, theslide valve  will be adjusted in approximately 5% increments tomatch capacity requirements.  The lag circuit will not start untilthe lead circuit reaches 70% capacity. The lead circuit will re-main at 70% and the http://www.51wendang.com/doc/437ec10ed908de0667a81455lag circuit will increase in capacity until italso reaches 70% capacity. The control will alternate betweencircuits to maintain the same percentage of capacity on eachcircuit until they reach 100%.

slide valve fully unloaded. As additional capacity is re-quired, the slide valve  will be adjusted in approximately 5%increments to match capacity requirements until the circuit isfully loaded. Once the circuit is fully loaded and additional ca-pacity is required, the control will start the lag circuit fully un-loaded. The control will continue load the lag circuit in approx-imately 5% increments to match capacity requirements untilboth circuit reach 100% capacity.

configure this option with the Touch Pilot  display:

NAMEPATH

NO.VALUEStaged Loading Sequence

Config USER

= NoNo (Equal)Yes (Staged)

To configure this option with thttp://www.51wendang.com/doc/437ec10ed908de0667a81455he Navigator  display:

EXPANSION

Sequence

OPTN

= EqualSelect

Load Control — can be a factory-installed option or a field-installed accessory.Minimum Load Control

installed, and its operation is desired, the Minimum LoadControl must be enabled. Once enabled, the valve will be oper-ational only during the first stage of cooling.

configure this option with the Touch Pilot display:

NAMEPATH

NO.VALUE

= No

Gas

(No Minimum Bypass Select

MenuFACTORY

Service14

Control)

Installed)

(Minimum Load A power cycle is required for the values to take effect.To configure this option with the Navigator display:

PATH

http://www.51wendang.com/doc/437ec10ed908de0667a81455= No Minimum HGBPHot Gas

Select

UNIT

Control

Installed

= Minimum Load A power cycle is required for the values to take effect.available for the control of two units installed in series or paral-Dual Chiller Control — The dual chiller routine is

supplying chilled fluid on a common loop. One chiller mustbe configured as the master chiller, the other as the slave chill-er. For parallel applications, an additional leaving fluid temper-ature thermistor (dual chiller LWT) must be installed in thecommon chilled water piping as described in the InstallationInstructions for both the master and slave chillers. See the FieldWiring section in the 30XW Installation Instructions for dualchiller LWT sensor control wiring.

field configured for operation. Both chillers must be on theThe control algorithm relies on several parameters that mustsame Carrier Comhttp://www.51wendang.com/doc/437ec10ed908de0667a81455fort Network&#174;On both chillers, Master/Slave Select ( bus with different addresses.MSSLMaster/Slave Select,ers in Series () must be enabled. The water piping arrangement, Chill-The master chiller must be programmed with the Slave ChillerChiller in Series, SERI), must be configured.Address (gramming parameters may be configured to meet applicationSlave Address, SLVA). Additional optional pro-requirements.

which chiller is the lead machine. The options are Al-Lead/Lag Balance Select (Lead Lag Select, LLBL) deter-ways Lead, Lag if Fail, and Runtime Select. Under RuntimeSelect control, the lead chiller will change based on the time in-crement selected in the Lead/Lag Balance Delta configuration(between the master and the slave remains less than the Lead/Lead/Lag Balance Data, LLBD). If the run hour differenceLag Balance Delta, the chiller designated as the lead willremain the lead chiller. The Lead/Lag changeover betweenhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 themaster and the slave chiller due to hour balance will occur dur-ing chiller operating odd days, such as day 1, day 3, and day 5of the month, at 12:00 a.m. If a lead chiller is not designated,the master chiller will always be designated the lead chiller.the start of the lag chiller in two ways. The Lead PulldownThe dual chiller control algorithm has the ability to delayTime parameter (time delay initiated after starting the lead chiller, before

Pulldown Type, LPUL) is a one-timechecking whether to start an additional chiller. This time delaygives the lead chiller a chance to remove the heat that thechilled water loop picked up while being inactive during an un-occupied period. The second time delay, Lead/Lag Delay (Start TimerLagstage of the lead chiller and the start of the lag chiller. This pre-, LLDY) is a time delay imposed between the lastvents enabling the lag chiller until the lead/lag delay timer hasexpired.://www.51wendang.com/doc/437ec10ed908de0667a81455rthe Start if Error Higher parameter (A quicker start of the lag chiller can be accomplished byHigherStart if Erroring water temperature and the set point is greater than the con-, LL.ER). If the difference between the common leav-figured value, then the lag chiller will start.

the Lag Minimum Running Time configuration (A minimum on time for the lag chiller can be programmedMinimum Running Timethe control to run the lag chiller for the programmed minimum, LAG.M). This parameter causesLagon time. The Lag Unit Pump Select (LAGPLag Unit Pump Control,while the chiller is off. This parameter is only active in Parallel) can be configured such that the pump can be on or offChiller Operation.

be completed to start the machine. On the master chiller,For units with a Touch Pilot display, two additional stepsthe Master Control Type must be configured for the start con-trol defined in the Machine Control http://www.51wendang.com/doc/437ec10ed908de0667a81455configuration. To start themachines, the master chiller must be started with the Start/Stopbutton and Master Mode selected. The slave chiller must bestarted with the CCN Mode selected.

below.

application, Parallel and Series, are described sepa-DUAL CHILLER CONTROL FOR PARALLEL APPLI-CATIONS applications using the Touch Pilot display, see Table 25. To— To configure the master chiller for parallelconfigure the master chiller for parallel applications using theNavigator display, see Table 26.

Touch Pilot display, see Table 27. To configure the slaveTo configure the slave chiller for parallel applications usingchiller for parallel applications using the Navigator display, seeTable 28.

CHILLER PUMP CONTROL FOR PARALLELCHILLER APPLICATIONS — It dedicated pump be used for each unit. The chiller must startis recommended that aand stop its own water pump located on its own piping. Ifpumps are http://www.51wendang.com/doc/437ec10ed908de0667a81455not dedicated for each chiller, chiller isolationvalves are required and each chiller must open and close itsown isolation valve.

CHILLER CONTROL FOR SERIES APPLICA-TIONS tions using the Touch Pilot  display, see Table 29. To— To configure the master chiller for series applica-configure the master chiller for series applications using theNavigator  display, see Table 30.

Touch Pilot  display, see Table 31. To configure the slaveTo configure the slave chiller for series applications usingchiller for series applications using the Navigator  display,see Table 32.

CHILLER PUMP CONTROL FOR SERIESCHILLER APPLICATIONS — Pump control for series chill-er applications is controlled by the master chiller only. Thecontrol of the slave chiller is directed through commands emit-ted by the master chiller. The slave chiller has no action inmaster/slave operations. The slave chiller only verifies thatCCN communicatihttp://www.51wendang.com/doc/437ec10ed908de0667a81455on with the master chiller is present. See theDual Chiller Sequence of Operation section on page 56.

Table 25 — Dual Master Chiller Control Parameters for Parallel Applications with Touch Pilot  Display

NAME

/Slave Select

Menu Config MST_SLV

NO.

(Master)

: 0 (Disable)1=Local Control2=Remote Control3=CCN ControlDefault: 1

for proper control type.

be set to the Slave Chiller’s address. The master and slave chiller must have different addresses and be on the same Bus NumberDefault: 2

(Master Always Leads)1 (Lag Once Failed Only)2 (Lead/Lag Runtime Select)Default: 0 (Master Always Leads)Range: 40 to 400 hoursDefault: 168 hours

: 2 to 30 minutesDefault: 10 minutesRange: 0 to 60 minutesDefault: 0 minutes

: 3.0 to 18  F (1.7 to 10.0  C)Default: 4.0  F (2http://www.51wendang.com/doc/437ec10ed908de0667a81455.2  C)Range: 0 to 150 minutesDefault: 0 minutes0 (Stop If Unit Stops)1 (Run If Unit Stops)

: 0 (Stop If Unit Stops)Default: NoValue: No

Control TypeMain Menu Config MST_SLV7

AddressMain Menu Config MST_SLV11

Lag SelectLead/Lag Balance DeltaLag Start TimerLead Pulldown TimeStart If Error Higher

Minimum Running TimeLag Unit Pump ControlChiller In Series

Menu Config MST_SLVMain Menu Config MST_SLVMain Menu Config MST_SLVMain Menu Config MST_SLVMain Menu Config MST_SLVMain Menu Config MST_SLVMain Menu Config MST_SLVMain Menu Config MST_SLV

26 — Dual Master Chiller Control Parameters for Parallel Applications with Navigator  Display

EXPANSION

/Slave Select

RSET

: Disable

be set to the Slave Chiller’s adhttp://www.51wendang.com/doc/437ec10ed908de0667a81455dress. The master and slave chiller must have different addresses and be on the same Bus NumberDefault: 2

: Always Lead, Lag if Fail, Runtime SelDefault: Always LeadRange: 40 to 400 hoursDefault: 168 hours

: 2 to 30 minutesDefault: 10 minutes

: 3.0 to 18  F (1.7 to 10.0  C)Default: 4.0  F (2.2  C)

: Off If U Stp, On If U StopDefault: Off If U StpRange: 0 to 60 minutesDefault: 0 minutesNo

: No

to desired control

AddressConfiguration RSET

.ERLAG.MLPULSERIOPER

Lead Lag SelectLead/Lag Balance DeltaLag Start DelayStart If Error HigherLag Unit Pump SelectLead Pulldown TimeChillers in SeriesOperating Control Type

RSETConfiguration RSETConfiguration RSETConfiguration RSETConfiguration RSETConfiguration RSETConfiguration RSETOperating ModesSLCT

Table 27 — Dual Slave Chiller Controhttp://www.51wendang.com/doc/437ec10ed908de0667a81455l Parameters for Parallel Applications with Touch Pilot  Display

NAME

/Slave Select

Menu Config MST_SLV

NO.

(Slave)

: 0 (Disable)1 (Local Control)2 (Remote Control)3 (CCN Control)Default: 1

for proper control type.

be set to the Slave Chiller’s address. The master and slave chiller must have different addresses and be on the same Bus NumberDefault: 2

(Master Always Leads) 1 (Lag Once Failed Only)2 (Lead/Lag Runtime Select)

: 0 (Master Always Leads) Range: 40 to 400 hoursDefault: 168 hours

: 2 to 30 minutesDefault: 10 minutesRange: 0 to 60 minutesDefault: 0 minutes

: 3.0 to 18  F (1.7 to 10.0  C)Default: 4.0  F (2.2  C)Range: 0 to 150 minutesDefault: 0 minutes0 (Stop If Unit Stops)1 (Run If Unit Stops)

: 0 (Stop If Unit Stops)No

://www.51wendang.com/doc/437ec10ed908de0667a81455ault: No

Control TypeMain Menu Config MST_SLV7

AddressMain Menu Config MST_SLV11

Lag SelectLead/Lag Balance DeltaLag Start TimerLead Pulldown TimeStart If Error Higher

Minimum Running TimeLag Unit Pump ControlChiller In Series

Menu Config MST_SLVMain Menu Config MST_SLVMain Menu Config MST_SLVMain Menu Config MST_SLVMain Menu Config MST_SLVMain Menu Config MST_SLVMain Menu Config MST_SLVMain Menu Config MST_SLV

28 — Dual Slave Chiller Control Parameters for Parallel Applications with Navigator  Display

EXPANSION

/Slave Select

RSET

: Disable

be set to the Slave Chiller’s address. The master and slave chiller must have different addresses and be on the same Bus NumberDefault: 2

: Always Lead, Lag if Faihttp://www.51wendang.com/doc/437ec10ed908de0667a81455l, Runtime SelDefault: Always LeadRange: 40 to 400 hoursDefault: 168 hours

: 2 to 30 minutesDefault: 10 minutes

: 3.0 to 18  F (1.7 to 10.0  C)Default: 4.0  F (2.2  C)

: Off If U Stp, On If U StopDefault: Off If U StpRange: 0 to 60 minutesDefault: 0 minutesNo,

: NoCCN Control

AddressConfiguration RSET

.ERLAG.MLPULSERIOPER

Lead Lag SelectLead/Lag Balance DeltaLag Start DelayStart If Error HigherLag Unit Pump SelectLead Pulldown TimeChillers in SeriesOperating Control Type

RSETConfiguration RSETConfiguration RSETConfiguration RSETConfiguration RSETConfiguration RSETConfiguration RSETOperating ModesSLCT

Table 29 — Dual Master Chiller Control Parameters for Series Applications with Touch Pilot Display

NAME

/Slave Select

Menu Config MST_SLV

://www.51wendang.com/doc/437ec10ed908de0667a81455LINE NO.

(Master)

: 0 (Disable)1 (Local Control)2 (Remote Control)3 (CCN Control)

: 1 (Local Control)

: Configure for proper control type.Must be set to the Slave Chiller’s address. The master and slave chiller must have different addresses and be on the same Bus NumberDefault: 2

(Master Always Leads)1 (Lag Once Failed Only)2 (Lead/Lag Runtime Select)Default: 0 (Master Always Leads)Range: 40 to 400 hoursDefault: 168 hours

: 2 to 30 minutesDefault: 10 minutesRange: 0 to 60 minutesDefault: 0 minutes

: 3.0 to 18  F (1.7 to 10.0  C)Default: 4.0  F (2.2  C)Range: 0 to 150 minutesDefault: 0 minutes0 (Stop If Unit Stops)1 (Run If Unit Stops)

: 0 (Stop If Unit Stops)Yes

: No

Control TypeMain Menu Config MST_SLV7

AddressMain Menu Config MST_SLV11

Lag SelectLead/Lag Balance Dhttp://www.51wendang.com/doc/437ec10ed908de0667a81455eltaLag Start TimerLead Pulldown TimeStart If Error Higher

Minimum Running TimeLag Unit Pump ControlChiller In Series

Menu Config MST_SLVMain Menu Config MST_SLVMain Menu Config MST_SLVMain Menu Config MST_SLVMain Menu Config MST_SLVMain Menu Config MST_SLVMain Menu Config MST_SLVMain Menu Config MST_SLV

30 — Dual Master Chiller Control Parameters for Series Applications with Navigator  Display

EXPANSION

/Slave Select

RSET

: Disable

be set to the Slave Chiller’s address. The master and slave chiller must have different addresses and be on the same Bus NumberDefault: 2

: Always Lead, Lag if Fail, Runtime SelDefault: Always LeadRange: 40 to 400 hoursDefault: 168 hours

: 2 to 30 minutesDefault: 10 minutes

: 3.0 to 18 http://www.51wendang.com/doc/437ec10ed908de0667a81455 F (1.7 to 10.0  C)Default: 4.0  F (2.2  C)

: Off If U Stp, On If U StopDefault: Off If U StpRange: 0 to 60 minutesDefault: 0 minutesYES

: NO

to desired value

AddressConfiguration RSET

.ERLAG.MLPULSERIOPER

Lead Lag SelectLead/Lag Balance DeltaLag Start DelayStart If Error HigherLag Unit Pump SelectLead Pulldown TimeChillers in SeriesOperating Control Type

RSETConfiguration RSETConfiguration RSETConfiguration RSETConfiguration RSETConfiguration RSETConfiguration RSETOperating ModesSLCT

Table 31 — Dual Slave Chiller Control Parameters for Series Applications with Touch Pilot  Display

NAME

/Slave Select

Menu Config MST_SLV

NO.

(Slave)

: 0 (Disable)1 (Local Control)2 (Remote Control)3 (CCN Contrhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ol)

: 1 (Local Control)

: Configure for proper control type.Must be set to the Slave Chiller’s address. The master and slave chiller must have different addresses and be on the same Bus NumberDefault: 2

(Master Always Leads) 1 (Lag Once Failed Only)2 (Lead/Lag Runtime Select)Default: 0 (Master Always Leads)Range: 40 to 400 hoursDefault: 168 hours

: 2 to 30 minutesDefault: 10 minutesRange: 0 to 60 minutesDefault: 0 minutes

: 3.0 to 18  F (1.7 to 10.0  C)Default: 4.0  F (2.2  C)Range: 0 to 150 minutesDefault: 0 minutes0 (Stop If Unit Stops)1 (Run If Unit Stops)

: 0 (Stop If Unit Stops)Yes

: No

Control TypeMain Menu Config MST_SLV7

AddressMain Menu Config MST_SLV11

Lag SelectLead/Lag Balance DeltaLag Start TimerLead Pulldown TimeStart If Error Higher

Minimum Running TimeLag Unit Pump ControlChiller In http://www.51wendang.com/doc/437ec10ed908de0667a81455Series

Menu Config MST_SLVMain Menu Config MST_SLVMain Menu Config MST_SLVMain Menu Config MST_SLVMain Menu Config MST_SLVMain Menu Config MST_SLVMain Menu Config MST_SLVMain Menu Config MST_SLV

32 — Dual Slave Chiller Control Parameters for Series Applications with Navigator Display

EXPANSION

/Slave Select

RSET

: Disable

be set to the Slave Chiller’s address. The master and slave chiller must have different addresses and be on the same Bus NumberDefault: 2

: Always Lead, Lag if Fail, Runtime Sel

: Always LeadRange: 40 to 400 hoursDefault: 168 hours

: 2 to 30 minutesDefault: 10 minutes

: 3.0 to 18  F (1.7 to 10.0  C)Default: 4.0  F (2.2  C)

: Off If U Stp, On If U StopDefault: Off If U StpRange: 0 to http://www.51wendang.com/doc/437ec10ed908de0667a8145560 minutesDefault: 0 minutesYES

: NOCCN Control

AddressConfiguration RSET

.ERLAG.MLPULSERIOPER

Lead Lag SelectLead/Lag Balance DeltaLag Start DelayStart If Error HigherLag Unit Pump SelectLead Pulldown TimeChillers in SeriesOperating Control Type

RSETConfiguration RSETConfiguration RSETConfiguration RSETConfiguration RSETConfiguration RSETConfiguration RSETOperating ModesSLCT

change of the leaving fluid temperature. If the unit is in a Cool-Ramp Loading — Ramp Loading limits the rate of

mode and configured for Ramp Loading Select (Loading SelectRampbefore deciding to increase capacity. First, the control calcu-, RL.S), the control makes two comparisonslates the temperature difference between the control point andleaving fluid temperature. If the difference is greater than 4&#176; F(2.2&#176; C) and the rate of change (http://www.51wendang.com/doc/437ec10ed908de0667a81455&#176;F or &#176;C per minute) is morethan the configured Cool Ramp Loading rate (Loadingof capacity.

, CRMP), then the control does not allow any increaseCooling RampTo configure this option with the Touch Pilot display:

NAMEPATHLINE NO.

Loading Select Main MenuConfig USER5Yes

Ramp Range: 0.2 to 2.0 &#176;F Loading

Main MenuSetpoint

(0.1 to 1.1 &#176;C)Default: 1.0 &#176;F (0.5 &#176;C)

configure this option with the Navigator display:

.S

Load

OPTNYes

Ramp

COOL

:   0.2 to 2.0 &#176;F

(0.1 to 1.1 &#176;C)Default:  1.0 &#176;F (0.5 &#176;C)

to the basic leaving fluid temperature set point and theTemperature Reset — Temperature reset is a value

://www.51wendang.com/doc/437ec10ed908de0667a81455ing sum of these values is the new control point. When anon-zero temperature reset is applied, the chiller controls to thenew control point, not the set point. The type of temperature re-set is configured with the Cooling Reset Type (SelectCooling Resetable: Return Water Reset, Space Temperature Reset, and 4-20, CRST) variable. Types of temperature reset are avail-mA Temperature Reset.

or leaving fluid temperature, based on the configura-Under normal operation, the chiller will maintain a constanttion, approximately equal to the chilled fluid set point. As thecooler load varies, the cooler fluid temperature difference willchange in proportion to the load. For example, if the chiller wasselected for a Entering to Leaving Water Temperaturedifference of 10 F (5.5 C) at full load, at 50% load the tempera-ture difference would be 5 F (2.2 C). See Fig. 19. Because thechange in temperature through the cooler is a measure of http://www.51wendang.com/doc/437ec10ed908de0667a81455thebuilding load, the temperature difference reset is the averagebuilding load. Usually the chiller size and fluid temperature setpoint are selected based on a full-load condition. At part load,the fluid temperature set point may be lower than required. Ifthe fluid temperature were allowed to increase at part load, theefficiency of the machine would increase. The chiller can alsobe set for return water temperature control. See Fig. 20.

temperature reset are also available and are discussedOther indirect means of estimating building load and con-below.

Select (To verify that reset is functioning correctly, subtract the Set-(Control Point, Current Setpoint, CTPT) to determine the degrees reset.

) from the Control PointRETURN WATER RESET — The control system is capableof performing fluid temperature reset based on cooler fluidtemperature difference. Because the change in temperaturethrough the coohttp://www.51wendang.com/doc/437ec10ed908de0667a81455ler is a measure of the building load, the tem-perature difference reset is, in effect, an average building loadreset method.

temperature set point to be reset upward as a function ofReturn Water Temperature Reset allows for the chilledthe fluid temperature difference (building load).

: Return Water Temperature Reset should not be usedwith variable cooler flow rate systems.

be configured. Cooling Reset Type (To use Return Water Temperature Reset, four variablesSelectTemp (, CRSTcooler temperature difference (T) where no chilled water tem-Delta T No Reset Value) must be enabled. The variable Delta T No ResetCooling Reset, CRT1) should be set to theperature reset should occur. The variable Delta T Full ResetTemp (cooler temperature difference where the maximum chilledDelta T Full Reset Value, CRT2) should be set to thewater temperature reset should occur. The variable DegreesCool Reset (to the maximuhttp://www.51wendang.com/doc/437ec10ed908de0667a81455m amount of reset desired.

Reset Deg. Value, DGRC) should be setTo configure this option with the Touch Pilot  display:

NAMEPATH

NO.

Reset Select

Config USER19Default =0 (No Reset)2 (Delta T)Delta T No Reset ValueMain

Setpoint SETPOINT7Default = 0 F (0 C)Delta T Full Reset ValueMain

Setpoint SETPOINT8Default = 0 F (0 C)Cooling Reset Deg. Value

Setpoint SETPOINT

= 0 F (0 C)

configure this option with the Navigator  display:

EXPANSIONPATH

Reset Default = Type

RSETNo ResetDelta T TempCRT1Delta T No Reset TempSetpoints COOLDefault = 0 F (0 C)CRT2Delta T Full Reset TempSetpoints COOLDefault = 0 F (0 C)DGRC

Cool Reset

COOL

= 0 F (0 C)

, the chilled water thttp://www.51wendang.com/doc/437ec10ed908de0667a81455emperature will be reset by 5&#176; FIn the example in Fig. 21 using Return Water Temperature(2.8&#176; C) when the Fluid Temperature Difference is 2&#176; F(1.1&#176; C) and 0&#176; F (0&#176; C) reset when the Temperature Differenceis 10&#176; F.

also capable of temperature reset based on space temperatureTEMPERATURE RESET — The control system is(SPT). An accessory sensor must be used for SPT reset(33ZCT55SPT). The Energy Management Module (EMM) isalso required for temperature reset using space temperature.configured. Cooling Reset Type (To use Space Temperature Reset, four variables must bemust be enabled. The space temperature at which no tempera-Cooling Reset Select, CRST)ture reset is required, Space T No Reset Temp (Reset Valuewhich full temperature reset is required, Space T Full Reset, CRS1) must be set. The space temperature atSpace T NoTemp (the amount of temperature reset desired, Degrees Cool ResetSpace T Fuhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ll Reset Value, CRS2) must be set. Finally,(Cooling Reset Deg. Value, DRGC), must be set.

configure this option with the Touch Pilot display:

NAMEPATH

NO.VALUECooling Reset Default =0 Select

Main Menu

USER

(No Reset)

(Space Temp)Space T No Reset Value Main Menu

SETPOINT11Default = 14 F (–10 C)Space T Full Reset Value Main Menu

SETPOINT12Default = 14 F (–10 C)Cooling Reset Deg. Value

Main MenuSetpoint SETPOINT

= 0 F (0 C)

To configure this option with the Navigator display:

CRS2DGRC

EXPANSIONCooling Reset TypeSpace T No Reset Temp

T Full Reset Temp

Cool Reset

RSETSetpoints COOLSetpoints COOLSetpoints COOL

= No ResetSpace TempDefault = 14 F (–10 C)Default = 14 F (–10 http://www.51wendang.com/doc/437ec10ed908de0667a81455C)Default = 0 F (0 C)

[此处图片未下载成功]

Care should be taken when interfacing with other controlsystems due to possible power supply differences such as afull wave bridge versus a half wave rectification. Connec-tion of control devices with different power supplies mayresult in permanent damage. The ComfortLink  controlsincorporate power supplies with half wave rectification. Asignal isolation device should be utilized if the signal gen-erator incorporates a full wave bridge rectifier.

configure this option with the Touch Pilot  display:

NAMECooling Reset Select

No Reset ValueCurrent Full Reset ValueCooling Reset Deg. Value

NO.

=0 (No Reset)3 (4-20mA Control)Default = 0.0Default = 0.0Default = 0.0 F (0.0 C)

the space temperature reset example in Fig. 22, 0&#176; F(0&#176; C) chilled water set point reshttp://www.51wendang.com/doc/437ec10ed908de0667a81455et at 72 F (22.2 C) spacetemperature and 6&#176; F (3.3&#176; C) reset at 68 F (20.0 C) spacetemperature.

-20 mA TEMPERATURE RESET — The control system isalso capable of temperature reset based on an externally pow-ered 4 to 20 mA signal. The Energy Management Module(EMM) is required for temperature reset using a 4 to 20 mAsignal.

use 4-20 mA Temperature Reset, four variables must beconfigured. Cooling Reset Type (Cooling Reset Select, CRST)must be enabled. The milliamp signal at which no temperaturereset is required, Current No Reset Value (Current No ResetValue, CRV1), must be set. The milliamp signal at which fulltemperature reset is required, Current Full Reset Value (Cur-rent Full Reset Value, CRV2), must be set. Finally, theamount of temperature reset desired, Degrees Cool Reset(Cooling Reset Deg. Value, DRGC), must be set.

[此处图片未下载成功]

Config USER Setpoint SETPOINT Setpoint SETPOINT Sehttp://www.51wendang.com/doc/437ec10ed908de0667a81455tpoint SETPOINT

MenuMain MenuMain Menu

Menu

configure this option with the Navigator  display:

CRV2DGRC

EXPANSIONCooling Reset Type

No Reset TempCurrent Full Reset TempDegrees Cool Reset

RSETSetpoints COOLSetpoints COOLSetpoints COOL

= No Reset4-20mA InputDefault = 0.0Default = 0.0Default = 0.0

the example in Fig. 23, at 4 mA no reset takes place andat 20 mA, 5&#176; F (2.8&#176; C) chilled water set point reset is required.

[此处图片未下载成功]

37

[此处图片未下载成功]

[此处图片未下载成功]

38

[此处图片未下载成功]

the unit capacity to be limited during periods of peak energyDemand Limit — Demand limit is a feature that allowsusage. This allows the owner to keep energy costs down. Thereare three types of demand limiting that can be configured. Thefirst type ihttp://www.51wendang.com/doc/437ec10ed908de0667a81455s through 2-step switch control, which will reducethe maximum capacity to 2 user configurable percentages. Thesecond type is by 4 to 20 mA signal input which will reduce themaximum capacity linearly between 100% at a 4 mA inputsignal (no reduction) down to the user-configurable level at a20 mA input signal. The third type uses the CCN Loadshedmodule and has the ability to limit the current operating capaci-ty to maximum and further reduce the capacity if required. De-mand limit control can be based on a calculated capacity levelor by compressor current level.

: If using the compressor current level for demand limit,take into account the other power draws such as the condenser-fan motors when determining the limit value desired.

CONTROLLED  DEMAND  LIMIT — The trol system is capable of demand limit based on a field-sup-con-plied switch for 1-step demand limit or 2 switches for 2-stepdemand limit. One-step demahttp://www.51wendang.com/doc/437ec10ed908de0667a81455nd limit is standard. The 2-stepswitch control of demand limiting requires the Energy Man-agement Module (EMM). Demand limit steps are controlledby two relay switch inputs field wired to TB5-5 and TB5-14for Switch 1 and TB6-14 and TB6-15 for Switch 2.

limit contact will put the unit on the first demand limitFor demand limit by switch control, closing the first de-level, either by capacity or compressor current. The unit willnot exceed the percentage of capacity or compressor currententered as Demand Limit Switch 1 set point. Closing contactson the second demand limit switch prevents the unit from ex-ceeding the demand limit entered as Demand Limit Switch 2set point. The demand limit percent capacity or compressorcurrent that is set to the lowest demand takes priority if both de-mand limit inputs are closed. If the demand limit percentagedoes not match unit operation, the unit will limit capacity orcurrent to the closest shttp://www.51wendang.com/doc/437ec10ed908de0667a81455tep without exceeding the value.

by configuring the Demand Limit Select variable (To use demand limit, select the type of demand limiting tomand Limit Type SelectDemand Limit set points based on the type selected.

, DMDC) to Switch. Configure theDe-stalled. One-step demand limit control does not require the en-ergy management module. To configure Demand Limit forswitch control, three parameters for 1-step switch control mustbe configured. For 2-step control, four parameters must beconfigured. The parameters are: the type of Demand LimitSelection (for Switch Limit Set Point 1 (Demand Limit Type SelectThe setting for Switch Limit Set Point 2 (Switch Limit Setpoint 1, DMDC), the setting, DLS1),point 2,Switch Limit Set-lect, CUR.S DLS2). Current Limit Select must be set to NO.), and Current Limit Select (Current Limit Se-To configure this option with the Touch Pilot  display:

NAMEPATHLINE NO.

://www.51wendang.com/doc/437ec10ed908de0667a81455

Limit

SelectConfig USER

(Switch Control)Default = 0 (None)Switch Limit

1Setpoints SETPOINT

Default = 100%Switch Limit Setpoint 2Setpoints SETPOINT34(Not required for 1-Step)

= 100%Current Limit Select

USER

= No

configure this option with the Navigator  display:

EXPANSIONPATH

Limit Select

RSETSWITCH

= NONEDLS1Switch Limit Setpoint 1Setpoints MISCDefault = 100%DLS2Switch Limit Setpoint 2Setpoints MISC(Not required for 1-Step)

= 100%CUR.S

Limit Select

OPTN

: NO

is desired with the first switch closure limiting theIn the following example, 2-step demand limit based oncapacity to 60%. The second switch closure is to limit thecapacity to 40%.http://www.51wendang.com/doc/437ec10ed908de0667a81455 Demand Limit Switch 1 is 60% and DemandLimit Switch 2 is 40%.

PILOT DISPLAYNAVIGATOR DISPLAY

NameValue

Limit Type Select1DMDCSWITCHSwitch Limit Setpoint 160%DSL160%Switch Limit Setpoint 240%DSL240%Current Limit SelectNo

.SNO

. One-step demand limit control does not require theenergy management module. Four parameters for 1-step switchcontrol must be configured. For 2-step control, five parametersmust be configured. The parameters are: the type of DemandLimit Selection (setting for Switch Limit Set Point 1 (Demand Limit Type Select, DMDCDLS1Setpoint 2), the setting for Switch Limit Set Point 2 (Switch Limit Setpoint 1), the,Select, DLS2), the Current Limit Select (Current LimitSwitch Limitsignal, (, CUR.SCurrent Limit at 100%), and the Compressor Current limit at 100%, CUR.F).

configure this option with the Touch Pilot display:

NAMEPhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ATH

NO.VALUEDemand Limit Type SelectConfig USER241 (Switch Control)Default = 0 (None)Switch Limit Setpoint 1Setpoints SETPOINT33Default = 100%Switch Limit Setpoint 2Setpoints SETPOINT34(Not required for 1-Step)

= 100%Current Limit Select

USER30YDefault = Noes

Limit at 100%

USER

= 2000.0 Amps

configure this option with the Navigator  display:

EXPANSIONPATH

Limit SWITCHSelectConfiguration RSETDefault = NONEDSL1Switch Limit Setpoint 1Setpoints MISCDefault = 100%

Switch Limit (Not required Setpoint 2Setpoints MISCfor 1-Step)Default = 100%CUR.SCurrent Limit Select

OPTNNO

: NOCUR.F

Limit at 100%

OPTN

= 2000

POWERED (4 to 20 mA) CAPACITYBASED DEMAND LIMIT — The module is required for 4 http://www.51wendang.com/doc/437ec10ed908de0667a81455to 20 mA demand limit control. Anenergy managementexternally powered 4 to 20 mA signal must be connected toTB6-1 and TB6-2. To configure demand limit for 4 to 20 mAcontrol based on unit capacity, four parameters must be config-ured. The parameters are: the type of Demand Limit Selection39

(100% capacity limit takes place (Demand Limit Type Select, DMDC), the current at whichLimitplace (, DMMXmA For 100% DemandLimit Selection (mA For 0% Demand Limit), the current at which 0% capacity limit takesCurrent Limit Select, DMZE, CUR.S), and the Current).

[此处图片未下载成功]

Care should be taken when interfacing with other controlsystems due to possible power supply differences such as afull wave bridge versus a half wave rectification. Connec-tion of control devices with different power supplies mayresult in permanent damage. incorporate power supplies with half wave rectification. AComfortLink  controlssignalhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 isolation device should be utilized if the signal gen-erator incorporates a full wave bridge rectifier.

configure this option with the Touch Pilot  display:

NAMEPATHLINE NO.

Limit Type SelectConfig USER242 (4-20mA Control)Default = 0 (None)mA For 100% Demand LimitConfig USER28Default = 0.0 mAmA For 0% Demand LimitConfig USER29Default = 10.0 mACurrent Limit Select

USER

= No

configure this option with the Navigator display:

EXPANSION

Limit

RSET4-20MA INPUTDefault = NONEDMMXmA for 100%

LimConfiguration RSETDefault = 0.0 mADMZEmA for 0%

Limit

RSETDefault = 10.0 mACUR.SCurrent Limit

OPTN

: NO

% and a 20 mA Demand Limit signal ishttp://www.51wendang.com/doc/437ec10ed908de0667a81455 0%. The 4 toIn the following example, a 4 mA signal is Demand Limit20 mA signal is connected to TB6-1 and TB6-2. The demandlimit is a linear interpolation between the two values entered. InFig. 24, if the machine receives a 12 mA signal, the machinecontrols will limit the capacity to 50%.

POWERED (4 to 20 mA) CURRENTBASED DEMAND LIMIT  — The module is required for 4 to 20 mA demand limit control. Anenergy managementexternally powered 4 to 20 mA signal must be connected toTB6-1 and TB6-2. To configure demand limit for 4 to 20 mAcontrol based on compressor current, five parameters must beconfigured. The parameters are: the type of Demand LimitSelection (which 100% capacity limit takes place (Demand Limit Type Select, DMDC), the current atDemand Limitlimit takes place (, DMMXmA For 100%Current Limit Selection (mA For 0% Demand Limit), the current at which 0% capacity, DMZE), thethe Compressor Current limit at 100% sighttp://www.51wendang.com/doc/437ec10ed908de0667a81455nal (Current Limit Select, CUR.S), andat 100%, CUR.F).

LimitTo configure this option with the Touch Pilot display:

NAMEPATHLINE NO.

Limit Type SelectConfig USER242 (4-20mA Control)Default = 0 (None)mA For 100% Demand LimitConfig USER28Default = 0.0 mAmA For 0% Demand LimitConfig USER29Default = 10.0 mACurrent Limit Select

USER30YDefault = No

Limit at 100%

USER

= 2000.0 Amps

configure this option with the Navigator display:

EXPANSIONPATH

Limit 4-20MA INPUTSelect

RSETDefault = NONEDMMX

for 100% Demand LimConfiguration RSETDefault = 0.0 mADMZEmA for 0%

Limit

RSETDefault = 10.0 mACUR.S

Limit

OPTNYES

: NOCUR.F

Limithttp://www.51wendang.com/doc/437ec10ed908de0667a81455

100%

OPTN

= 2000

compressor current is 2000 amps and a 20 mA DemandIn the following example, a 4 mA signal is Demand LimitLimit signal corresponds with a compressor current of 0 amps.The 4 to 20 mA signal is connected to TB6-1 and TB6-2. Thedemand limit is a linear interpolation between the two valuesentered. If the machine receives a 12 mA signal, the machinecontrols will limit the total compressor current capacity to1000 amps. See Fig. 25.

LOADSHED CONTROLLED DEMAND LIMIT —To configure Demand Limit for CCN Loadshed control, theunit Operating Type Control must be in CCN control. With theTouch Pilot  display, the machine must be started with CCNControl. For the Navigator  display, the Operating ControlType (I/O Button, OPER) must be CCN CONTROL.

module can force the demand limit variable andThe unit must be controlled by a Chillervisor module. Thhttp://www.51wendang.com/doc/437ec10ed908de0667a81455edirectly control the capacity of the machine. Additionally, theunit’s set point will be artificially lowered to force the chiller toload to the demand limit value.

Storage Operation — configured to make and store ice. The energy managementChiller operation can be

and an Ice Done Switch are required for operation inthe Ice Mode. In this configuration, the machine can operatewith up to three cooling set points: Cooling Set Point 1 (ing Setpoint 1,Cool-Cooling Set Point 2 ( CSP.1ing the Unoccupied period when the ice build is complete (IceCooling Setpoint 2) is used during the Occupied period;, CSP.2) is used dur-Done Switch is closed); and Cooling Ice Set Point (Ice SetpointCoolingwhile ice is building (Ice Done Switch is open).

, CSP.3) is used during the unoccupied periodTo configure this option with the Touch Pilot display:

NAMEPATH

NO.VALUEIce Mode Enable

://www.51wendang.com/doc/437ec10ed908de0667a81455

configure this option with the Navigator display:

EXPANSIONPATH

.M

Mode Enable

power cycle is required for the values to take effect.pable of broadcasting time, date, and holiday status to all ele-Broadcast Configuration — The 30XW chiller is ca-

in the CCN system. In the stand-alone mode, broadcastmust be activated to utilize holiday schedules and adjust fordaylight saving time. If the chiller is to be connected to a CCNsystem, determine which system element is to be the networkbroadcaster to all other system elements. Broadcast is activatedand deactivated in the BRODEFS Table. It is accessible fromTouch Pilot display (ConfigService Tool. It is not accessible through Navigator display. BRODEFS) or through Networka broadcast is activated by a device that has been designated asOnly one element should be http://www.51wendang.com/doc/437ec10ed908de0667a81455configured as a broadcaster. Ifa network broadcaster, then broadcasted time, date, and holidaystatus will be updated over the CCN system. If broadcast is en-abled, a broadcast acknowledger must also be enabled. The

[此处图片未下载成功]

acknowledger cannot be the same machine as the broadcastingmachine.ACTIVATE — The Activate variable enables the broadcastfunction of the ComfortLink controls. If this variable is set to 0,this function is not used and holiday schedules and daylightsavings compensation are not possible. Setting this variable to1 allows the machine to broadcast and receive broadcasts onthe network. The following information is broadcast: the timewith compensation for daylight savings, date, and holiday flag.Set this variable to 2 for stand-alone units that are not con-nected to a CCN. With this configuration, daylight saving timeand holiday determination will be done without broadcastingthrough the bushttp://www.51wendang.com/doc/437ec10ed908de0667a81455. This variable can only be changed when usingthe Touch Pilot display, ComfortVIEW  software, or

Service Tool. This variable cannot be changed withthe Navigator display.

configure this option with the Touch Pilot display:

NAMEActivate

[此处图片未下载成功]

BRODEFS

NO.

= 0 to 2Default = 2

ACKNOWLEDGER  —  This configurationdefines if the chiller will be used to acknowledge broadcastmessages on the CCN bus. One broadcast acknowledger isrequired per bus, including secondary buses created by the useof a bridge. This variable can only be changed with the TouchPilot display, ComfortVIEW software, or Network Service

Tool. This variable cannot be changed with the Navigatordisplay.

configure this option with the Touch Pilot display:

NAMEPATH

NO.

://www.51wendang.com/doc/437ec10ed908de0667a81455adcast acknowledger

-ID

Control

ROUTING CONTROL — Alarms recorded on thechiller can be routed through the CCN. To configure this op-tion, the which CCN elements will receive and process alarms. Input forComfortLink control must be configured to determinethe decision consists of eight digits, each of which can be set toeither 0 or 1. Setting a digit to 1 specifies that alarms will besent to the system element that corresponds to that digit. Set-ting all digits to 0 disables alarm processing. The factory de-fault is 00000000. See Fig. 26. The default setting is is basedon the assumption that the unit will not be connected to a net-work. If the network does not contain a ComfortVIEW, Com-fortWORKS&#174;abling this feature will only add unnecessary activity to the, TeLink, DataLINK , or BAClink module,  en-CCN communication bus.

be modified with the Navigator dhttp://www.51wendang.com/doc/437ec10ed908de0667a81455isplay.

option can be modified by the Touch Pilot display. It11010000. This Alarm Routing status will transmit alarms toTypical configuration of the Alarm Routing variable isComfortVIEW software, TeLink, BAClink, and DataLINK.To configure this option with the Touch Pilot display:

NAMEPATH

NO.

Routing Control

ALARMDEF

= 00000000

EQUIPMENT PRIORITY — The device uses the equipment priority value when sorting alarmsComfortVIEWby level. The purpose of the equipment priority value is to de-termine the order in which to sort alarms that have the samelevel. A priority of 0 is the highest and would appear first whensorted. A priority of 7 would appear last when sorted. For ex-ample, if two chillers send out identical alarms, the chiller withthe higher priority would be listed first. The default is 4. Thisvariable can only be changed whehttp://www.51wendang.com/doc/437ec10ed908de0667a81455n using the Touch Pilot dis-play, ComfortVIEW software, or Network Service Tool. Thisvariable cannot be changed with the Navigator  display. Toconfigure this option with the Touch Pilot  display:

NAMEPATH

NO.

Equipment Priority

ALARMDEF

= 0 to 7Default = 4

FAILURE RETRY TIME — This vari-able specifies the amount of time that will be allowed to elapsebetween alarm retries. Retries occur when an alarm is notacknowledged by a network alarm acknowledger, which maybe either a ComfortVIEW software or TeLink. If acknowledge-ment is not received, the alarm will be re-transmitted after thenumber of minutes specified in this decision. This variable canonly be changed with the Touch Pilot display, ComfortVIEW,or Network Service Tool. This variable cannot be changed withthe Navigator display. To configure this option with the TouchPilot display:http://www.51wendang.com/doc/437ec10ed908de0667a81455

NAMEPATH

NO.

Failure Range =

Time

ALARMDEF

to 240 minutesDefault = 10 minutes

-ALARM TIME — This variable specifies the amount oftime that will be allowed to elapse between re-alarms. A re-alarm occurs when the conditions that caused the initial alarmcontinue to persist for the number of minutes specified in thisdecision. Re-alarming will continue to occur at the specified

until the condition causing the alarm is corrected. Thisvariable can only be changed with the Touch Pilot display,ComfortVIEW, or Network Service Tool. This variable cannotbe changed with the Navigator display. To configure this optionwith the Touch Pilot display:

NAMEPATH

NO.

Time

ALARMDEF

= 1 to 254 minutes255 = Re-Alarm DisabledDefault = 30 minutes

://www.51wendang.com/doc/437ec10ed908de0667a81455M SYSTEM NAME — This system element name that will appear in the alarms generatedvariable specifies theby the unit control. The name can be up to 8 alphanumericcharacters in length. This variable can only be changed whenusing the Touch Pilot display, ComfortVIEW, or NetworkService Tool. This variable cannot be changed with theNavigator display.

configure this option with the Touch Pilot display:

NAMEPATH

NO.

System Name

ALARMDEF

= PRO_XAXQ

Saving  Time  Configuration   — 30XW chiller control contains software which can automati- The

correct for daylight saving time. This software is accessi-ble from the Touch Pilot display, ComfortVIEW, or NetworkService Tool. It is not accessible through the Navigator display.1. The start of Daylight Saving must be configured by settingTo enable this feature, Daylight Saving Selhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ect must be set tothe Month, Day of Week, and Week of Month. The end forDaylight Saving must also be configured. To configure this op-tion with the Touch Pilot display, see Table 33.

33 — Daylight Savings Time Configuration

NAMEPATH

NO.

BRODEFS11 or 2

= 2Daylight

SelectConfig BRODEFS7Enable

= Dsble

MonthConfig BRODEFS9Enter Starting Month for

SavingDay of Week (1=Monday)Config BRODEFS10Enter the Day of the Week Daylight Saving StartsWeek of MonthConfig BRODEFS11Enter Week of the Month Daylight Saving StartsLeavingConfigBRODEFS12MonthConfig BRODEFS13Enter Ending Month for

SavingDay of Week (1=Monday)Config BRODEFS14Enter the Day of the Week Daylight Saving endsWeek of Month

BRODEFS

Week of the Month Daylight Saving endsCapacity Chttp://www.51wendang.com/doc/437ec10ed908de0667a81455ontrol Overrides — pacity control overrides (The following ca-

modify the normal operation routine. If any of the overrideActive Capacity Override, CAP.S)conditions listed below are satisfied, the override will deter-mine the capacity change instead of the normal control. Over-rides are listed by priority order and are often linked to unit op-erating modes. See Table 34 for a list of overrides. See the Op-erating Modes section on page 56 for more informationregarding operating modes.

Temperature is less than Brine Freeze Set Point (Freeze SetpointBrinecapacity is removed.

, LOSP)   2.0&#176; F (1.1&#186; C) then a stage of42

NOTE: The freeze set point is 34 F (1.1 C) for fresh watersystems (Cooler Fluid Type, FLUD=1). The freeze set pointis Brine Freeze Set Point (Brine Freeze Setpoint, LOSP), forMedium Temperature Brine systems (Cooler Fluid Type,FLUD=2).

overrides attempt to avohttp://www.51wendang.com/doc/437ec10ed908de0667a81455id the low suction temperaturealarms and are active only when the compressor is runningbeyond the fully unloaded level. The slide valve in the affectedcircuit will be decreased in position if the Saturated SuctionTemperature is less than Brine Freeze Set Point (Brine FreezeSetpoint, LOSP) –18.0 F (–10 C) for 90 seconds, or the Satu-rated Suction Temperature is less than –4 F (–20 C).

Point, CTPT) andthe Leaving Water Temperature (Cooler Leaving Fluid, LWT)reaches a predetermined limit and the rate of change of the wa-ter is 0&#186; F per minute or still decreasing.

(Cooler Entering Fluid, EWT) is less than the Control Point(Control Point, CTPT).

Select, RL.S=ENBL) and the difference between theLeaving Water Temperature and the Control Point is greaterthan 4&#186; F (2.2&#186; C) and the rate of change of the leaving water isgreater than Cool Ramp Loading Rate (Cooling Ramp Load-ing, CRMP). Opehttp://www.51wendang.com/doc/437ec10ed908de0667a81455rating mode 5 (MD05) will be in effect.

. The user can then use Service Test functions to test theunit. All safeties and higher priority overrides are monitoredand acted upon.

: The user cannot activate this override mode.

unit capacity is greater than the active capacity limitvalue, a stage is removed. If the current capacity is lower thanthe capacity limit value, the control will not add a stage thatwill result in the new capacity being greater then the capacitylimit value. Operating mode 4 (MD04) will be in effect.

(Cooler Flow Switch, LOCK) is closed.

Temperature (Cooler Leaving Fluid, LWT) and theControl Point (Control Point, CTPT) exceeds a calculatedvalue and the rate of change of the water temperature is greaterthan –0.1&#186; F/min, a stage will be added.

Gas Bypass Select, HGBP)and is set to 1, 2 or 3. This override will add a stage of capacityif the next shttp://www.51wendang.com/doc/437ec10ed908de0667a81455tage is Minimum Load Control, when the differ-ence between the Leaving Water Temperature (Cooler Leav-ing Fluid, LWT) and the Control Point (Control Point, CTPT)exceeds a calculated value and the rate of change of the watertemperature is greater than a fixed value.

at this capacity stage for the next 90 seconds. Duringthis time, no capacity control algorithm calculations will bemade. If the capacity step is a compressor, an additional90-second delay is added to the previous hold time (see Over-ride #22). This override allows the system to stabilize beforeanother capacity stage is added or removed. If a condition of ahigher priority override occurs, the higher priority override willtake precedence. Operating Mode 10 (MD10) will be in effect.is close to the control point and slowly moving towards it.ers, the unit will increase capacity to attempt to load to the de-mand limited value.

is run every 4 seconds. Ihttp://www.51wendang.com/doc/437ec10ed908de0667a81455f the Saturated Condensing Tem-perature for the circuit is above the High Pressure Threshold(High Pressure Threshold, HP.TH) then the position of slidevalve will be unloaded.

(Heat/Cool Status, HC.ST=2).

[此处图片未下载成功]

43

Table 34 — Capacity Control Overrides

CONTROL OVERRIDES

Cooler Freeze Protection

Circuit A Low Saturated Suction Temperature in Cooling3Circuit B Low Saturated Suction Temperature in Cooling4—

Low Temperature cooling and High Temperature Heating (LWT)6Low Temperature cooling and High Temperature Heating (EWT)7Ramp Loading

Service Manual Test Override9Demand Limit

Cooler Interlock Override

High Temperature Cooling and Low Temperature Heating12High Temperature Cooling and Low Temperature Heating (minimum load control in effect)

Minimum On/Off and Off/On Time Delay14Slow Change Override

System Manager Capacihttp://www.51wendang.com/doc/437ec10ed908de0667a81455ty Control16Circuit A High Pressure Override17Circuit B High Pressure Override18—

Standby Mode20—21—

Minimum On Time Delay

Circuit A Low Saturated Suction Temperature in Cooling24Circuit B Low Saturated Suction Temperature in Cooling25—26—27—28—29—30—31—32—33—

Circuit A Low Refrigerant Charge35Circuit B Low Refrigerant Charge36—37—38—39—40—

Circuit A High Current Override42Circuit B High Current Override43—

Circuit A High Suction Superheat at Part Load45Circuit B High Suction Superheat at Part Load46—47—48—49—50—51—52—

Circuit A Delay for Unloading the Slide Valve54Circuit B Delay for Unloading the Slide Valve55—56—57—58—

Circuit A Low Oil Level60Circuit B Low Oil Level61—

Circuit A High Motor Temperature Override63Circuit B High Motor Temperature Override64—65—

Circuit A High Discharge Gas Override67

B High Discharge Gas Overridehttp://www.51wendang.com/doc/437ec10ed908de0667a81455

capacity changes, an will be added to Override #13 delay. No compressor will beadditional 90-second delaydeenergized until 3 minutes have elapsed since the last com-pressor has been turned ON. When this override is active, thecapacity control algorithm calculations will be performed, butno capacity reduction will be made until the timer has expired.A control with higher precedence will override the MinimumOn Time Delay.

same point or unload to raise the saturated suction tempera-ture. This algorithm will be active if at least 1 compressor in thecircuit is on and one of the following conditions is true:

.Saturated Suction Temperature is less than the BrineFreeze Setpoint ((3.3&#186; C).

Freeze Setpoint, LOSP) –6&#186; F2.Saturated Suction Temperature is less than the BrineFreeze Setpoint (circuit approach (Leaving Water Temperature – SaturatedBrine Freeze Setpoint, LOSP) and theSuctiohttp://www.51wendang.com/doc/437ec10ed908de0667a81455n Temperature) is greater than 15&#186; F (8.3&#186; C) andthe Circuit Superheat (Discharge Gas Temperature – Sat-urated Discharge Temperature) is greater than 25&#186; F(13.9&#186; C).

: The freeze set point is 34 F (1.1 C) for freshwater systems (freeze set point is Brine Freeze Set Point (Cooler Fluid Type, FLUD=1). TheSetpointsystems (, LOSPBrine FreezeCooler Fluid Type), for Medium Temperature Brine, FLUD=2).

, 21 (Circuit A) or 22 (Circuit B) will be in effect.If any of these conditions are met, the appropriate operatinging with no refrigerant in the circuit. This algorithm runs onlywhen the circuit is not operational (compressors is OFF). Thereare several criteria that will enable this override:

.The saturated suction temperature or saturated dischargetemperature is less than –13 F (–25 C).2.Both of these conditions must be true:

.The saturated suction temperature or saturateddischarge temhttp://www.51wendang.com/doc/437ec10ed908de0667a81455perature is less than leaving fluidtemperature by more than 5.4&#186; F (3.0&#186; C).

.Saturated suction temperature or saturated dis-charge temperature is less than 41 F (5 C).3.All of these conditions must be true:

.The saturated suction temperature or saturateddischarge temperature is less than leaving fluidtemperature by more than 5.4&#186; F (3.0&#186; C).

.Saturated suction temperature or saturated dis-charge temperature is less than 41 F (5 C).

.Saturated suction temperature or saturated dis-charge temperature is less than the brine freezepoint (than 6&#186; F (3.3&#186; C).

Freeze Setpoint, LOSP) by moreNOTE: The freeze set point is 34 F (1.1 C)for fresh water systems (FLUDBrine Freeze Setpoint,point (=1). The freeze set point is brine freeze settemperature brine systems (Brine Freeze Setpoint, LOSP), for mediumFLUD=2).

Fluid Type,4.Both of these conditions must be thttp://www.51wendang.com/doc/437ec10ed908de0667a81455rue:

.The saturated suction temperature or saturateddischarge temperature is less than leaving fluidtemperature by more than 5.4&#186; F (3.0&#186; C).

b.Saturated suction temperature or saturated dischargetemperature is less than 41 F (5 C).

operating mode, 21 (Circuit A) or 22 (Circuit B) will be inIf any of these conditions 1, 2, 3 or 4 are met, the appropri-effect.

is run every 4 seconds. If the compressor current is great-er than 79% of must trip amps (MTA) but less than 85% MTAthen the capacity will be held at current capacity. If the com-pressor current is greater than 85% MTA then capacity will bereduced by repositioning the slide valve until the current is lessthan 85% MTA (Must Trip Amps, MTA.X).

90% open and the suction superheat is higher than thesuperheat control point for more than 5 minutes, then the cir-cuit will be shut down.

or power cycle. http://www.51wendang.com/doc/437ec10ed908de0667a81455A delay of 20 minutes will elapse for allunits. The delay allows the slide valve of the compressor tomove back to its fully unloaded position. The delay is adjustedaccording to the percent of the compressor running capacitybefore it is shut down. If the compressor is stopped normally,no delay will be applied. If the compressor is shut down by thelocked rotor alarm, a full delay will be applied before the com-pressor is allowed to re-start.

the circuit from starting up with a low oil level. If thisoverride occurs three times, the low oil level alarm will betripped.

— This override prevents the compressor motor temperaturefrom rising above the high temperature limit, but still allowsthe chiller to run close to the high temperature limit by unload-ing the compressor. If the motor temperature is greater than214 F (101.1 C), the compressor will not load. This overridewill remain active until the temperature drops belhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ow 214 F(101.1 C). If the motor temperature is greater than 225 F(107.2 C) for 60 seconds, the circuit capacity will decrease byone stage. If the motor temperature is greater than 228 F(108.9), the circuit capacity will decrease by one stageimmediately.

—1.If the leaving fluid temperature exceeds the freeze set-point (LOSP)   5.4 &#176;F (3 &#176;C) and the compressor is not atfull load, the compressor capacity will be increased whendischarge gas temperature exceeds 190 F (87.8 C). Com-pressor capacity will be allowed to continue increasinguntil discharge gas temperature falls below 175 F(79.4 C).  When the temperature is above the limit minus2&#176; F (1.1&#176; C) increase in capacity will not be allowed.This override will remain active until the discharge gastemperature drops below the limit by –3&#176; F (–1.7&#176; C).

.If the leaving fluid temperature is 3.6 &#176;F (2 &#176;C) or morebelow the freeze setpoint (Lhttp://www.51wendang.com/doc/437ec10ed908de0667a81455OSP), the compressor capaci-ty will be decreased when discharge gas temperature ex-ceeds 190 F (87.8 C). If after five minutes, the dischargegas temperature falls below 175 F (79.4 C), the compres-sor will be allowed to load again.(MBB) uses the saturated condensing temperature input fromHead Pressure Control — The Main Base Board

discharge pressure transducer to control the head pressurecontrol signal. Head pressure control is maintained through acalculated set point which is automatically adjusted based onactual saturated condensing and saturated suction temperaturesso that the compressor(s) is (are) always operating within themanufacturer’s specified envelope. The control will automati-cally reduce the unit capacity as the saturated condensing tem-perature approaches an upper limit. See capacity overrides#16-18. The control will indicate through an operating modethat high ambient unloading is in effect. If the saturatedhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 con-densing temperature in a circuit exceeds the calculated maxi-mum, the circuit will be stopped. For these reasons, there areno head pressure control methods or set points to enter. Thecontrol will modulate the 0 to 10v head pressure control outputsignal when condensing temperature is below the minimumhead pressure requirement for the compressor. To use headpressure control, the optional MLV/COND board must be in-stalled. In addition, the Condenser Vtory configuration must be set to Yes and 0-10 V signal wiringalve Select item under fac-connections must be made to TB7 terminals 1 and 2.

CONDENSER FLUID TEMPERATURE HEADPRESSURE CONTROL OPTION — Units will start and op-erate down to 65 F (18.3 C) entering condenser water tempera-ture as standard. Operation with entering condenser water tem-peratures below 65 F (18.3 C) requires a field-supplied and in-stalled condenser fluid control valve.

position is controllhttp://www.51wendang.com/doc/437ec10ed908de0667a81455edboard, channel 9, to maintain the head pressure set point. Unitsizes 325-400 use a common condenser so the MBB uses thehighest saturated condensing temperature of either circuit. As asafety feature, if the circuit is on and if the saturated condens-ing temperature reaches the condensing set point  10&#176; F, thevalve is opened to its maximum position to avoid a high pres-sure alarm. The water valve is fully closed when the circuit isOFF on unit sizes 150-200 and if both circuits are off on unitsizes 325-400.

fully open when the unit operates in heating modeIf the unit is configured as a heat machine, the valve will beand when the condenser leaving water temperature becomesgreater than the head pressure set point.

. The minimum condenser valve position is very im-Maximum and minimum condenser valve position is con-portant to avoid condenser freeze risks as condenser freeze pro-tection is ensured byhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 the condenser pump.

configure this option with the Touch Pilot  display:

NAMEPATH

NO.

Water Val Sel

FACTORY13YES

Val

StpSetpoint

Range: 80 to120 F(26.7 to 48.9 C)Default: 86 F (30 C)Recl Valve Min Position

SERVICE119Range: 0 to 50?fault: 20%

Valve Max Position

SERVICE120Range: 20 to 100?fault: 100%Prop PID Gain Varifan

SERVICE16Range: -20 to 20Default: 2.0

PID Gain Varifan

SERVICE17Range: -5.0 to 5.0Default: 0.2

PID Gain Varifan

SERVICE1

: -20 to 20Default: 0.4

To configure this option with the Navigator  display:

EXPANSIONPATH

.V

Valve

UNITYESW.SCTWater Val Cond StpSetpoint Mhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ISCRange: 80 to140 F(26.7 to 60 C)

: 86 F (30 C)HR.MIReclaim Water Valve Min

SERVRange: 0 to 50?fault: 20%

.MA

Water Valve

SERVRange: 20 to 100?fault: 100%HD.PG

Proportion

SERVRange: –10 to 10Default: 2.0

.DG

Derivative

SERVRange: –10 to 10Default: 0.4

.IG

Integral Gain

[此处图片未下载成功]

SERV

: –10 to 10Default: 0.2

: Operation of the head pressure control valve can beverified by entering Quick Test. From the Navigator display,go to Service Test.A. From the Touch Pilot dis-play, go to MAIN MENU_TST1_VFANA.

-START-UP

: Complete the Start-Up Checklistfor 30XW Liquid Chillers at the end of this publication.The checklist assureshttp://www.51wendang.com/doc/437ec10ed908de0667a81455 proper start-up of a unit, andprovides a record of unit condition, applicationrequirements, system information, and operation atinitial start-up.

been completed.

not attempt to start the chiller until the following checksSystem Check

.Check to ensure the unit is level per the installationinstructions.

.Electrical power source must agree with unit nameplate.3.Check that auxiliary components, such as the chilled fluidand condenser fluid circulating pumps, air-handlingequipment, or any other equipment to which the chillersupplies liquid are operational. Consult manufacturer's in-structions. If the unit has field-installed accessories, besure all are properly installed and wired correctly. Referto unit wiring diagrams.

.Open compressor suction service valves (if equipped).5.Open discharge, liquid line, oil line, and economizer (ifequipped) service valves.

.Fill the chiller fluid circhttp://www.51wendang.com/doc/437ec10ed908de0667a81455uit with clean water (with recom-mended inhibitor added) or other non-corrosive fluid tobe cooled. Bleed all air out of high points of system. Ifunit is exposed to temperatures below 32 F (0&#176; C), suffi-cient inhibited propylene glycol or other suitable corro-sion inhibited antifreeze should be added to the chillerwater and condenser water circuit to prevent possiblefreeze-up. The chilled water loop must be cleaned beforethe unit is connected. To set the maintenance time forcleaning and inspecting loop strainers, go to Ctrl (days), days. Refer to the system pump package literature forW.FIL. Values for this item are counted asWater Filterspecific internal inspection/cleaning requirements.7.Check tightness of all electrical connections.

.Vshould be A-B-C for proper compressor rotation.

power supply phase sequence. The phase sequenceSTART-UPCAUTION

not manually operate contactors. Serious damage to thehttp://www.51wendang.com/doc/437ec10ed908de0667a81455

[此处图片未下载成功]

machine may result.

Start-Up — under supervision of a qualified refrigeration technician.

start-up should be done only

.Be sure all discharge, oil, and suction valves (if equipped)and liquid line service valves are open.

://www.51wendang.coming the unit control, set leaving-fluid set point (ing Setpoint 1necessary.

, CSP.1). No cooling range adjustment isCool-3.If optional control functions or accessories are beingused, the unit must be properly configured. Refer toConfiguration Options section for details.

.Start the chilled fluid and condenser pumps, if unit is notconfigured for pump control. (PUMP=0; Condenser Pump Sequence, Cooler Pumps SequenceHPUM = No),http://www.51wendang.complete the Start-Up Checklist to verify all componentsare operating properly.

.Check the cooler flow switch for proper operation. En-sure that the flow switchttp://www.51wendang.com/doc/437ec10ed908de0667a81455h input indicates closed when thepump is on and open when the pump is off.

.Turn Enable/Off/Remote contact switch to Enable position.8.Allow unit to operate and confirm that everything isfunctioning properly. Check to see that leaving fluidtemperature agrees with leaving set point Control Point(Control Point, CTPT).

Limitations

listed in Table 35.

— Unit operating temperature limits are65 F (18.3 F), field installed accessory head pressure controlvalve is required. Contact your Carrier representative fordetails.

duty application (below 40 F [4.4 C] LCWT) forchiller normally requires factory modification. Contactyour Carrier Representative for details regarding spe-cific applications. Operation below 40 F (4.4 C) LCWTwithout modification can result in compressor failure.Table 35 — Temperature Limits for Standard Units

Cohttp://www.51wendang.com/doc/437ec10ed908de0667a81455ndenser EWT11043.3Minimum Condenser EWT6518.3Maximum Condenser LWT*11847.8Maximum Cooler EWT 7021.1Maximum Cooler LWT6015.6Minimum Cooler LWT**

.4

—Entering Fluid (Water) TemperatureLWT—Leaving Fluid (Water) Temperature

*T140 F (60 C).

limit for high condensing/heat reclaim option units are  Pulldown can be accomplished from 95 F (35 C).

For sustained operation, EWT should not exceed 85 F (29.4 C).**Unit requires brine modification for operation below thistemperature.

VOLTAGE

Power Supply — Minimum and maximum acceptablesupply voltages are listed in the Installation Instructions.

3-Phase Supply Voltage — Never operate a motorwhere a phase imbalance between phases is greater than 2%.To determine percent voltage imbalance:

(BC) 239 – 236 = 3 v

(AC) 239 – 238 = 1 v

deviation ishttp://www.51wendang.com/doc/437ec10ed908de0667a81455 4 v.

.Determine percent voltage imbalance:

% Voltage Imbalance = 100 x

% Voltage Imbalance = 100 x

voltage deviation from   avg voltage

voltage

= 1.7%

voltage imbalance is satisfactory as it is below themaximum allowable of 2%.

: If the supply voltage phase imbal-ance is more than 2%, contact the local electricutility company immediately. Do not operate unituntil imbalance condition is corrected.

FLUID LOOP VOLUME — To obtain propertemperature control, loop fluid volume must be at least 3 gal-lons per ton (3.25 L per kW) of chiller nominal capacity for airconditioning and at least 6 gallons per ton (6.5 L per kW) forprocess applications. Refer to application information in Prod-uct Data literature for details.

RATE REQUIREMENTS — Standard chillers shouldbe applied with nominal flow rates within those listed in theEhttp://www.51wendang.com/doc/437ec10ed908de0667a81455vaporator and Condenser Flow Rates table. Higher or lowerflow rates are permissible to obtain lower or higher tempera-ture rises. Minimum flow rates must be exceeded to assureturbulent flow and proper heat transfer in the cooler. SeeTable 36. See Fig. 27-43 for cooler pressure drop curves.

maximum voltage deviation is the largest differencebetween a voltage measurement across 2 legs and the averageacross all 3 legs.

: Supply voltage is 240-3-60.

[此处图片未下载成功]

AB = 243vBC = 236vAC = 238v

.Determine average voltage:Average voltage=

236 238

==

239

.Determine maximum deviation from average voltage:

(AB) 243 – 239 = 4 v

Fluid/Entering FluidMinimumMaximum40 F (4.4 C)/60 F (15.6 C)/45 F (7.2 C)70 F (21.1 C)MinimumMaximumFlow RateFlow RateGPML/sGPML/s20012.672045.438424.2152095.91207.648030.321313.476548.340825.716151http://www.51wendang.com/doc/437ec10ed908de0667a8145501.91288.051032.224115.286954.846329.21834115.71459.157936.530119.01085  68.457936.52290144.518111.472345.632920.71183  74.663139.82497157.519712.478849.735722.51285  81.168543.22712171.121413.585754.040325.4114991.477348.83059193.024215.296660.942927.0154497.482351.93259205.625716.2102964.948130.41733109.392458.33658230.828918.2115572.9

36 — Evaporator and Condenser Flow Rates

Fluid/Entering FluidMinimumMaximum*70 F (21.1 C)/118 F (47.8 C)/65 F (18.3 C)110 F (43.3 C)MinimumMaximumFlow RateFlow RateGPML/sGPML/s24015.196060.648030.31600100.9————25516.1102064.451032.21700107.3————29018.31158731.057936.51930121.8————36222.8144791.372345.62411152.1————39424.9157799.578849.72628165.8————42827.01713108.185754.02855180.1————48330.51932121.996660.93220203.2————51532.52058129.8102964.93430216.4————57836.42310145.7115572.93850242.9————

RateGPML/s38http://www.51wendang.com/doc/437ec10ed908de0667a81455424.238424.238424.240825.740825.740825.746329.246329.246329.257936.557936.546329.263139.863139.846329.268543.268543.246329.277348.877348.877348.882351.982351.982351.992458.392458.392458.3

RateGPML/s48030.348030.3——51032.251032.2——57936.557936.5——72345.672345.6——78849.778849.7——85754.085754.0——96660.996660.9——102964.9102964.9——115572.9115572.9——

XW UNIT

pass

passThree passTwo passOne passThree passTwo passOne passThree passTwo passOne passThree passTwo passOne passThree passTwo passOne passThree passTwo passOne passThree passTwo passOne passThree passTwo passOne passThree pass

*Maximum condenser fluid temperature shown for standard condensingoption. High condensing or heat machine option may have leaving fluid tem-peratures up to 140 F (60 C) and entering up to 128http://www.51wendang.com/doc/437ec10ed908de0667a81455 F (53.3 C).

CAUTION

[此处图片未下载成功]

Operation below minimum flow rate could generatealarms, which could result in damage to the cooler.

[此处图片未下载成功]

Consult application data section in the Product Dataliterature and job design requirements to determine flow raterequirements for a particular installation.

[此处图片未下载成功]

48

[此处图片未下载成功]

49

[此处图片未下载成功]

[此处图片未下载成功]

50

[此处图片未下载成功]

[此处图片未下载成功]

51

[此处图片未下载成功]

[此处图片未下载成功]

52

[此处图片未下载成功]

[此处图片未下载成功]

53

[此处图片未下载成功]

[此处图片未下载成功]

54

[此处图片未下载成功]

[此处图片未下载成功]

55

[此处图片未下载成功]

OPERATION

of Operation — With a command to startthe chiller, the cooler and condenser pumps will start. Afterverifying water flow, the control will monitor the http://www.51wendang.com/doc/437ec10ed908de0667a81455entering andleaving water temperatures. If the need for mechanical coolingis determined, the control decides which circuit and compres-sor to start. The control will start the required compressor com-pletely unloaded. The control will continue to load this circuitby moving the slide valve to satisfy cooling requirements.Once fully loaded, the control will start an additional circuit(sizes 325-400 only) to satisfy the load as required.

those chillers configured for heat machine duty, the con-trol will load compressors to satisfy the required heating setpoint provided there is a cooling load. Operating as a heat ma-chine requires the unit configuration of thr Unit Type (TYPE),High Condensing Select (H.CON), and Heat Cool Select(HC.SE) parameters.

of each circuit under normal conditions occurs inthe opposite sequence to loading. Once the circuit is fully un-loaded the compressor is shut off and the EXV will clhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ose com-pletely.

to start the chiller, the master chiller determineswhich chiller will become the lead chiller based on the configu-ration of Lead Lag Select, LLBL and Lead/Lag Balance Da-ta, LLBD. The lead chiller is always started first and the lagchiller is held at zero percent capacity by the master chillerforcing the lag demand limit value to 0%. If Lead PulldownTime (Lead Pulldown Time, LPUL) has been configured, thelead chiller will continue to operate alone for that specifiedtime. After the Lead Pulldown Time timer has elapsed andwhen the lead chiller is fully loaded, either all available com-pression is on or at the master demand limit value, then the lagstart timer (Lag Start Timer, LLDY) is initiated. When thepulldown timer and lag start timer has elapsed and the Com-bined Leaving Chilled Water Temperature is more than 3&#176; F(1.7&#176; C) above the set point, then the lag chiller is started. If the

://www.51wendang.com/doc/437ec10ed908de0667a81455r56

chiller’s water pump was not started when the machineswent into occupied mode, the lag chiller water pump will bestarted. The lag chiller will start with the master chiller forcingthe lag chiller demand limit value (LAG_LIM) to the master’sdemand limit value. If lead/lag capacity balance is selected,once the lag chiller has started, the master shall try to keep thedifference in capacity between lead and lag less than 20%. Themaster shall then be responsible for water loop capacitycalculation, and will determine which chiller, the lead or lag,will increase or decrease capacity. When the load reduces, thelag chiller will be the first chiller to unload. To accomplish this,the lead chiller set point is decreased by 4&#176; F (2.2&#176; C) until thelag chiller unloads.

OPERATION — For parallel chiller pump operation,the lead chiller’s water pump will be started. The lag chiller’swater pump will be maintained offhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 if Lag Unit Pump Control,LAGP=0. The internal algorithm of lead chiller will control ca-pacity of the lead chiller.

series chiller operation, the pump is always controlledby the master chiller.

Modes — Operating modes are override

Chiller Sequence of Operation  —  With a

that affect normal operation of the equipment. Morethan one operating mode can be in effect at the same time.Some operating modes have corresponding capacity controloverrides in the Capacity Control Overrides section onpage 42.

the Touch Pilot display, the status of the operatingmodes can be found in the MODES submenu, which is underthe STATUS menu. Each operating mode and its status (Yes =active, No = inactive) is listed.

[此处图片未下载成功]

For the Navigator display, the status of the operating modescan be found in the MODE submenu under the OPERATINGMODES menu. The 6 top priority operating http://www.51wendang.com/doc/437ec10ed908de0667a81455modes are dis-played in MD01 through MD06. To view the modes with theNavigator display:

MD02MD03MD04MD05MD06

EXPANSIONFirst Active ModeSecond Active ModeThird Active ModeFourth Active ModeFifth Active ModeSixth Active Mode

modes MODEOperating modesMODEOperating modes MODEOperating modes MODEOperating modes MODEOperating modesMODE

-320-320-320-320-320-32

Table 37 for a list of operating modes.

DELAY IN EFFECT — This mode is checkedfor when the unit is started. This mode is active when the Min-utes Off Time (Unit Off to On Delay, DELY) timer is active.The unit will not start until the timer has expired. The modewill terminate when the timer expires.

SETPOINT IN USE — This mode is checked forwhen the unit is ON. The mode is active when Cooling Set-point 2 (Cooling Setpoint 2, CSP.2) or Ice Setpoint (CoolingIce Setpoint, CSP.3) ishttp://www.51wendang.com/doc/437ec10ed908de0667a81455 in use. While in this mode, the ActiveSetpoint (Current Setpoint, SETP) will show the CSP.2 orCSP.3 value.

in this mode, the unit will operate to the Cooling Set-point 2 (CSP.2) or Ice Setpoint (CSP.3). The mode will termi-nate when the Cooling Setpoint 2 (CSP.2) or Ice Setpoint(CSP.3) is no longer in use.

IN EFFECT — This mode is checked for when theunit is ON. The mode will be active when Temperature Reset(Cooling Reset Select, CRST) is enabled either by CRST=1(Outside Air Temperature), CRST=2 (Return Water), CRST=3(4-20 mA Input), or CRST=4 (Space Temperature) and reset isactive.

in this mode, the Active Setpoint (Current Setpoint,SETP) will be modified according to the programmed infor-mation and will be displayed as the Control Point (Control

, CTPT). The mode will terminate when the TemperatureReset is not modifying the active leaving water set point, caus-ing SETP to be the shttp://www.51wendang.com/doc/437ec10ed908de0667a81455ame as CTPT.DEMAND LIMIT ACTIVE — This mode is checked forwhen the unit is ON. The mode is active when Demand Limit(Demand Limit Type Select, DMDC) is enabled either byDMDC=1 (Switch), DMDC=2 (4-20 mA Input), or the NightTime Low Sound Capacity Limit (Capacity Limit, LS.LT).The Active Demand Limit Value (Active Demand LimitVal, LIM) will display the current demand limit according tothe programmed information and the unit’s capacity will be re-duced to the amount shown or lower. The mode will terminatewhen the Demand Limit command has been removed.RAMP LOADING ACTIVE — This mode is checked forwhen the unit is ON. The mode is active when Ramp Loading(Ramp Loading Select, RL.S) is enabled and the followingconditions are met:

.The leaving water temperature is more than 4&#176; F (2.2&#176; C)from the Control Point (Control Point, CTPT), and

.The rate of change of the leaving water temperature isgreater than the Cool Ramp http://www.51wendang.com/doc/437ec10ed908de0667a81455Loading (Cooling RampLoading, CRMP).

control will limit the percent capacity increase until oneof the two conditions above are no longer met, then the modewill terminate.

PUMPS ROTATION — This mode is checked forwhether the unit is ON or OFF. The mode is active when theCooler Pump Sequence (Cooler Pump Run Status,PUMP=2) (2 Pumps Automatic Changeover) and the PumpRotation Delta Timer (Pump Auto Rotation Delay, ROT.P)have expired.

control will switch the operation of the pumps. Thelead pump will operate normally. The lag pump will be started,becoming the lead, and then the original lead pump will be shutdown. This mode will terminate when the pump operation hasbeen completed.

37 — 30XW Operating Modes

OPERATING

NUMBER

EXPANSIONStartup Delay in EffectSecond Setpoint in UseReset in Effecthttp://www.51wendang.com/doc/437ec10ed908de0667a81455

Limit ActiveRamp Loading ActiveCooler Heater Active*Cooler Pumps RotationPump Periodic StartSystem Manager ActiveMast Slave Ctrl ActiveAuto Changeover ActiveFree Cooling ActiveReclaim Active

Low EWT LockoutCondenser Pumps RotationIce Mode in EffectLow Suction Circuit ALow Suction Circuit BHigh DGT Circuit AHigh DGT Circuit B

Pres Override Cir AHigh Pres Override Cir BLow Superheat Circuit ALow Superheat Circuit B

PILOT DISCRIPTIONStartup Delay in EffectSecond Setpoint in UseReset in Effect

Limit ActiveRamp Loading ActiveCooler Heater ActiveCooler Pumps RotationPump Periodic StartSystem Manager ActiveMast Slave Active

Changeover ActiveFree Cooling ActiveReclaim Active

Low EWT LockoutCondenser Pumps RotationIce Mode in EffectLow Suction Circuit ALow Suction Circuit BHigh DGT Circuit AHigh DGT Circuit B

Pres Override Cir AHigh Prehttp://www.51wendang.com/doc/437ec10ed908de0667a81455s Override Cir BLow Superheat Circuit ALow Superheat Circuit B

PILOTLINE NUMBER

PILOT

/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/No

*Not applicable.

PUMP PERIODIC START — This mode is active when thecooler pump is started due to the Periodic Pump Start configu-ration (has not run that day, a pump will be started and will run for 2Pump Sticking Protection, PM.PS=YES). If the pumpseconds at 2:00 PM. If the machine is equipped with dualpumps, Pump no. 1 will run on even days (such as day 2, 4, 6of the month). Pump no. 2 will run on odd days (such as day 1,3, 5 of the month). The mode will terminate when the pumpshuts down.

MANAGER ACTIVE — This when the unit is ON or OFF. This mode is active if a Systemmode is checkhttp://www.51wendang.com/doc/437ec10ed908de0667a81455edManager such as Building Supervisor, Chillervisor SystemManager, or another CCN device is controlling the machine.specific commands received from the System Manager. TheWhen this mode is active, the machine will respond to themode will be terminated if the System Manager control isreleased.

SLAchecked for if the machine is ON. This mode is active if MasterVE CONTROL ACTIVE — This mode isSlave Control has been enabled. This occurs when two ma-chines are programmed, one as the master (lectSlave Select, MSSL=, MSSL=21 [Master]) and the other as a slave (Master/Slave Se- [Slave]).

/pacity control commands issued by the master controller. ThisBoth the master and slave machines will respond to the ca-may include control point changes and demand limit com-mands. This mode will terminate when Master Slave Controlhas been disabled.

CHANGEOVER ACTIVE — This supported.

is notFREE COOLING ACTIhttp://www.51wendang.com/doc/437ec10ed908de0667a81455VE — This mode is not supported.RECLAIM ACTIVE — This mode is not supported.

HEAT ACTIVE — This mode is not supported.HEATING LOW EWT LOCKOUT — This supported.

is notCONDENSER PUMPS ROTATION — This checked for whether the unit is ON or OFF. The mode is activemode iswhen the condenser pump sequence (Sequence, (Pump Auto Rotation Delay, HPUM = Yes) and the pump rotation delta timerCondenser PumpROT.P) have expired.

MODE IN the unit is ON. This mode is active when Ice Setpoint (EFFECT — This mode is checked for whenIce SetpointSetpoint (, CSP.3) is in use. While in this mode, the ActiveCoolingSetpointpoint (, CSPCurrent Setpoint.3, SETP) will show the Cooling Ice(CSP.3CSP) is no longer in use.

.3). This mode will terminate when the Ice Setpoint value and the unit will operate to the Ice Set-DEFROST ACTIVE ON CIR A — This mode is not supported.DEFROST ACTIVE ON CIR B — This mode is not supporhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ted.LOW SUCTION CIRCUIT ALOW SUCTION CIRCUIT B

modes are checked when the circuit is ON. Theappropriate circuit mode will be active if one of the follow-ing conditions is true:

.If the circuit’s saturated suction temperature (SST) ismore than 6&#176; F (3.3&#176; C) less than the freeze point andboth the cooler approach (Leaving Water Temperature –SST) and superheat (Suction Gas Temperature – SST) aregreater than 15&#176; F (8.3&#176; C).

.If the circuit is ON and the circuit’s SST is more than18&#186; F (10.0&#186; C) below the freeze point for more than90 seconds.

.If the circuit’s saturated suction temperature is morethan 6&#176; F (3.3&#176; C) below the freeze point for more than3 minutes.

freeze point is 34&#176; F (1.1&#176; C). For medium temperatureFor a fresh water system (Cooler Fluid Type, FLUD =1),brine systems, (is Brine Freeze Set Point (Cooler Fluid TypeBrine Freeze Setphttp://www.51wendang.com/doc/437ec10ed908de0667a81455oint, FLUD=2), the freeze point, LOSP).teria 2 and 3 capacity will be decreased on the circuit. TheFor criterion 1, no additional capacity will be added. For cri-mode will terminate when the circuit’s SST is greater than thefreeze point minus 6&#176; F (3.3&#176; C) or the circuit has alarmed.Alarms 56 and 57 on page 78.If this condition is encountered, see Possible Causes forHIGH DGT CIRCUIT A

DGT CIRCUIT B — The circuit may be increased to reduce circuit discharge gascapacity of the affectedtemperature.

PRES OVERRIDE CIR A

PRES OVERRIDE CIR B — This for when the circuit is ON. The appropriate circuit mode willmode is checkedbe active if the discharge pressure for the circuit, DischargePressure Circuit A (Pressure Circuit B (Discharge Pressure, DP.A), DischargePressure Circuit C (the High Pressure Threshold (Discharge PressureDischarge Pressure, DP, DP.B), or DischargeHP.TH).

Pressure http://www.51wendang.com/doc/437ec10ed908de0667a81455Threshold.C), is greater than,minutes following the capacity reduction, the circuit’s saturatedThe capacity of the affected circuit will be reduced. Twocondensing temperature (SCTaffected circuit will not be allowed to add capacity for at least 5t 2) is calculated and stored. Theminutes following the capacity reduction. If after 5 minutes,the circuit’s saturated condensing temperature is less thanSCTwill be added. If additional capacity is required, the control willt 2 –3&#176; F (1.7&#176; C), and then if required, percent capacitylook for other circuits to add capacity.

temperature is less than SCTThis mode will terminate once the circuit’s saturated con-t 2 –3&#176; F (1.7&#176; C).

A1.03. on page 84.

this condition is encountered, see Possible Causes forLOW SUPERHEAT CIRCUIT A

SUPERHEAT CIRCUIT B — for when the circuit is ON. The appropriate circuit mode willThis mode is checkedbe http://www.51wendang.com/doc/437ec10ed908de0667a81455active if the circuit’s superheat (discharge gas temperature— SCT) is less than 18&#176; F (10&#176; C).

is greater than 18&#176; F (10&#176; C). The control will look forNo additional capacity will be added until the circuit’s su-other circuits to add capacity if additional steps of capacity arerequired. This mode will terminate once the affected circuit’ssuperheat is greater than 18&#176; F (10&#176; C).

PIf this condition is encountered, see Possible Causes for.11 and P.12 on page 80.

sense temperatures and up to 8 transducers to sense pressureSensors — The electronic control uses up to 13 thermistors

controlling chiller operation. These sensors are outlinedbelow. See Fig. 44 for thermistor and transducer locations.THERMISTORS (Tables 38-39B) — Thermistors monitoring the chiller’s operation include: cooler entering    wa-that areter, cooler leaving water, condenser entering water, http://www.51wendang.com/doc/437ec10ed908de0667a81455condenserleaving water, dual chiller leaving water, compressor suction gastemperature, compressor discharge gas temperature, economiz-er temperature, and compressor motor temperature. Thesethermistors are 5 kture versus resistance. The space temperature thermistor is 10  at 77 F (25 C) and are identical in tempera-kSee Fig. 44 for thermistor locations.

at 77 F (25 C) and has a different temperature vs. resistance.See Fig. 45 and 46.

On  all sizes, this thermis-the cooler.

water nozzle of the condenser. See Fig. 45 and 46. — On all sizes with heatthe entering water nozzle of the condenser.— On all sizes, thissor of each circuit. There is one thermistor for each circuit.end of the compressor for the circuit. There is one thermistorfor each circuit.

in a friction fit well located in the economizer line forthe circuit. There is one thermistor for each circuit.

in ehttp://www.51wendang.com/doc/437ec10ed908de0667a81455ach compressor. One spare is provided. — This sensor (part no.door space and is used for water temperature reset. The sensorshould be installed as a wall-mounted thermostat would be (inthe conditioned space where it will not be subjected to either acooling or heating source or direct exposure to sunlight, and 4to 5 ft above the floor).

temperature sensor wires are to be connected toterminals in the unit main control box. The space temperaturesensor includes a terminal block (SEN) and a RJ11 female con-nector. The RJ11 connector is used to access the Carrier Com-fort Network&#174; (CCN) system at the sensor. See Fig. 45 and 46.To connect the space temperature sensor (see Fig. 47):

://www.51wendang.coming a 20 AWG twisted pair conductor cable rated forthe application, connect one wire of the twisted pair to

SEN terminal and connect the other wire to the otherSEN terminal located under the cover of thehttp://www.51wendang.com/doc/437ec10ed908de0667a81455 spacetemperature sensor.

.Connect the other ends of the wires to terminals 7 and 8on TB6 located in the unit control box.

on the CCN can be monitored from the space at thesensor through the RJ11 connector, if desired. To wire the RJ11connector into the CCN:

.Cut the CCN wire and strip ends of the red ( ), white(ground), and black (–) conductors. (If another wire colorscheme is used, strip ends of appropriate wires.)

.Insert and secure the red ( ) wire to terminal 5 of thespace temperature sensor terminal block.

.Insert and secure the white (ground) wire to terminal 4 ofthe space temperature sensor.

.Insert and secure the black (–) wire to terminal 2 of thespace temperature sensor.IMPORTANT: The cable selected for the RJ11connector wiring MUST be identical to the CCNcommunication bus wire used for the entire network.Refer to Table 11 for acceptable wiring.

.Connect the othehttp://www.51wendang.com/doc/437ec10ed908de0667a81455r end of the communication bus cable tothe remainder of the CCN communication bus.

: The Energy Management Module (EMM) is requiredfor this accessory.

— There are four pressure transducers percircuit (3 per circuit for sizes 150 and 325), and two differenttypes of transducers: low pressure (green connector) and highpressure (black connector). See Fig. 44 for transducer loca-tions.

-pressure type:

Suction pressure transducer (SPT) Economizer pressure transducer (EPT)High-pressure type:

Discharge pressure transducer (DPT) Oil pressure transducer (OPT)

38 — Thermistor Identification

ID

*SGTB*DGTADGTBECTAECTBDUALCAMTCBMTSPT

Entering Water ThermistorEvaporator Leaving Water ThermistorCondenser Entering Water ThermistorCondenser Leaving Water ThermistorCircuit A Suction Gas ThermistorCircuit Bhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 Suction Gas ThermistorCircuit A Discharge Gas ThermistorCircuit B Discharge Gas ThermistorCircuit A Economizer ThermistorCircuit B Economizer ThermistorDual Chiller LWT ThermistorCircuit A Motor TemperatureCircuit B Motor TemperatureSpace Temperature Thermistor

AT 77 F (25 C)

k  5k  5k  5k  5k  5k  5k  5k  5k  5k  5k  5k  5k  10k

POINTMBB-J6-CH2MBB-J6-CH1MBB-J6-CH4MBB-J6-CH5EXV1-J3-THAEXV2-J3-THACPM-A-J9-CH02CPM-B-J9-CH02EXV1-J3-THBEXV2-J3-THBMBB-J6-CH3CPM-A-J9-CH01CPM-B-J9-CH01EMM-J6-CH2

*SGTA and SGTB for 30XW150-325 units are connected to the EXV1 board.

Table 39A — 5K Thermistor Temperature (&#176;F) vs Resistance

(F)(Ohms)–2598,010–2494,707–2391,522–2288,449–2185,486–2082,627–1979,871–1877,212–1774,648–1672,175–1569,790–1467,490–1365,272–1263,133–1161,070–1059,081–957,162–855,311–753,526–651,804–550,143–448,541–346,996–245,505–144,06604http://www.51wendang.com/doc/437ec10ed908de0667a814552,679141,339240,047338,800437,596536,435635,313734,231833,185932,1761031,2021130,2601229,3511328,4731427,6241526,8041626,0111725,2451824,5051923,7892023,0962122,4272221,7792321,1532420,5472519,9602619,3932718,8432818,3112917,7963017,2973116,8143216,3463315,8923415,4533515,0273614,61437

,214

(F)(Ohms)3813,8263913,4494013,0844112,7304212,3874312,0534411,7304511,4164611,1124710,8164810,5294910,250509,979519,717529,461539,213548,973558,739568,511578,291588,076597,686607,665617,468627,277637,091646,911656,735666,564676,399686,238696,081705,929715,781725,637735,497745,361755,229765,101774,976784,855794,737804,622814,511824,403834,298844,196854,096864,000873,906883,814893,726903,640913,556923,474933,395943,318953,243963,170973,099983,031992,964100

,898

(F)(Ohms)1012,8351022,7731032,7131042,6551052,5971062,5421072,4881082,4361092,3851102,3351112,2861122,2391132,1921142,1471152,103116http://www.51wendang.com/doc/437ec10ed908de0667a814552,0601172,0181181,9771191,9371201,8981211,8601221,8221231,7861241,7501251,7151261,6801271,6471281,6141291,5821301,5501311,5191321,4891331,4591341,4301351,4011361,3731371,3451381,3181391,2911401,2651411,2401421,2141431,1901441,1651451,1411461,1181471,0951481,0721491,0501501,0291511,007152986153965154945155925156906157887158868159850160832161815162798163

(F)(Ohms)164765165750166734167719168705169690170677171663172650173638174626175614176602177591178581179570180561181551182542183533184524185516186508187501188494189487190480191473192467193461194456195450196445197439198434199429200424201419202415203410204405205401206396207391208386209382210377211372212367213361214356215350216344217338218332219325220318221311222304223297224289225

Table 39B — 5K Thermistor Temperature (&#176;C) vs Resistance

(C)(Ohms)–32100,260–3194,165–3088,480–2983,170–2878,125–2773,580–266http://www.51wendang.com/doc/437ec10ed908de0667a814559,250–2565,205–2461,420–2357,875–2254,555–2151,450–2048,536–1945,807–1843,247–1740,845–1638,592–1538,476–1434,489–1332,621–1230,866–1129,216–1027,633–926,202–824,827–723,532–622,313–521,163–420,079–319,058–218,094–117,184016,325115,5152

,749

(C)(Ohms)314,026413,342512,696612,085711,506810,959910,441109,949119,485129,044138,627148,231157,855167,499177,161186,840196,536206,246215,971225,710235,461245,225255,000264,786274,583284,389294,204304,028313,861323,701333,549343,404353,266363,13437

,008

(C)(Ohms)382,888392,773402,663412,559422,459432,363442,272452,184462,101472,021481,944491,871501,801511,734521,670531,609541,550551,493561,439571,387581,337591,290601,244611,200621,158631,118641,079651,041661,006679716893869906708767183672

(C)(Ohms)7377574747757197669377669786457962380602815838256483547845318551686502874898847789466904569144692436http://www.51wendang.com/doc/437ec10ed908de0667a8145593427944199541096402973939838599376100367101357102346103335104324105312106299107

62

[此处图片未下载成功]

SERVICE

Assembly  — 30XW175,200,250,275,300,350,400 units has an economizer Each circuit on

. The 30XW150,325 units do not have an economizerand have one main electronic expansion valve. The30XW150,325 units are controlled the same way as units witha separate economizer assembly. See Fig. 48.

Expansion Valve (EXV) — for a cutaway view of the EXVSee Fig. 49

enters valve through the top. As refrigerant passes through. High-pressure liquid refriger-the orifice, pressure drops and refrigerant changes to a 2-phasecondition (liquid and vapor). The electronic expansion valveoperates through an electronically controlled activation of astepper motor. The stepper motor stays in position unless pow-er pulses initiate the two discrete sets of motor stahttp://www.51wendang.com/doc/437ec10ed908de0667a81455tor windingsfor rotation in either direction. The direction depends on thephase relationship of the power pulses.

that are transformed into linear motion by theThe motor directly operates the spindle, which has rotatingtransmission in the cage assembly. The valve cone is a V-porttype which includes a positive shut-off when closed.

control of the refrigerant flow. The stepper motor has ei-The large number of steps and long stroke results in very ac-ther 4260 (main) or 2785 (economizer) steps.

EXV CONTROL — Each circuit has a thermistor lo-cated in a well in the discharge line of the compressor (DGT)and another one located in the compressor motor cavity (SGT).Each circuit also has discharge and suction pressure transducer.Discharge and suction pressure as measured by the transducersare converted to saturated temperatures.

[此处图片未下载成功]

[此处图片未下载成功]

heat to control the poshttp://www.51wendang.com/doc/437ec10ed908de0667a81455ition of the EXVthe temperature of the discharge gas and the saturated dis-. The difference betweencharge temperature is the superheat. The EXV module controlsthe position of the electronic expansion valve stepper motor tomaintain the discharge superheat set point.

to control the position of the EXVThe EXV control logic has several overrides, which are also.  Approach between SST and LWTMaximum Operating Pressure (MOP)

, is equal to or less than the pinch set point then theEXV will not open any further even though discharge super-heat set point is not met. Pinch set point is calculated usingsuction superheat, discharge superheat and pinch offset. Pinchoffset is used to adjust calculated pinch set point do to accuracyof transducers and thermistors.

to start at higher cooler fluid temperatures without over-loading the compressor. This is commonly referred to as MOP(maximum operating pressure). http://www.51wendang.com/doc/437ec10ed908de0667a81455If the SST is equal to or greaterthan the MOP set point then the MBB will try to control theEXV position to maintain the MOP set point.

between approximately 18 and 25 F (10 and 14 C), orThe discharge superheat leaving the compressor is main-less. Because EXV status is communicated to the Main BaseBoard (MBB) and is controlled by the EXV modules, it is pos-sible to track the valve position. The unit is then protectedagainst loss of charge and a faulty valve. During initial start-up,the EXV is fully closed. After an initialization period, valveposition is tracked by the EXV module by constantly monitor-ing the amount of valve movement.

EXV CONTROL — The is controlled by the circuit EXV board. There is an economizereconomizer EXVgas temperature thermistor and economizer pressure transducerlocated in the line, which runs from the economizer assembly tothe compressor. The economizer pressure is converted thttp://www.51wendang.com/doc/437ec10ed908de0667a81455o satu-rated temperature and is used to calculate economizer superheat.63

Economizer superheat equals economizer temperature minussaturated economizer temperature. The economizer EXV onlyoperates during normal conditions when the capacity of thecircuit is greater than 70%. Once the capacity of the circuit isgreater than 70% the MBB will start controlling the economizerEXV to maintain economizer superheat set point, which is ap-proximately 8&#176; to 12&#176; F (4.4&#176; to 6.7&#176; C). If the circuit capacity isless than 70%, the economizer EXV will be closed.

economizer EXV has one override. If the discharge gastemperature exceeds 195 F (90.6 C) the economizer EXV willstart to open. The EXV will be controlled to maintain dischargegas temperature at approximately 195 F (90.6 C).

it appears that main EXV or economizer EXV is notproperly controlling circuit operation to maintain correct super-heat, therehttp://www.51wendang.com/doc/437ec10ed908de0667a81455 are a number of checks that can be made using testfunctions and initialization features built into the microproces-sor control. See the Service Test section to test EXVs.

TROUBLESHOOTING PROCEDURE — There aretwo different economizer EXVs. Both of the economizerEXVs have a total of 2785 steps. There are three different mainEXVs, which all have a total of 4260 steps. The EXV motormoves at 150 steps per second. Commanding the valve toeither 0% or 100% will add an additional 160 steps to themove, to ensure the valve is open or closed completely.

the steps below to diagnose and correct EXVproblems. Check EXV motor operation first. Switch theEnable/Off/Remote (EOR) Contact switch to the Off position.Check the appropriate circuit EXV, Circuit A EXV % Open(Circuit A EXV Position, EXV.A) or Circuit B EXV % Open(Circuit B EXV Position, EXV.B). The current value of 0 willbe displayed. Increase the EXV position to selechttp://www.51wendang.com/doc/437ec10ed908de0667a81455t 100% valveposition. The actuator should be felt moving through the EXV.To close the valve, select 0%. The actuator should knock whenit reaches the bottom of its stroke. See Table 40 for a list ofEXV modes and submodes.

the valve is not working properly, continue with the fol-lowing test procedure:

the 8-position DIP switch on the board for the properaddress (Fig. 10). Check the EXV output signals at appropriate

on the EXV module. For 30XW150,325 units, con-nect the positive test lead to EXV-J2A terminal 5 for Circuit Aand to EXV-J2B terminal 5 for Circuit B.

30XW175,200,250,275,300,350,400 units connect pos-itive test lead to EXV(X)-J2A terminal 5 for EXV(X) andEXV(X)-J2B terminal 5 for Economizer EXV(X). Using theService Test procedure on page 86, move the valve output un-der test to 100%. DO NOT short meter leads together or pin 5to any other pin, as board damage will occur. Durihttp://www.51wendang.com/doc/437ec10ed908de0667a81455ng the nextseveral seconds, carefully connect the negative test lead to pins1,2,3 and 4 in succession. Digital voltmeters will average thissignal and display approximately 6 vdc. If the output remainsat a constant voltage other than 6 vdc or shows 0 volts, removethe connector to the valve and recheck.Select 0% to close the valve.

: When the valve is stationary, the output from the EXVboard is 12-vdc.

Tables 6 and 7. If a problem still exists, replace theEXV board. If the reading is correct, the expansion valve andEXV wiring should be checked. Check the EXV connector andinterconnecting wiring.

.Check color-coding and wire connections. Make surethey are connected to the correct terminals at the EXVboard and EXV plug and that the cables are not crossed.2.Check for continuity and tight connection at all pinterminals.

the resistance of the EXV motor windings. For30XW150,325 units remove the EXV mhttp://www.51wendang.com/doc/437ec10ed908de0667a81455odule plug EXV-J2Afor Circuit A EXV and EXV-J2B for Circuit B EXV. For30XW175,200,250,275,300,350,400 units remove the EXVmodule plug EXV(X)-J2A for main EXV and EXV(X)-J2B foreconomizer EXV. Check the resistance of the two windings be-tween pins 1 and 3 for one winding and pins 2 and 4 for the oth-er winding. The resistance should be 52 ohms (&#177; 5.2 ohms).

[此处图片未下载成功]

Also check pins 1-4 for any shorts to ground.

INSPECTING/OPENING ELECTRONIC EXPANSIONVALVES

: Obtain replacement gaskets beforeopening EXV. Do not re-use gaskets.

check the physical operation of an EXV, the followingsteps must be performed.

.Close the liquid line service valve of the circuit to bechecked. Put the Enable/Off/Remote Contact (EOR)switch in the Off position. Enter the Service Test modeand change Service Test Enable, T.REQ from OFF toON. A password may be required. Switch the EORswitchhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 to the Enable position. Under the COMP sub-mode, enable one of the compressors (CP.xn) for the cir-cuit. Let compressor run until gage on suction pressureport reads 10 psig (68.9 kPa). Turn the compressor off.The compressor will turn off. Immediately after the com-pressor shuts off, manually close the actuated ball valve(ABV). If the unit is equipped with suction service valvesand economizer service valves, close both valves. Clos-ing the valves will minimize the amount of charge thatwill have to be removed from the system after pumpdown.

.Remove any remaining refrigerant from the system lowside using proper recovering techniques. The economizerassembly has a 1/4-in. access connection which can beused to remove charge from the inlet of the EXVs. Turnoff the line voltage power supply to the compressors.

body of the EXV. Tighten the motor to the body to 36 ft-lb(50 N-m) and then tighten the valve another 30 degrees.http://www.51wendang.com/doc/437ec10ed908de0667a81455

Liquid Indicator — Clear flow of liquid refrigerantindicates sufficient charge in system. Bubbles in the sight glassindicate undercharged system or presence of noncondensables.Moisture in system, measured in parts per million (ppm),changes color of indicator. See Table 41. Change filter drier atfirst sign of moisture in system.

: Unit must be in operation at least12 hours before moisture indicator can give an accu-rate reading.

unit running, indicating element must be in con-tact with liquid refrigerant to give true reading.

41 — Color Indicators when Moisture is Present in Refrigerant

INDICATORGreen — Dry

-green — CautionYellow — Wet

a,75 F (24 C) (ppm)&lt;3030-100&gt;100

a,125 F (52 C) (ppm)&lt;4545-170&gt;170

[此处图片未下载成功]

Ensure refrigerant is removed from both the inlet and outletof EXV assemblhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ies. Equipment damage could result.3.The expansion valve motor is hermetically sealed insidethe top portion of the valve. See Fig. 49. Disconnect theEXV plug. Carefully unscrew the motor portion from thebody of the valve. The EXV operator will come out withthe motor portion of the device. Reconnect the EXV plug.4.Enter the appropriate EXV test step under the (QUIC)Service Test mode Locate the desired item Circuit AEXV Position, EXV.A or Circuit B EXV Position,EXV.B. Change the position to 100%. Observe the opera-tion of the lead screw. See Fig. 49. The motor should beturning, raising the operator closer to the motor. Motoractuator movement should be smooth and uniform fromfully closed to fully open position. Select 0% and checkopen to closed operation. If the valve is properly connect-ed to the processor and receiving correct signals, yet doesnot operate as described above, the sealed motor portionof the valve should be replaced.IMPOhttp://www.51wendang.com/doc/437ec10ed908de0667a81455RTANT: Obtain replacement gasket beforeopening EXV. Do not re-use gaskets.

re-installing the motor, be sure to use a new gasket in theassembly. See Fig. 50. It is easier to install the motor assemblywith the piston in the fully closed position. Insert the motor into

Drier — Whenever moisture-liquid indicator showspresence of moisture, replace filter drier(s). There is one filterdrier assembly on each circuit with two cores. Refer to the Car-rier Standard Service Techniques Manual, Chapter 1, Refriger-ants, for details on servicing filter driers.

Line Service Valve — This valve is located immediatelyahead of filter drier, and has a 1/4-in. access connection for fieldcharging. In combination with compressor discharge servicevalve, each circuit can be pumped down into the high side forservicing.

Assembly — The 30XW units utilize

compressors with a modulating slide valvhttp://www.51wendang.com/doc/437ec10ed908de0667a81455e which variescapacity from 15% to 100% of compressor capacity for eachcircuit. See Fig. 51 for a view of a typical 06T compressor.The slide valve position is varied by opening and closing the2 solenoid valves located on the compressor. To unload thecompressor, both solenoids are deenergized. To increase incapacity both solenoid valves are energized together whichwill cause the slide valve to slide towards the fully loaded posi-tion. To stop the loading process solenoid 2 is energized andsolenoid 1 is deenergized. This will cause the slide valve tomaintain its current position. There is no feedback for the posi-tion of the slide valve. The control utilizes compressor currentas an indicator of the slide valve position. Once the calculatedposition of the slide valve reaches 100% circuit capacity, thecontrol will try to increase capacity again if the compressorcurrent continues to increase. The control will continue to loadthe compressohttp://www.51wendang.com/doc/437ec10ed908de0667a81455r until the compressor current no longerincreases. At that time the control will energize both solenoidsand the circuit will be considered fully loaded.

OIL SYSTEM — Each compressor/circuithas its own oil system which includes an oil filter, oil solenoid,check valve, oil level switch, oil pressure transducer, and an oilshut-off valve. A typical oil system is shown in Fig. 52. SeeTable 42.

40 — EXV Modes and Submodes

TYPE AND CIRCUIT

, Circuit AEXV, Circuit B

EXV, Circuit AEconomizer EXV, Circuit B

PILOT  PATH

MenuStatusQCK_TST1Q_EXVAMain MenuStatusQCK_TST1Q_EXVBMain MenuStatusQCK_TST1Q_ECO_AMain MenuStatusQCK_TST1Q_ECO_B

PATH

Test ModeQUICEXV.AService Test ModeQUICEXV.BService Test ModeQUICECO.AService Test ModeQUICECO.B

Table 42 — Unit Oil Quantities

XW UNIT SIZE

-20025http://www.51wendang.com/doc/437ec10ed908de0667a814550-300325-400

CHANGE (gal, [liters])Circuit ACircuit B6.0 [22.7]—8.0 [30.3]—5.0 [18.9]5.0 [18.9]

Manufacturer. . . . . . . . . . . . . . . . . . . . .Emkarate RL220XL Oil Type. . . . . . . . . . . . . . . . . . . Inhibited polyolester-basedsynthetic compressor lubricant for use with screw compressors. ISO Viscosity Grade. . . . . . . . . . . . . . . . . . . . . . . . . . . . .220Do not reuse drained oil or any oil that has been exposed tothe atmosphere.

is available in the quantities shown in Table 43 fromyour local Carrier representative.

43 — Oil Part No. Information

Quart1 Gallon5 Gallon

PART NO.

-2325P903-2301P903-2305

unsure if there is low oil charge in the system, follow thesteps below:

.If the unit shuts off repeatedly from a low oil level alert itmay be an indication of inadequate oil charge; however, itcould also indicatehttp://www.51wendang.com/doc/437ec10ed908de0667a81455 that the oil is not being recovered fromthe low-side of the system.

.Begin running the unit at full load for 11/2 hours. Use themanual Test Mode feature of Service Test if the unit doesnot normally run at full load.

: An adequate load must be available.

.After running the unit for 11/2 hours at full load, allow theunit to restart and run normally. If low oil alarms persist,continue with the following steps.

.Close the liquid line service valve and place a pressuregage on top of the cooler. Enable the Service Test featureand turn the Enable/Off/Remote switch to the enable po-sition. Start the desired circuit by turning it on under theTEST function: CP.A for compressor A, CP.B for com-pressor B, or CP.C for compressor C.

.When the compressor starts successfully observe thecooler pressure when the pressure reads 10 psig(68.9 kPa), turn the Emergency Switch (SW2) to the OFFposition. The compreshttp://www.51wendang.com/doc/437ec10ed908de0667a81455sor should stop.

.Open the liquid line service valve and allow the unit torestart normally. If low oil level alarms persist, continuewith the following steps.

[此处图片未下载成功]

66

67

[此处图片未下载成功]

1access fitting port located downstream of the valve and bleed/4-in.off oil trapped between the service valve and the oil solenoidvalve. A quart of oil is typically what is removed during thisprocess. Remove the charging hose. Unscrew the nuts fromboth ends of the oil filter and remove the oil filter. Remove theprotective caps from the new oil filter and install, being carefulnot to lose or damage the new O-ring located on the new oil fil-ter. Draw a vacuum at the Schrader port. Remove the charginghose and open the oil line ball valve. Check both fittings forleaks.

SERVICE Vis a factory-installed option for 30XW units. It is located in theALVE — The suction service valvhttp://www.51wendang.com/doc/437ec10ed908de0667a81455esuction outlet of the cooler. The suction service valve is boltedbetween the cooler outlet and the suction flange piping. Thesuction service valve shaft has a locking device located on theshaft to lock the valve in either a fully open position or a fullyclosed position. The locking device must be pulled out prior tomoving the valve handle to a fully open or a fully closed posi-tion. See Fig. 53A and 53B.

[此处图片未下载成功]

LOW FLUID TEMPERATURE — Main Base Board is pro-grammed to shut chiller down if leaving fluid temperaturedrops below 34 F (1.1 C) for cooler fluid type water or belowBrine Freeze Setpoint (cooler fluid type brine. The unit will shut down without aBrine Freeze Setpoint, LOSP) forpumpout. When fluid temperature rises to 6&#176; F (3.3&#176; C) above

leaving fluid set point, safety resets and chiller restarts.Reset is automatic as long as this is the first occurrence.

OF FLUID FLOW PROThttp://www.51wendang.com/doc/437ec10ed908de0667a81455ECTION — All 30XW ma-chines include an integral flow switch that protects the cooleragainst loss of cooler flow. In addition, all models ordered forheat reclaim duty have factory installed condenser water sen-sors and an integral flow switch.TUBE retubing can be done. The number of tubes plugged determinesPLUGGING — A leaky tube can be plugged untilhow soon the cooler may be removed. Loss of unit capacity and efficiency as wellmust be retubed. All tubes in the cooleras increased pump power will result from plugging tubes.Failed tubes should be replaced as soon as possible. Up to 10%of the total number of tubes per pass can be plugged beforeretubing is necessary. Fig. 54 shows an Elliott tube plug and across-sectional view of a plug in place. See Tables 44-47 forplug components. If the tube failure occurs in both circuitsusing tube plugs will not correct the problem. Contact yourlocal Carrier representative for assistance.

://www.51wendang.com/doc/437ec10ed908de0667a81455ION

extreme care when installing plugs to prevent damageto the tube sheet section between the holes.

(All Sizes) Plug Component Parts

44 — Condenser (Sizes 150-300) and COMPONENTPART NUMBER

TubesBrass Pin853103-1*

Ring

-657 or 670* (Measure inside diameter of tube before ordering.)

Holes without TubesBrass Pin853103-1A*Brass Ring853002-738*LoctiteNo. 675 Locquic

“N”

*Order directly from Elliot Tube Company, Dayton, OH or RCD. Can be obtained locally.

45 — Condenser (Sizes 150-300) and Evaporator (All Sizes) Tube Components

.

Sheet Hole Diameter0.752 to 0.75719.10 to 19.23Tube OD

.742 to 0.74818.85 to 19.00Tube ID after Rolling

(includes expansion due to clearance.)

.666 to 0.681

.92 to 17.30

— — Inside http://www.51wendang.com/doc/437ec10ed908de0667a81455DiameterOutside Diameter

: Tbe flush with tube sheet (both ends).

replaced along heat exchanger head partitions mustTable 46 — Condenser (Sizes 325-400) Plug

Parts

NUMBERFor TubesBrass Pin853103-2A*Brass Ring

-918*For Holes without tubesBrass Pin853103-3*Brass Ring853002-988*LoctiteNo. 675 Locquic

“N”

Can be obtained locally.

[此处图片未下载成功]

*Order directly from Elliot Tube Company, Dayton, OH or RCD.68

Table 47 — Condenser (Sizes 325-400) Tube

.

Sheet Hole Diameter

[此处图片未下载成功]

1.000 to 1.00825.40 to 25.60Tube OD

.992 to 0.998

[此处图片未下载成功]

25.20 to 25.35Tube ID after Rolling

(includes expansion due to clearance.)

.918 to 0.935

.32 to 23.75

— — Inside Diahttp://www.51wendang.com/doc/437ec10ed908de0667a81455meterOutside Diameter

: Tbe flush with tube sheet (both ends).

replaced along heat exchanger head partitions mustFig. 54 — Elliott Tube Plug

— When retubing is required, obtain service ofqualified personnel experienced in boiler maintenance and

[此处图片未下载成功]

repair. Most standard procedures can be followed when retub-ing the coolers. An 8% crush is recommended when rollingreplacement tubes into the tubesheet.

prior to rolling. This material is intended to “wick” into thePlace one drop of Loctite No. 675 or equivalent on top ofarea of the tube that is not rolled into the tube sheet, and preventfluid from accumulating between the tube and the tube sheet.New tubes must also be rolled into the center tubesheet toprevent circuit to circuit leaks.

COOLER HEAD BOLTS

if there is visible signs of deterioration, cuts ordamage. Apply a thin film ohttp://www.51wendang.com/doc/437ec10ed908de0667a81455f grease to the O-ring beforeinstallation. This will aid in holding the O-ring in the groovewhile the head is installed. Torque all bolts to the followingspecification and in sequence:

/4

-in. Diameter Perimeter Bolts (Grade 5). . . . (271 to 305 N-m)

to 225 ft-lb1.Install all bolts finger tight.

.Bolt tightening sequence is outlined in Fig. 55. Followthe numbering or lettering sequence so that pressure isevenly applied to O-ring.

.Apply torque in one-third steps until required torque isreached. Load ceeding to next one-third step.

bolts to each one-third step before pro-4.No less than one hour later, retighten all bolts to requiredtorque values.

.After refrigerant is restored to system, check for refriger-ant leaks using recommended industry practices.6.Replace cooler insulation.

/CLEANING HEAT EXCHANGERS — In-spect and clean cooler tubes at the end of thehttp://www.51wendang.com/doc/437ec10ed908de0667a81455 first operatingseason. Because these tubes have internal ridges, a rotary-typetube cleaning system is necessary to fully clean the tubes. Tubecondition in the cooler will determine the scheduled frequencyfor cleaning, and will indicate whether water treatment isadequate in the chilled water/brine circuit. Inspect the enteringand leaving water thermistor wells for signs of corrosion orscale. Replace the well if corroded or remove any scale iffound.

scale may require chemical treatment for its preven-tion or removal. Consult a water treatment specialist forproper treatment procedures.

TREATMENT — Untreated water may result in corrosion, scaling, erosion or algae. Theor improperly treatedservices of a qualified water treatment specialist should beobtained to develop and monitor a treatment program.

[此处图片未下载成功]

CAUTION

must be within design flow limits, clean and treathttp://www.51wendang.com/doc/437ec10ed908de0667a81455edto ensure proper machine performance and reduce thepotential of tubing damage due to corrosion, scaling, andalgae. Carrier assumes no responsibility for cooler damageresulting from untreated or improperly treated water.CHILLED WATER FLOW SWITCH — A flow switch is installed in the entering water nozzle for all ma-factory-installedchines. See Fig. 56 and 57. This is a thermal-dispersion flowswitch. Figure 56 shows typical installation. If nuisance trips ofthe sensor are occurring, follow the steps below to correct:initiated. The warm-up period may take up to 30 seconds.When power is supplied to the device, a warm-up period isWhen enough flow is detected, the switch contacts will close.The switch closure does not indicate minimum flow require-ments have been met for the machine.

.Check to confirm that all strainers are clean, valves areopen and pumps are running. For the case of variablefrequency drive (VFD) controlled pumps, http://www.51wendang.com/doc/437ec10ed908de0667a81455ensure theminimum speed setting has not been changed.

.Measure the pressure drop across the cooler (evaporator).Use the cooler pressure drop curves in Fig. 27-43 to cal-culate the flow and compare this to system requirements.3.If the contacts do not close with sufficient flow, thencheck the wiring connection to the MBB. If the input sig-nal is not closed, then the switch needs to be replaced.

WIRING

. 56 — Chilled Water and Condenser

Flow SwitchCONDENSER WATER FLOW SWITCH AND THERMIS-TORS leaving water thermistors are factory-installed for all heat ma-— A condenser water flow switch and entering andchines and chillers with optional medium temperature brine.See Fig. 56 and 57. This is a thermal-dispersion flow switch.Figure 56 shows typical installation. If nuisance trips of thesensor are occurring, follow the steps below to correct:

. The warm-up period may take up to http://www.51wendang.com/doc/437ec10ed908de0667a8145530 seconds.When power is supplied to the device, a warm-up period isWhen enough flow is detected, the switch contacts will close.The switch closure does not indicate minimum flow require-ments have been met for the machine.

.Check to confirm that all strainers are clean, valves areopen and pumps are running. For the case of variablefrequency drive (VFD) controlled pumps, ensure theminimum speed setting has not been changed.

.Measure the pressure drop across the condenser. Use thecondenser pressure drop curves in Fig. 27-43 to calculatethe flow and compare this to system requirements.

.If the contacts do not close with sufficient flow, thencheck the wiring connection to the MBB. If the input sig-nal is not closed, then the switch needs to be replaced.

Circuit

TESTING — Units are shipped with complete operat-ing charge of refrigerant R-134a or nitrogen (see Physical Datatables supphttp://www.51wendang.com/doc/437ec10ed908de0667a81455lied in the 30XW installation instructions) andshould be under sufficient pressure to conduct a leak test. Ifthere is no pressure in the system, introduce enough nitrogen tosearch for the leak. Repair the leak using good refrigerationpractices. After leaks are repaired, system must be evacuatedand dehydrated.

CHARGE — Refer to Physical Data tablessupplied in the 30XW installation instructions. Immediatelyahead of filter drier in each circuit is a factory-installed liquid

service valve. Each valve has a 1for charging liquid refrigerant.

/4-in. access connectionnameplate. Open liquid line service valve; start unit and allowit to run several minutes fully loaded. Check for a clear sightglass. Be sure clear condition is liquid and not vapor.

rating point (54/44  F evaporator; 85/95 F condenser). Atthese conditions and with the circuit at full load, charge to aclear sightglass and a liquidhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 line temperature of 90 to 93 F (32.2to 33.9 C).

tube entering the bottom of the cooler. This fitting is locatedAdd 5 lb (2.3 kg) of liquid charge into the fitting located onbetween the electronic expansion valve (EXV) and the cooler.temperature. If needed, add additional liquid charge, 5 lbAllow the system to stabilize and then recheck the liquid(2.3 kg) at a time, allowing the system to stabilize betweeneach charge addition. Slowly add charge as the sight glassbegins to clear to avoid overcharging.

: When adjusting refrigerant charge, circu-late fluid through cooler and condenser continuously toprevent freezing and possible damage to both. Do notovercharge, and never charge liquid into the low-pressureside of system.

[此处图片未下载成功]

Safety Devices — safety devices and protection logic built into the electronicThe 30XW chillers contain many

. Following is a description of the majohttp://www.51wendang.com/doc/437ec10ed908de0667a81455r safeties.

COMPRESSOR PROTECTION

the current transducers or make any changes to thefactory-installed and configured headers. The configuration ofthese headers defines the must trip amps (MTA) at which theCPM will turn the compressors off. Determine the cause fortrouble and correct the problem before resetting the CPM. SeeAppendix D for MTA settings and configuration headers.

-pressure switch. All compressors have factory-installedEach CPM board also reads the status of each compressor’shigh-pressure switches. See Table 48.

48 — High-Pressure Switch Settings

XW UNITshut down. The CPM will reset automatically when the switchIf the switch opens during operation, the compressor will be

, however, a manual reset of the control is required torestart the compressor.COOLER PROTECTION

34 F (1.1 C) for water or more than 8set point for Fluid Type = brihttp://www.51wendang.com/doc/437ec10ed908de0667a81455ne. When the fluid temperature  F (4.4  C) belowrises 6resets and the chiller restarts. Reset is automatic as long as this  F (3.3  C) above the leaving fluid set point, the safetyis the first occurrence of the day.

: If unit is installed in an area whereambient temperatures fall below 32 F (0&#176; C), a suit-able corrosion-inhibited antifreeze solution must beused in the chilled water and condenser water circuit.

[此处图片未下载成功]

cuit between the condenser and the liquid line shutoff valve.Relief Devices — Fusible plugs are located in each cir-

RELIEF Vcircuit and are located on all coolers and condensers. TheseALVES — Valves are installed in eachvalves are designed to relieve if an abnormal pressure conditionarises. Relief valves on all coolers relieve at 220 psi (1517 kPa).These valves should not be capped. If a valve relieves, it shouldbe replaced. If the valve is not replaced, it may rhttp://www.51wendang.com/doc/437ec10ed908de0667a81455elieve at a lowerpressure, or leak due to trapped dirt from the system which mayprevent resealing. V220 psi (1517 kPa). Valves on standard condensers relieve atunits relieve at 300 psi (2068 kPa).

on high condensing and heat reclaimPressure relief valves located on shells have 3connections for relief. Some local building codes require that/4-in. NPTrelieved gases be exhausted to a specific location. This connec-tion allows conformance to this requirement. Refer to Installa-tion Instructions for details.

are only recommended guidelines. Jobsite conditionsRecommended Maintenance Schedule — The fol-

dictate that maintenance schedule is performed more oftenthan recommended.Every month:

Check moisture indicating sight glass for possible refriger-Every 3 months:

loss and presence of moisture.  Check refrigerant charge.

all refrigerant joints and valveshttp://www.51wendang.com/doc/437ec10ed908de0667a81455 for refrigerant leaks; repair as necessary.

Check chilled water and condenser flow switch operation.Check oil filter pressure drop.

12 months:

Check all electrical connections; tighten as necessary. Inspect all contactors and relays; replace as necessary.

accuracy of thermistors; replace if greater than &#177;2&#176; F (1.2&#176; C) variance from calibrated thermometer.

accuracy of transducers; replace if greater than &#177;5 psi (34.47 kPa) variance.

to be sure that the proper concentration of antifreezeis present in the chilled water and condenser loops, if applicable.

VCheck refrigerant filter driers for excessive pressure drop;erify that the chilled water loop is properly treated.

replace as necessary.

chilled water and condenser strainers, clean as necessary.

Perform Service Test to confirm operation of all components.Checkhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 for excessive cooler approach (Leaving ChilledWater Temperature – Saturated Suction Temperature) which may indicate fouling. Clean cooler vessel if necessary.Obtain oil analysis; change as necessary.

and possible remedies.

Table 49 for an abbreviated list of symptoms, possibleAlarms and Alerts — stantly monitors the unit and generates warnings when abnor-The integral control system con-

or fault conditions occur. Alarms may cause either a circuit(Alert) or the whole machine (Alarm) to shut down. Alarmsand Alerts are assigned codes as described in Fig. 58. Thealarm/alert indicator LED on the Navigator  module isilluminated when any alarm or alert condition is present. If anAlert is active, the Alarm Indicator LED will blink. If an Alarmis active, the Alarm Indicator LED will remain on. Currentlyactive Alerts and Alarms can be found in (ALRM).

Alarm,reset alarmshttp://www.51wendang.com/doc/437ec10ed908de0667a81455 will reset without any intervention if the conditionThe controller generates two types of alarms. Automaticthat caused the alarm corrects itself. Manual reset alarmsrequire the service technician to check for the alarm cause andreset the alarm. The following method must be followed toreset manual alarms:

and correct it. To reset the alarm, set Before resetting any alarm, first determine the cause of theThe alarms will be reset. Indicator light will be turned off whenR.ALM to YES.switched correctly. Do not reset the chiller at random withoutfirst investigating and correcting the cause(s) of the failure.first one or two digits indicate the alarm source and are listed inEach alarm is described by a three or four-digit code. TheFig. 58. The last two digits pinpoint the problem. See Table 50.

Table 49 — Troubleshooting

Does Not Run

CAUSE

for power to http://www.51wendang.com/doc/437ec10ed908de0667a81455unit

or incorrect unit configurationActive alarm

operating mode

Operates too Long or Continuously

refrigerant charge

in chilled water loop

EXVLoad too highActive alarm

operating mode

Does Not Load

alarm

operating mode

saturated suction temperatureLow suction superheat

Does Not Run

alarm

compressor contactor

Water Pump is ON, but Cooler freeze protectionthe Machine is OFF

REMEDY

Check overcurrent protection device.

Check non-fused disconnect (if equipped).  Restore power to unit.Check unit configuration.

Alarm status. See the Alarms and Alerts section and follow troubleshooting instructions.

for Operating Modes. See the Operating Modes section and follow trouble-shohttp://www.51wendang.com/doc/437ec10ed908de0667a81455oting instructions

for leak and add refrigerant.Purge water loop.

Check EXV, clean or replace.

Check EXV cable, replace if necessary.  Check EXV board for output signal.Unit may be undersized for application

Alarm status. See the Alarms and Alerts section and follow troubleshooting instructions.

for Operating Modes. See the Operating Modes section and follow trouble-shooting instructions.

Alarm status. See the Alarms and Alerts section and follow troubleshooting instructions.

for Operating Modes. See the Operating Modes section and follow trouble-shooting instructions.

Operating Modes 21 and 22.

(20 C). See Alarms 74 and 75 for potential causes.

circuit capacity is not allowed to increase if the circuit superheat is less than 18&#176; F (10&#176; C). See Alarms 74 and 75 for potential causes.

Alarm status. See http://www.51wendang.com/doc/437ec10ed908de0667a81455the Alarms and Alerts section and follow troubleshooting instructions.

instructions.  Check control wiring.

Check scroll protection module.

Check contactor operation, replace if necessary.

water loop temperature too low. Check cooler heater.

Does Not Run

—Electronic Expansion Valve

ALARM CODES AND POSSIBLECAUSES

1 — Cooler Fluid Entering (th.01)Alarm 2 — Cooler Fluid Leaving (th.02)

for Trip — This alarm criterion is tested whether theunit is on or off if the temperature as measured by the thermis-tor is outside of the range –40 to 245 F (–40 to 118.3 C).

to be Taken — The unit shuts down normally, or is notallowed to start.

Method — Automatic, the alarm will reset once thethermistor reading is within the expected range.

Causes — If this condition is encountehttp://www.51wendang.com/doc/437ec10ed908de0667a81455red, check thefollowing items:

sensor wiring to the Main Base Board sensor accuracy

the Thermistors section on page 58 for thermistor de-scription, identifiers and connections.Alarm 3 — Circuit A (th.03) Alarm 4 — Circuit B (th.04)

: Alarms 3 and 4 are not used or supported. If this condi-tion is encountered, confirm machine configuration.Alarm 5 — Condenser Entering Fluid (th.06)

for Trip — This alarm criterion is tested whether theunit is on or off if the temperature as measured by the thermis-tor is outside of the range –40 to 245 F (–40 to 118.3 C).

to be Taken — If the unit is in the cool mode (Heat/Cool Status = 0) no action will be taken. If the unit is a heat

(Unit Type = 4) and if the unit is in heat mode (Heat/Cool Status = 1), then the machine shall continue to run, but adefault rise_per_%_unit_capacity_on of 0.1&#176; F shall be usedby thhttp://www.51wendang.com/doc/437ec10ed908de0667a81455e capacity control function. Heating reset based on DeltaT (Heating Reset Select = 2) will be disabled.

Method — Automatic, the alarm will reset once thethermistor reading is within the expected range.

Causes — If this condition is encountered, check thefollowing items:

sensor wiring to the Main Base Board sensor accuracy

the Thermistors section on page 58 for thermistor descrip-tion, identifiers and connections.

6 — Condenser Leaving Fluid (th.07)

for Trip — This alarm criterion is tested whether theunit is on or off if the temperature as measured by the thermis-tor is outside of the range –40 to 245 F (–40 to 118.3 C).

to be Taken — If the unit is in the cool mode (Heat/Cool Status = 0) no action will be taken. If the unit is a heatmachine (Unit Type = 4) and if the unit is in heat mode (Heat/Cool Status = 1), the unit shuts down normally, orhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 is notallowed to start.

Method — Automatic, the alarm will reset once thethermistor reading is within the expected range.

Causes — If this condition is encountered, check thefollowing items:

sensor wiring to the Main Base Board sensor accuracy

the Thermistors section on page 58 for thermistor descrip-tion, identifiers and connections.

Alarm 7— Reclaim Entering Fluid (th.08)Alarm 8 — Reclaim Leaving Fluid (th.09)

: Alarms 7 and 8 are not used or supported. If this condi-tion is encountered, confirm machine configuration.

for Trip — This alarm criterion is tested whether theunit is ON or OFF. The alarm will be tripped if the unit isconfigured as a master or a slave (Master/Slave Select,MSSL), leaving temperature control is selected (EnteringFluid Control, EWTO), and if the temperature measured bythe CHWS (chilled water sensor) fluid sensor is outside thttp://www.51wendang.com/doc/437ec10ed908de0667a81455herange of –40 to 245 F (–40 to 118.3 C).

to be Taken — Master/slave operation is disabled andthe chiller returns to stand alone mode.

Method — Reset is automatic when the thermistor read-ing is inside the range of –40 to 245 F (–40 to 118.3 C).

Causes — If this condition is encountered, check thefollowing items:

sensor wiring to the Main Base Board a faulty thermistor

the Thermistors section on page 58 for thermistor de-scription, identifiers and connections.Alarm 11 — Circuit A (th.12) Alarm 12 — Circuit B (th.13)

for Trip — This alarm criterion is tested whether theunit is ON or OFF. If the suction gas temperature as measuredby the thermistor is outside of the range –40 to 245 F (–40 to118.3 C).

to be Taken — The affected circuit shuts downnormally.

Method — Automatic, once the thermistor reading iswithin the expected range. Thhttp://www.51wendang.com/doc/437ec10ed908de0667a81455e affected circuit will restart oncethe alarm has cleared.

Causes — If this condition is encountered, check thefollowing items:

sensor wiring to the EXV board board for a faulty channel a faulty thermistor

the Thermistors section on page 58 for thermistor descrip-tion, identifiers and connections.

50 — Alarm Codes

DESCRIPTIONNUMBER

Cooler Entering Fluid

Cooler Leaving Fluid

Circuit A Defrost Thermistor4Circuit B Defrost Thermistor

Entering

ThermistorCondenser LeavingFluid ThermistorReclaim CondenserEntering ThermistorReclaim CondenserLeaving Thermistor

/Slave Common Fluid Thermistor

FOR ALARM

TAKENBY CONTROL

measured Unit be shut down or by the controllhttp://www.51wendang.com/doc/437ec10ed908de0667a81455er isnot allowed to startoutside of the rangeof –40 F to 245 F

be shut down or not allowed to start

CAUSEFaulty Sensor,wiring error or failed main base boardConfiguration errorFaulty Sensor,wiring error or failed main base board

error

A Suction GasThermistor

B Suction GasThermistor

A Discharge GasThermistor

B Discharge GasThermistor

A Condenser Sub-cooling Liquid ThermistorCircuit B Condenser Sub-cooling Liquid ThermistorSpace TemperatureThermistor

heater feedbackthermistor

A Economizer GasThermistor

B Economizer GasThermistor

——————

chiller deacti-vated. Master andhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 slave machines operate in stand- alone modeCircuit shut down or not allowed to start

Sensor,wiring error or failed main base board

Sensor,wiring error, failedEXV or CPM board

supported

error

tripped

economizer function disabled

Sensor, wiring error, failed EMM

errorFaulty Sensor,wiring error, failed

board

——————Carrier Comfort Network&#174;

Protection ModuleEnergy Management ModuleEntering Water TemperatureElectronic Expansion ValveHigh Pressure SwitchLeaving Water TemperatureMinimum Load Valve

Operating PressureMust Trip Amps

Suction TemperatureUnderwriters Laboratories

Table 50 — Alarm Codes (cont)

://www.51wendang.com/doc/437ec10ed908de0667a81455PREFIXCODEPr

B1E1E203

DESCRIPTIONREASON FOR ALARMNUMBER

Circuit A DischargeMeasured voltage is

vdc or SST &gt; EWT and

&lt; 50% for 1 minute27Circuit B Discharge

Circuit A Suction Transducer30Circuit B Suction Transducer32Circuit A Reclaim Pumpdown

Transducer

Circuit B Reclaim Pumpdown

Transducer

Circuit A Oil Pressure

Circuit B Oil Pressure

Circuit A EconomizerMeasured voltage is

Transducer 0 vdc

Circuit B Economizer

Transducer

Loss of communication with No communication

Board Awith CPM board

Loss of communication with

Board B

of communication with EXV Board 1

://www.51wendang.com/doc/437ec10ed908de0667a81455arLoss of communication with EXV Board 2

of communication with Energy Management Board

communication with

board

TAKENBY CONTROLCircuit shut down or not allowed to start

CAUSEFaulty transducer,wiring error, failed main

board orfan board

error

shut down or not allowed to start

transducer,wiring error, failed CPM

compressor shut

downDisable or not allow EMM functions 3 step and 4-20 mA and space tempera-ture reset, occu-pancy override and

build)Unit shut down or not allowed to start

communication with

board

CPM address, wrong unit configura-tion, wiring error, power

, failedCPhttp://www.51wendang.com/doc/437ec10ed908de0667a81455M boardWrong EXV board address, wrong unit configuration, wiring error, power loss,failed EXV boardWrong board address, wrong unit configuration, wiring error, power loss to module, failed module

of communication with AUX Board 6

communication with MLV/COND Board

Freeze ProtectionEntering or leaving therm-Condenser Freeze Protectionistor sensed a tempera-ture at or below freeze Circuit A

Freeze ProtectionCircuit B

A Low SuctionTemperature

B Low SuctionTemperature

A High SuctionSuperheat

B High SuctionSuperheat

saturated suction temperatures detected for

period of time

&gt;98%,

superheat &gt; 30 F, and SST&lt;MOP for more

5 minutes

board address, wrhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ong unit configuration, wiring error, power loss to module, failed module

shut down or Automatic, first Faulty thermistor, faulty not allowed to startoccurrence in wiring, low water flow,

hours;low loop volume, fouled manual ifcooler, or freezemultiple alarms conditionswithin 24 hours

shut downAutomatic, first Faulty thermistor, faulty

in wiring, low water flow, 24 hours;low loop volume, fouled manual ifcooler, or freezemultiple alarms conditionswithin 24 hours

shut downManualFaulty transducer,

wiring, faulty thermistor, faulty EXV, low refrigerant charge, plugged or restricted

line

——————

Comfort Network&#174;

Protection ModuleEnergy Management ModuleEntering Water TemperatureElectronic Expansion ValveHigh Pressure Switch

——————Leaving Wathttp://www.51wendang.com/doc/437ec10ed908de0667a81455er TemperatureMinimum Load Valve

Operating PressureMust Trip Amps

Suction TemperatureUnderwriters Laboratories

Table 50 — Alarm Codes (cont)

DESCRIPTIONNUMBER

Circuit A Low Suction

Circuit B Low Suction

FOR ALARMEXV&lt;5% and either the suction superheat is less than the set point by at least 5 F or the suction temperature is greater than MOP set point for more than 5 minutesLockout Switch ClosedExternal pump interlock

TAKENBY CONTROLCircuit shut down

CAUSEFaulty transducer, faulty wiring, faulty thermistor, faulty EXV,

incorrectconfigurationLockout Switch Closed

EMM boardExternal pump off. Faulty jumper wiring when channel not usedFaulty communication wiring, no powershttp://www.51wendang.com/doc/437ec10ed908de0667a81455upply to the external

communication wiring, no power or control power to the main base board of either module

oil filter, faulty oil transducer, oil check valve stuck, plugged oil

oil filter, closed oil valve, bad oil solenoid, oil check valve stuck, faulty oil pressure transducerPlugged oil filter

Failure

Box Thermostat Failure/Reverse RotationLoss of communication with System Manager

shut down or not allowed to startUnit shut down or not allowed to startUnit change to stand-alone operationUnit change to stand-aloneoperationCircuit shut down

of communication with an external control device for more than

minutes

/Slave communication Communication between Failurethe master and slave

lostCihttp://www.51wendang.com/doc/437ec10ed908de0667a81455rcuit A Low Oil Pressure Circuit B Low Oil Pressure

pressure and suction pressure differential is less than the set point

nn

A Max Oil Filter Differ-ential Pressure

B Max Oil Filter Differ-ential Pressure

A High Oil Filter Drop Pressure

B High Oil Filter Drop Pressure

A Low Oil LevelCircuit B Low Oil LevelMaster chiller configuration error Number 01 to nnNo factory configurationIllegal factory configuration Number 01 to 03

is in CCN emergency stop

pump #1 faultCooler pump #2 faultCondenser Flow SwitchFailure

A Reclaim Operation Failure

B Reclaim Operation Failure

A — High condensing temperature out of compres-sor envelope

B — High condenshttp://www.51wendang.com/doc/437ec10ed908de0667a81455ing temperature out of compres-sor envelope

——————

between dis-Circuit shut down

pressure and oil pressure is greater than 50 psi for more than

seconds

between dis-Alert generated

pressure and oil pressure is greater than 30 psi for more than

minutes

level switch openCircuit shut down or

allowed to startUnit not allowed to start in Master-slave

ConfigurationUnit not allowed to

or incompatible Unit not allowed to configuration datastartEmergency stop com-Unit shut down or

has been receivednot allowed to startPump interlock status does not match pump

switch open

shuts down, if available, another pump will startUnit shut down

or incompatible configuration data

://www.51wendang.com/doc/437ec10ed908de0667a81455ual

oil level, faulty switch, wiring error, failed CPM board, oil solenoid stuck openConfiguration errorConfiguration errorConfiguration errorCarrier ComfortNetwork&#174; Emergency Stop command received

contacts, wiring error or low control voltage. Configuration

.

flow switch, low condenser flow, faulty wiring, faulty MBB, condenser pump offConfiguration error

—NoneManual

capacity over-rides due to highsaturated discharge

shut downAutomatic

or restrictedcondenser water flow.Fouled condenser

.

——————

Comfort Network&#174;

Protection ModuleEnergy Management ModuleEntering Water TemperatureElectronichttp://www.51wendang.com/doc/437ec10ed908de0667a81455 Expansion ValveHigh Pressure Switch

Water TemperatureMinimum Load Valve

Operating PressureMust Trip Amps

Suction TemperatureUnderwriters Laboratories

Table 50 — Alarm Codes (cont)

DESCRIPTIONNUMBER

Circuit A — Repeated low

temp overrides

Circuit B — Repeated low

temp overrides111112113114115117118120121

entering water tempera-ture in heating

pump #1 defaultCondenser pump #2 defaultCircuit A High Discharge Temperature

B High Discharge Temperature

A Low Economizer Pressure

B Low Economizer Pressure

A Slide Valve Control Unverifiable

B Slide Valve Control Unverifiable

flow switch set point configuration failure

://www.51wendang.com/doc/437ec10ed908de0667a81455r flow switch failure

FOR ALARMMultiple capacity

due to low satu-rated suction temperature

supportedNot supported

TAKENBY CONTROLCircuit shut down

CAUSEInaccurate

, faulty EXV, low refrigerant charge, plugged or restricted liquid line filter drier.

—Faulty contacts, wiring error or low control voltage. Configuration

.

transducer/high pressure switch, low/restricted condenser

transducer, faulty main base board, faulty wiring, closed suction service valve,

EXV

valve stuck, inac-curate initial current

—None

—Manual

gas tempera-ture is higher than 212 F for more than 90 secondsThe economizer pressure is below the suction pres-sure more than 14.5 psi for more than 10 secondsIf 100% load current is less thttp://www.51wendang.com/doc/437ec10ed908de0667a81455han 1.1 times of30% load current, or for1 minute when active cooling setpoint isgreater than 32 F.

—Flow switch open

shut downManual

shut downManual

errorUnit shut down

if unit Faulty flow switch, low

running, cooler flow, faultyautomaticwiring, faulty cooler otherwisepump, faulty main base

error, EWT and

sensors swapped

requiredEconomizer EXV fail-ure  (175, 200, 250,

, 300, 350, 400 only), faulty CPM board, low refrigerant

thermistor, faulty

, faulty CPM

, press Loss of condenser air reset button on flow, operation beyond

envelope,

high pressure switch, faulty wiring, faulty CPM board

beyond

://www.51wendang.com/doc/437ec10ed908de0667a81455pressor envelope, incorrect configuration

motor fail-ure, unloader slide

failure, compres-sor mechanical failure

fuse, wiring

, loose terminals

, B1

-01,133-01

Exchanger Tempera-ture Sensors SwappedService maintenance alert Number # nn

Motor tempera-ture too high

detects EWT below LWT for 1 minuteField programmed elapsed time has expired for maintenance timeCompressor temperature higher than 232 F for more than 90 seconds

shut down

shut down

-02,133-02132-03,133-03

Motor tempera-ture out of range

High pressure switch protectionCompressor temperature reading out of the range of

–40 F to 245 F

input on CPM board

shut downCircuit shttp://www.51wendang.com/doc/437ec10ed908de0667a81455hut down

-04,133-04132-05,133-05132-06,133-06132-07,133-07132-08,133-08132-09,133-09

Over currentCompressor Locked rotor

board detects high motor current compared

MTA setting

board detects locked rotor current compared with MTA settingCPM board detects cur-rent unbalance greater than 65% for more than

second

shut downCircuit shut down

Phase loss L1Compressor Phase loss L2Compressor Phase loss L3Compressor Low current alarm

shut down

detects motor cur-rent less than a certain percentage of the MTA setting, compressor not

shut downManual

supply discon-nected, blown fuse, wiring error, contact deenergized, faulty current toroid high pressure switch trip.

——————

Comfort Networkhttp://www.51wendang.com/doc/437ec10ed908de0667a81455&#174;Compressor Protection ModuleEnergy Management ModuleEntering Water TemperatureElectronic Expansion ValveHigh Pressure Switch

——————

Water TemperatureMinimum Load Valve

Operating PressureMust Trip Amps

Suction TemperatureUnderwriters Laboratories

Table 50 — Alarm Codes (cont)

, B1

DESCRIPTIONNUMBER

-10,Compressor Y delta starter 133-10current increase failure alarm

FOR ALARMIf the delta mode current is not 25% greater than the current in Y modeCPM board detects greater than 15% of MTA current for 10 seconds after shutting off the com-pressor contactor. Oil solenoid is energized.CPM board detects greater than 15% of MTA current for 10 seconds after three attemptsCPM board detects phase reversal from current

setting is out of the http://www.51wendang.com/doc/437ec10ed908de0667a81455allowed MTA rangeCPM board MTA setting do not match factory

board dipswitch S1

changedCPM board detects a

failureSoftware error

error

TAKENBY CONTROLCircuit shut down

CAUSEPower supply to delta

not

, faulty delta contactor or wiring, faulty CPM boardFaulty contactor, con-tactor welded, wiring

-11,133-11

Contactor failureCircuit shut downManual

-12,133-12132-13,133-13

Unable to stop motor

Phase reversal

shut downManual

contactor,contactor welded,wiring errorTerminal block power supply lead not incorrect phase. Power supply leads going through toroid crossedIncorrect MTA setting, faulty CPM boardIncorrect CPM dip-switch setting,incorrect factory MTA shttp://www.51wendang.com/doc/437ec10ed908de0667a81455etting, faulty CPM

CPM dip-switch setting, faulty

boardPower supplyinterruption

noise, faulty

board

noise, faulty

board

Circuit shut downManual

-14,133-14132-15,133-15Compressor MTA configura-tion fault

Configuration switch mismatch

shut downCircuit shut down

-16,133-16132-17,133-17132-18,133-18132-19,133-19

Unexpected switch setting changeCompressor Power on resetCompressor UL 1998 critical section software error

UL 1998 current measure dual channelmismatch

——————

shut downCircuit shut downCircuit shut downCircuit shut down

——————

Comfort Network&#174;

://www.51wendang.com/doc/437ec10ed908de0667a81455ssor Protection ModuleEnergy Management ModuleEntering Water TemperatureElectronic Expansion ValveHigh Pressure Switch

Water TemperatureMinimum Load Valve

Operating PressureMust Trip Amps

Suction TemperatureUnderwriters Laboratories

14 — Circuit A (th.15)Alarm 15 — Circuit B (th.16)

for Trip — This alarm criterion is tested whether theunit is ON or OFF. The alarm is tripped if the temperaturemeasured by the Outdoor Air Thermistor sensor is outside therange of –40 to 245 F (–40 to 118.3 C).

to be Taken — The unit shuts down normally, or is notallowed to start.

Method — Automatic, the alarm will reset once thethermistor reading is within the expected range.

Causes — If this condition is encountered, check thefollowing items:

sensor wiring to the CPM board a faulty thermistor

a faulty channel on the boarhttp://www.51wendang.com/doc/437ec10ed908de0667a81455d

the Thermistors section on page 58 for thermistor descrip-tion, identifiers and connections.

17 — Circuit A (th.18) Alarm 18 — Circuit B (th.19)

: Alarms 17 and 18 are not used or supported. If thiscondition is encountered, confirm machine configuration.

for Trip — This alarm criterion is checked whether theunit is ON or OFF and if Space Temperature Reset has beenenabled. This alarm is generated if the outdoor-air temperatureas measured by the thermistor is outside of the range –40 to245 F (–40 to 118.3 C).

to be Taken — Unit operates under normal control.Temperature Reset based on Space Temperature is disabled.Reset Method — Automatic, once the thermistor reading iswithin the expected range. The Space Temperature Reset willresume once the alarm has cleared.

Causes — If this condition is encountered, check thefollowing items:

sensor wiring to thttp://www.51wendang.com/doc/437ec10ed908de0667a81455he Energy Management Module board for a faulty channel a faulty thermistor

thermistor descriptions, identifiers and connections, seethe Thermistors section.

: Alarm 20 is not used or supported. If this condition isencountered, confirm machine configuration.Alarm 21 — Circuit A (th.24)Alarm 22 — Circuit B (th.25)

for Trip — This alarm criterion is tested whether theunit is ON or OFF. The alarm is tripped if the Economizer gasreading is outside the range of –40 to 245 F (–40 to 118.3 C).77

Action to be Takenallowed to start.

— The unit shuts down normally, or is notReset Methodthermistor reading is within the expected range.

— Automatic, the alarm will reset once thePossible Causesfollowing items:

— If this condition is encountered, check the  sensor wiring to the EXV board a faulty thermistor

faulty channel on the board

the Thermistors section on phttp://www.51wendang.com/doc/437ec10ed908de0667a81455age 58 for thermistor descrip-tion, identifiers and connections.Alarm 26 — Circuit A (Pr.01)Alarm 27 — Circuit B (Pr.02)

for TripON or OFF. This alarm is generated if the voltage as sensed by — The criterion is tested whether the circuit isthe MBB is 0 vdc, which corresponds to the Navigator  dis-play of –7 psi (–48.3 kPa).

to be Takenallowed to start.

— The circuit is shut down normally, or notReset Methodgreater than 0 vdc, which corresponds to the Navigator display — Automatic, once the transducer voltage isof a value greater than –7 psi (–48.3 kPa).

Causesfollowing items:

— If this condition is encountered, check the  sensor wiring to Main Base Board board for a faulty channel for a faulty transducerconfirm unit configuration

29 — Circuit A (Pr.04) Alarm 30 — Circuit B (Pr.05)

for TripON or OFF. The alarm is generated if one of the following http://www.51wendang.com/doc/437ec10ed908de0667a81455— The criteria are tested whether the circuit iscriteria is met:

.If the voltage as sensed by the MBB is 0 vdc, whichcorresponds to the Navigator  display of  –7 psi(–48.3 kPa).

.The circuit is ON in cooling mode and the SaturatedSuction Temperature (for the circuit is greater than the Entering Water Tempera-Saturated Suction Temp, SST)ture and EXV opening is less than 50% for more than60 seconds.

to be Takennot allowed to start. — The circuit is shut down immediately, orReset Method

.Automatic, once the transducer voltage is greater than0 vdc, which corresponds to the Navigator display of avalue greater than –7 psi (–48.3 kPa).

.Automatic once the circuit’s saturated suction tempera-ture is lower than the Entering Water Temperature by 3&#176; F(1.6&#176; C). If this criterion trips the alarm 3 times within a24-hour period, the alarm changes to a manual reset.Possible Causesfollowing itemhttp://www.51wendang.com/doc/437ec10ed908de0667a81455s:

— If this condition is encountered, check the  sensor wiring to Main Base Board board for a faulty channel faulty transducer

entering water temperature sensorAlarm 34 — Circuit A (Pr.10)Alarm 35 — Circuit B (Pr.11)

for TripON or OFF. The alarm is generated if the voltage as sensed by

— The criteria are tested whether the circuit isthe CPM board is 0 vdc,  which corresponds to the Navigatordisplay of –7 psi (–48.3 kPa).

to be Takennot allowed to start.

— The circuit is shut down immediately, orReset Method greater than 0 vdc.

— Automatic, once the transducer voltage isPossible Causesfollowing items:

— If this condition is encountered, check the  sensor wiring to CPM board board for a faulty channel faulty transducer plugged oil filter

faulty oil solenoid valve coil stuck oil solenoid valveconfirm unit configuration

37 — Circuit A (Prhttp://www.51wendang.com/doc/437ec10ed908de0667a81455. 13) Alarm 38 — Circuit B (Pr. 14)

for TripON or OFF. The alarm is generated if the voltage as sensed by — The criteria are tested whether the circuit isthe MBB or Fan Board C is 0 vdc, which corresponds to theNavigator display of –7 psi (–48.3 kPa).

to be Takennot allowed to start.

— The circuit is shut down immediately, orReset Method greater than 0 vdc, which corresponds to the Navigator display— Automatic, once the transducer voltage isof a value greater than –7 psi (–48.3 kPa).

Causesfollowing items:

— If this condition is encountered, check the  sensor wiring to EXV Board EXV board for a faulty channel faulty transducer

faulty economizer EXV or EXV wiring

faulty economizer EXV channel on the board closed or partially closed suction service valveconfirm unit configuration

53 — Compressor Board A (Co.A1)Alarm 54 — Compressor Board B (Co.B1)://www.51wendang.com/doc/437ec10ed908de0667a81455parfor Tripunit is ON or OFF. If communication with the Compressor — The alarm criterion is tested whether theProtection Module Board (CPM) is lost for a period of 10 sec-onds, the alarm will be generated.

to be Takendown.

— The affected compressor will be shutReset MethodIf called for, the compressor will start normally.

— Automatic, if communication is established.Possible Causesfollowing items:

— If this condition is encountered, check the  power supply to the affected CPM board address of the CPM

local equipment network (LEN) wiringconfirm unit configuration

56 — Circuit A, EXV Board 1 (Co.E1)Alarm 57 — Circuit B, EXV Board 2 (Co.E2)

for Tripunit is ON or OFF. If communication with EXV1 or 2 is lost — The alarm criterion is tested whether thefor a period of 10 seconds, the alarm will be triggered.

to be Takendown normally. If Circuihttp://www.51wendang.com/doc/437ec10ed908de0667a81455t A or B is not operating, it will not be — If running, Circuit A or B will shutallowed to start.

Methodthe unit will start normally.

— Automatic, if communication is established,78

Causesfollowing items:

— If this condition is encountered, check the  power supply to EXV1 or 2 address of the EXV board

local equipment network (LEN) wiringconfirm unit configuration

for TripON or OFF and when a function that requires the Energy — The criterion is tested whether the unit isManagement Module (EMM) is configured. If communicationwith the EMM is lost for a period of 10 seconds, the alarm willbe triggered.

to be Taken(3-Step and 4-20 mA Demand Limit, 4-20 mA and Space — If any function controlled by the EMMTemperature Reset, Occupancy Override, and Ice Build) isactive, that function will be terminated. If an EMM function isprogrammed, and communicatiohttp://www.51wendang.com/doc/437ec10ed908de0667a81455n is lost, the function will notbe allowed to start.

Methodthe functions will be enabled.

— Automatic, if communication is established,Possible Causesfollowing items:

— If this condition is encountered, check the The EMM is installed, (EMM NRCP2 BoardEMM NRCP2 Board, EMM). Iftrol option that requires the EMM that may be enabled (cor-, EMM=YES, then check for a con- rect configuration if not correct). power supply to EMM address of the EMM

local equipment network (LEN) wiring

unit configuration to be sure that no options thatrequire the EMM are enabled

for Tripunit is ON or OFF. If units are configured for minimum load — The alarm criteria are checked whether thecontrol or head pressure control (HGBPHot Gas Bypass Select,communication with the AUX board is lost then the alarm will=Yes or Condenser Valve Select, CON.V=Yes). Ifbe generated.

to be Taken — Unihttp://www.51wendang.com/doc/437ec10ed908de0667a81455t shut down or not allowed to start.Reset Methodthe unit will start normally.

— Automatic, if communication is established,Possible Causesfollowing items:

— If this condition is encountered, check the  power supply to the MLV/COND board address of the MLV/COND board local equipment network (LEN) wiringconfirm network configuration

for Tripunit is ON or OFF. If the entering or leaving water thermistor — The alarm criteria are checked whether thesenses a temperature at the freeze point or less, the alarm willbe generated. For a fresh water system (FLUDCooler Fluid Typeperature brine systems (=1), the freeze point is 34 F (1.1 C). For medium tem-,freeze point is Brine Freeze Set Point (Cooler Fluid Type, FLUD=2), theLOSP).

Freeze Setpoint,Action to be TakenChilled water pump will be started.

— Unit shut down or not allowed to start.Reset MethodLWT rises to 6&#176; F (3&#176; C) above sethttp://www.51wendang.com/doc/437ec10ed908de0667a81455 point. Manual, if more than — Automatic, first occurrence in 24 hours ifone occurrence in 24 hours.

Causesfollowing items:

— If this condition is encountered, check the  entering and leaving fluid thermistors for accuracywaterflowrate

loop volume — low loop volume at nominal flow rates can in extreme cases bypass cold water to the cooler freezing conditions

freeze protection items for proper operation

glycol concentration and adjust If the Leaving Water Set Point is above 40 F (4.4 C) andLOSP accordingly

is glycol in the loop, consider using the MediumTemperature Brine option (to utilize the brine freeze point instead of 34 F (1.1 C)Cooler Fluid Type, FLUD=2)Alarm 68 — Circuit A (PAlarm 69 — Circuit B (P.02) .03)

for Tripunit is ON or OFF and both cooler and condenser fluid types — The alarm criteria are checked whether theare set for water. If the saturatedhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 condensing temperature is lessthan 34 F (1.1 C), the alarm will be generated.

to be Takenwill be shut down and the condenser pump output shall be — If the chiller is ON, the affected circuitturned on.  If the chiller is OFF, the unit is not allowed to start.Reset Methodperature rises above 40 F (4.4 C)

— Automatic when saturated condensing tem-Possible Causesfollowing items:

— If this condition is encountered, check the entering and leaving fluid thermistors for accuracy (if installed)

water flow rate freezing conditionslow refrigerant charge

71 — Circuit A (PAlarm 72 — Circuit B (P.05) .06)

for Tripcircuit is ON. This alarm is generated if one of the following — The criteria are tested only when thecriteria is met:

If the circuit Saturated Suction Temperature is below –13 F(–25 C) for more than 30 seconds or 40 seconds if OA less than 14 F (–10 C) or LWT is lehttp://www.51wendang.com/doc/437ec10ed908de0667a81455ss than 36 F (2.2 C).T isIf the circuit Saturated Suction Temperature is below –22 F(–30 C) for more than 10 seconds, or 20 seconds if OAthan 50 F (10 C).

lessAction to be Taken — The circuit is shut down immediately.the alarm. See Operating Modes 21 and 22 on page 54.

to the alarm trip, the control will take action to avoidReset MethodManual, if more than one occurrence in 24 hours.

— Automatic, first occurrence in 24 hours.Possible Causesfollowing items:

— If this condition is encountered, check the  sensor wiring to Main Base Board board for a faulty channel faulty suction transducer cooler water flow loop volume EXV operation

line refrigerant restriction, filter drier, service valve, etc

refrigerant charge

the Leaving Water Set Point is above 40 F (4.4 C) andthere is glycol in the loop, consider using the MediumTemperature Brine option (to utilize the brine freezhttp://www.51wendang.com/doc/437ec10ed908de0667a81455e point instead of 34 F (1.1 C).Cooler Fluid Type, FLUD=2)Alarm 74 — Circuit A (PAlarm 75 — Circuit B (P.08).09)

for Tripcuit is ON. This alarm is generated if  — The criteria are tested only when the cir-ria are met:

of the following crite- The EXV position is equal to or greater than 98%.

The circuit’s Suction Superheat (Suction Gas Temperature –Saturated Suction Temperature) is greater than the super- heat control set point.

circuit’s Saturated Suction Temperature is less thanMaximum Operating Pressure (MOP) set point (MOP Setpoint, MOP) for more than 5 minutes.EXVAction to be Taken — The circuit is shut down normally.Reset Method — Manual.

Causesfollowing items:

— If this condition is encountered, check the  suction pressure transducer wiring to Main Base Board board for a faulty channel a faulty suction transducer

gas thermistor wirinhttp://www.51wendang.com/doc/437ec10ed908de0667a81455g to EXV Board 1 or to EXV Board 2

suction gas thermistor sensor for accuracy

for EXV Board 1 or EXV Board 2 faulty channel EXV operation

liquid line refrigerant restriction, filter drier, service valve, etc.

chargeAlarm 77 — Circuit A (PAlarm 78 — Circuit B (P.11).12)

for TripON. This alarm is generated if the following criterion is met: — The criteria are tested when the circuit iscuit’s Suction Superheat (Suction Gas Temperature – SaturatedThe EXV position is equal to or less than 5% and the cir-Suction Temperature) is less than the Suction Superheat SetPoint (SetpointEXVleast 5&#176; F (2.8&#176; C) or the circuit Saturated Suction Temperature, SHPA Superheat Setpoint.B, or EXVC Superheat Setpoint, SHP.A, EXVB Superheat, SHP.C) by atis greater than Maximum Operating Pressure (MOP) set point(EXV MOP Setpoint, MOP) for more than 5 minutes.Action to be Taken — The circuit ihttp://www.51wendang.com/doc/437ec10ed908de0667a81455s shut down normally.

MethodManual, if more than one occurrence in 24 hours.

— Automatic, first occurrence in 24 hours.Possible Causesfollowing items:

— If this condition is encountered, check the  suction pressure transducer wiring to Main Base Board board for a faulty channel faulty suction transducer

gas thermistor wiring to EXV Board 1 or to EXV Board 2

suction gas thermistor sensor for accuracy EXV Board 1 or EXV Board 2 faulty channel EXV operation

confirm maximum operating pressure set pointrefrigerant charge level

for TripON or OFF. This alarm is generated if the lockout switch — The criteria are tested whether the unit is(located in the Energy Management Module) is closed duringnormal operation.

to be Takenately without going through the normal sequence and are not — All compressors are shut down immedi-allowed to start.

Methhttp://www.51wendang.com/doc/437ec10ed908de0667a81455odManual, if more than one occurrence in 24 hours.

— Automatic, first occurrence in 24 hours.Possible Causesfollowing items:

— If this condition is encountered, check the  chilled water flow switch operation

flow. Be sure all water isolation valves are open and check water strainer for a restriction interlock wiring circuit power supply to the pump

signal to the pump controller

chilled water pump operation

pump contactor for proper operation

for Tripunit is ON or OFF. If channel 15A on the MBB, which is used — The alarm criteria are checked whether thefor field wired external pump interlock, is open then the alarmwill be generated.

to be Taken — Unit shut down or note allowed to start.Reset Methodwill start normally.

— Automatic, if the channel is closed, the unitPossible Causesfollowing items:

— If this condition is encounterhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ed, check the jumper wiring on TB5-1 and TB5-2 when channel is not in use

external pump interlock open

wiring for the external pump interlock open

for TripON or OFF. This alarm is generated if the System Manager — The criterion is tested whether the unit ishad established communications with the machine and is thenlost for more than 2 minutes.

to be Takendepends on the configuration. If Auto Start when SM lost is — The action to be taken by the controlenabled, (unit will force the CCN Chiller Start Stop to Cooler Heater Delta Spt, AU.SM=YESall forced points from the System Manager. The unit will revertENBL), then the and clearto stand-alone operation.

Methodre-established.

— Automatic, once communication isPossible Causesfollowing items:

— If this condition is encountered, check the  communication wiring

supply to the System Manager and unit cohttp://www.51wendang.com/doc/437ec10ed908de0667a81455ntrolsCriteria for TripON or OFF and a master and slave machine has been config- — The criterion is tested whether the units areured, (SelectMaster/Slave Select, MSSL=1 and Master/Slaveminutes, this alarm is generated.

, MSSL=2). If communication is lost for more than 3Action to be Takeneach unit will operate in Stand-Alone mode.

— Dual chiller control will be disabled andReset Methodre-established.

— Automatic, once communication isPossible Causesfollowing items: — If this condition is encountered, check the  CCN wiring

control power to each Main Base Board, master and slaveconfirm correct configurationAlarm 84 — Circuit A (PAlarm 85 — Circuit B (P.67).68)

for Trippressor is ON. The alarm is generated if oil pressure is less — The criteria are tested only when the com-than either oil_sp1 or oil_sp2 as defined below, where:

= oil pressure transducer reading for thehttp://www.51wendang.com/doc/437ec10ed908de0667a81455 appropriate com-sp = suction pressure reading for the affected circuitdp = discharge pressure reading for the affected circuitoil_sp1 = 0.7 x (dp-sp)   sp

_sp2 = sp   7.2 psi (15 seconds after start)oil_sp2 = sp   14.5 psi (45 seconds after start)

Action to be Takenstopped. The other compressors will continue to operate. — The affected compressor will beReset Method — Manual.

Causesfollowing items:

— If this condition is encountered, check the  sensor wiring to the CPM Board board for a faulty channel faulty transducer plugged oil filter

faulty oil solenoid valve coil stuck oil solenoid valve stuck check valve

manual shut off valve to ensure it is not fully openconfirm unit configuration

87 — Circuit A (PAlarm 88 — Circuit B (P.70).71)

for Tripsor has been operating for at least 5 seconds. The alarm is — The criterion is tested when the http://www.51wendang.com/doc/437ec10ed908de0667a81455compres-generated if the difference between the Circuit Discharge Pres-sure and the Compressor Oil Pressure is greater than 50 psi(345 kPa) for more than 30 seconds.

to be Takenoff.

— The affected compressor will be turnedReset Method — Manual

Causesfollowing items:

— If this condition is encountered, check the check the discharge and oil sensor wiring to the Main Base Board and CPM board boards for a faulty channel faulty transducer plugged oil filter

faulty oil solenoid valve coil stuck oil solenoid valve stuck check valve

shut off valve to ensure it is not fully open

the power supply to the System Manager and unitcontrols.

90 — Circuit A (PAlarm 91 — Circuit B (P.84).85)

for Tripsor has been operating for at least 5 seconds. The alarm is gen- — The criterion is tested when the compres-erated if the difference between the Cirhttp://www.51wendang.com/doc/437ec10ed908de0667a81455cuit Discharge Pressureand the Compressor Oil Pressure is greater than 30 psi formore than 5 minutes.

to be Taken — The compressor will continue to run.Reset Method — Manual

Causesfollowing items:

— If this condition is encountered, check the discharge and oil sensor wiring to the Main Base Board and CPM board

boards for a faulty channel faulty transducer plugged oil filter

faulty oil solenoid valve coil stuck oil solenoid valve stuck check valve

shut off valve to ensure it is not fully open

the power supply to the System Manager and unitcontrols.

93 — Circuit A (PAlarm 94 — Circuit B (P.75).76)

for Trippressor is on or off. The alarm is generated if:

— The criteria are tested whether the com- the compressor is not running and an increase in capacity is required, then the compressor is not allowed to start.

chttp://www.51wendang.com/doc/437ec10ed908de0667a81455ompressor is running and the oil level switch is openfor more than 45 seconds.

to be Takenoff.

— The affected compressor will be turnedReset Method — Manual.

Causesfollowing items:

— If this condition is encountered, check the  oil level in the oil separator

oil level switch wiring to the CPM board CPM board for a faulty channel faulty oil level switch

solenoid valve stuck open

for TripON or OFF. The units must be configured as a Master and — The criterion is tested whether the unit isSlave machine (Slave Selecttion errors has been found. The “nn” refers to the error code, MSSLMaster/Slave Select=2), and one of the following configura-, MSSL=1 and Master/listed in Table 51.

to be Takencontrol.

— Unit not allowed to start in Master SlaveReset Method — Automatic

Causesfollowing:

— If this condition is encountered, http://www.51wendang.com/doc/437ec10ed908de0667a81455check the  CCN wiring.

Control power to each Main Base Board, master and slave. Move to first position.

unit configuration.

for TripON or OFF. The alarm will be generated if the  — The criterion is tested whether the unit isModel, TONS=0.

CapacityAction to be Taken — The unit is not allowed to start.

Methodplete. The configuration must be manually completed.

— Automatic after factory configuration is com-Possible Causesthe unit configuration.

— If this condition is encountered, confirmCriteria for TripON or OFF. The alarm will be generated if the one of the — The criterion is tested whether the unit isfollowing configuration errors is detected by the control. The“nn” refers to the error code listed in Table 52.

to be Taken — The unit is not allowed to start.

Method — Automatic after reconfiguration is completed.Possible Causesthe http://www.51wendang.com/doc/437ec10ed908de0667a81455unit configuration ( — If this condition is encountered, confirmNone, UNIT).

for TripON or OFF and when the machine receives a Carrier Comfort — The criterion is tested whether the units areNetwork&#174; (CCN) command for an Emergency Stop.

to be Takenstart.

— Unit will stop, or will not allowed toReset Methodis received.

— Automatic, once a return to normal commandPossible CausesCCN Emergency Stop command.

— If this condition is encountered, check for81

Table 51 — Master/Slave Alarm Code

ERROR CODE01020304050607080910111213

master or slave water pump is not configured while the control of the lag unit pump is required (lag_pump = 1)

and slave units have the same network address.There is no slave configured at the slave addressSlave pump_seq incorrect configuration

://www.51wendang.com/doc/437ec10ed908de0667a81455arThere is a conflict between the master and the slave LWT option: the master is configured for EWT control while the slave is configured for LWT control.

is a conflict between the master and the slave LWT option: the master is configured for LWT control while the slave is configured for EWT control.

is a conflict between the master and the slave pump option: the master is configured for lag pump control while the slave is not configured for lag pump control.

is a conflict between the master and the slave pump option: the master is not configured for lag pump control while the slave is configured for lag pump control.The slave chiller is in local or remote control (chilstat = 3)The slave chiller is down due to fault (chilstat = 5)

master chiller operating type is not Master: master_oper_typNo communication with slave.

and slave heat cool status are not the same.

://www.51wendang.com/doc/437ec10ed908de0667a81455EGEND

—Entering Water TemperatureLWT—Leaving Water Temperature

52 — Illegal Configuration Alarm Code

ERROR CODE010203

size is unknown.

option selected for Heat Pump machine.

Gas Bypass configured for a Heat Pump machine.

100 — Pump 1 Fault (P.32)Alarm 101 — Pump 2 Fault (P.33)

for Trip — The criterion is tested whether the units areON or OFF. This alarm will be generated if the cooler pumpinterlock opens. When starting the pump, the control mustread an open circuit for 3 consecutive reads. If the pump isoperating and the circuit opens, the alarm will be generatedimmediately.

to be Taken — The pump and machine will be shutdown. If there is another pump available, the control will startthat pump, restart the machine and clear the alarm. If no otherpump is available, the unit will remain OFF.Reset Method —http://www.51wendang.com/doc/437ec10ed908de0667a81455 Manual.

Causes — If this condition is encountered, check thefollowing items:

interlock wiring circuit

control signal to the pump controller

cooler pump contactor for proper operation control voltage for proper voltage

for Trip — The criteria are tested when the unit is ON.This alarm will be tripped if:

the flow switch fails to close after the Off/On delay

the condenser pump control is enabled (Condenser PumpSequence, HPUM) and the condenser flow switch fails toclose after the condenser pump is commanded on for morethan one minute

the flow switch is opened after normal operation.

to be Taken — For criteria 1 and 2 the compressor(s)will not be started. For criteria 3 all compressors will stop withno delay.

Method — Manual.

Causes — If this condition is encountered, check thefollowing items:

low chttp://www.51wendang.com/doc/437ec10ed908de0667a81455ondenser water flow faulty flow switch flow switch wiring

faulty channel on MBB (main mase board)Alarm 103 — Circuit A (P.34)Alarm 104 — Circuit B (P.35)

: Alarms 103 and 104 are not used or supported. If thiscondition is encountered, confirm machine configuration.Alarm 105 — Circuit A (P.37)Alarm 106 — Circuit B (P.38)

for Trip — The criterion is tested when the circuit isON. This alarm will be tripped if the circuit capacity is reducedmore than 8 times in 30 minutes due to high discharge gas tem-peratures. If no override occurs in a 30-minute period, thecounter is reset.

to be Taken — The affected circuit will be shut down.Reset Method — Automatic, after 30 minutes. If the alarm iscleared via the Manual method, the counter will be reset tozero.

Causes — If this condition is encountered, check thefollowing items:

Maximum Condensing Temperature (MCT) for the prohttp://www.51wendang.com/doc/437ec10ed908de0667a81455persetting

noncondensables in the refrigerant circuit low condenser water flow

refrigerant charge (overcharged) condenser tubes fouled

discharge service valve to be sure that it is open. Check thedischarge pressure transducer for accuracy unit configuration

108 — Circuit A (P.40)Alarm 109 — Circuit B (P.41)

for Trip — The criterion is tested when the circuit isON. If the circuit operates and if more than 8 successive circuit

capacity decreases (stop the compressor) have occurred becauseof low suction temperature protection overrides, the circuitalarm will be tripped. If no override has occurred for more than30 minutes, the override counter will be reset to zero.

to be TakenAlert relay will be energized.

— ALARM_LED will be set to blinking.Reset Methodto zero. If the alarm is cleared via the Manual method, the — Automatic, when the override counter retuhttp://www.51wendang.com/doc/437ec10ed908de0667a81455rnscounter will be forced to zero.

Causesfollowing items:

— If this condition is encountered, check the  suction transducer for accuracy suction transducer wiring EXV operation

refrigerant charge (undercharged) evaporator loop for low water flow evaporator leaving water temperature

service valve to be sure it is open. Discharge pres- sure transducer for accuracyunit configuration

: Alarm 111 is not used or supported. If this condition isencountered, confirm machine configuration.Alarm 112 — Pump 1 (PAlarm 113 — Pump 2 (P.73).74)

: Alarms 112 and 113 are not used or supported. If thiscondition is encountered, confirm machine configuration.Alarm 114 — Circuit A (PAlarm 115 — Circuit B (P.78).79)

for Tripis operating. This alarm will be tripped if the discharge gas tem- — The criterion is tested when the compressorperature is higher than 212 F (100 C) fohttp://www.51wendang.com/doc/437ec10ed908de0667a81455r more than 90 seconds.Action to be Takenstopped.

— The affected compressor will beReset Method — Manual.

Causesfollowing items:

— If this condition is encountered, check the Maximum Condensing Temperature (MCT) for the proper setting

noncondensables in the refrigerant circuit refrigerant charge (overcharged) condenser tubes fouled

discharge service valve to be sure that it is open, check the discharge pressure transducer for accuracyunit configuration

117 — Circuit A (PAlarm 118 — Circuit B (P.81).82)

for Tripsor is operating to prevent pumpdown conditions when the — The criterion is tested when the compres-suction service valve is closed. This alarm will be tripped if theeconomizer pressure is below the suction pressure more than1 bar (14.5 psi) for more than 10 seconds.

to be Takenstopped.

— The affected compressor will beReset Methohttp://www.51wendang.com/doc/437ec10ed908de0667a81455d — Manual.

Causesfollowing items:

— If this condition is encountered, check the  suction service valve is closed sensor wiring to the EXV boards boards for faulty channels faulty transducer

EXV operation

120 — Circuit A (PAlarm 121 — Circuit B (P.87).88)

for Tripsor is operating and the active cooling set point is greater than — The criteria are tested when the compres-32&#176; F (0&#176; C). This alarm will be tripped if:

The circuit is operating at 100% of capacity and the mea-sured current is less than 1.1 times the current at fullyunloaded 30% for more than one minute.

to be Takenrun.

— The affected compressor will continue toReset Method — Manual.

Causesfollowing items:

— If this condition is encountered, check the  faulty unloader solenoid valves faulty unloader solenoid coils

wiring of the unloaderhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 solenoid valves CPM board for faulty channels

transformer reading for accuracy

: Alarm 123 is not used or supported. If this condition isencountered, confirm machine configuration.

or off. This alarm will be tripped when the unit is ON if:Criteria for Trip — The criteria are tested when the unit is  The flow switch fails to close after the Off/On delay.

the master/slave control is active, the unit is the lag chillerand if the cooler flow switch fails to close within one minuteafter the cooler pump was restarted. The alarm is ignored ifthe lag cooler pump is stopped as a result of master/slave control.

flow switch is opened during normal operation.This alarm will be tripped when the unit is OFF if:

The cooler pump control is enabled (Sequencewhen the pump is enabled (, PUMP)  and the cooler flow switch is checkedCooler PumpsPFlow Checked if C Pump Off, pump is commandedhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 OFF for more than 2 minutes.

.LOC) and the cooler flow switch is closed after the coolerThe cooler pump control is enabled (Sequence, the Off/On delay after the cooler pump has been turned onPUMP) and the flow switch fails to close afterCooler Pumpsto protect the cooler from freezing.

and 2, the compressors will not be started.

to be Taken — If the unit is ON, for criteria for tripsout going through pumpdown. Cooler pump will be stoppedFor criteria for trip 3, all compressors will be stopped with-with no delay.

the unit is OFF, for criteria for trip 1, the unit will not start.Reset Methoding. Automatic if no compressors are operating.

— Manual if at least one compressor is operat-Possible Causesfollowing items:

— If this condition is encountered, check the  low chilled water flow a faulty flow switch flow switch wiring

Base Board for a faulty channel

fhttp://www.51wendang.com/doc/437ec10ed908de0667a81455or Trip chiller is ON and one or more compressors is running. This— The alarm criterion is checked when thealarm will be tripped if the entering water temperature is lessthan the leaving water temperature for more than 1 minute.Action to be Taken — The chiller is shut down immediately.Reset Method — Manual.

Possible Causes following items:

— If this condition is encountered, check the Check LWT and EWT wiring at main base board (connec- tor J6, channels 1,2).

for a faulty entering or leaving water temperature sensor.

cooler nozzles for proper water temperature sensorlocations.

for Tripor OFF and when the Servicing Alert decisions listed under — This alert is tested whether the unit is ONTime Clockgenerated if the one of the following configuration errors is MCFG have been enabled. The alarm will bedetected by the control. The “nn” refers to the error code listedin Tahttp://www.51wendang.com/doc/437ec10ed908de0667a81455ble 53.

53 — Service Maintenance Alert Codes

.01Circuit A Loss of Refrigerant ChargeSr.02Circuit B Loss of Refrigerant ChargeSr.04Water Loop Size Warning

.06Cooler Pump 1 Servicing RequiredSr.07Cooler Pump 2 Servicing RequiredSr.08Condenser Pump 1 Servicing RequiredSr.09Condenser Pump 2 Servicing RequiredSr.10Water Filter Servicing Required

.11Compressor A Oil Filter Servicing RequiredSr.12

B Oil Filter Servicing Required

to be Taken — None.

Method — Manual, after the service has been completed.Possible Causesencountered, check the following items: — If the Sr-01, 02, or 03 conditions are  sensor wiring to the Main Base Boardsensor for accuracy

132-01 — Circuit A (A1.01)Alarm 133-01 — Circuit B (B1.01)

for Tripcompressor is ON. This alarm will be generated if:

— The alarm criteria are checkedhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 when the The temperature is greater than 245 F (118 C) and it has been greater than 212 F (100 C) for 10 consecutive seconds.The compressor temperature is greater than 232 F (111 C)for 90 seconds (but less than 250 F [120 C]).

to be Taken — The circuit shuts down immediately.Reset Method — Manual

Causesfollowing items:

— If this condition is encountered, check the  faulty wiring and loose plugsfaulty CPM board

132-02 — Circuit A (A1.02)Alarm 133-02 — Circuit B (B1.02)

for Tripcompressor is ON. This alarm will be generated if: the temper- — The alarm criterion is checked when theature is greater than 245 F (118 C) and it has NOT been greaterthan 212 F (100 C) for 10 consecutive seconds.

to be Taken — The compressor will be stopped.Reset Method — Manual

Causesfollowing items:

— If this condition is encountered, check the  faulty comphttp://www.51wendang.com/doc/437ec10ed908de0667a81455ressor temperature thermistor faulty wiring and loose plugsfaulty CPM board

132-03 — Circuit A (A1.03)Alarm 133-03 — Circuit B (B1.03)

for Tripcompressor is ON. This alarm will be generated if the circuit — The alarm criterion is checked when thehigh-pressure switch (HPS) opens for more than 2 seconds.The CPM board monitors the HPS switch.

to be Taken — The compressor will be stopped.Reset Method — Manual (reset button on switch)

Causesfollowing items:

— If this condition is encountered, check the  loss of condenser water flow condenser pump failure

compressor operating beyond the operation envelope faulty high pressure switch or wiringfaulty CPM boardAlarm 132-04 — Circuit A (A1.04)Alarm 133-04 — Circuit B (B1.04)

for Tripcompressor is ON. This alarm will be generated if the CPM — The alarm criterion is checked when theboard detects a motor curhttp://www.51wendang.com/doc/437ec10ed908de0667a81455rent greater than 93% MTA (musttrip amps) and less than 2 times that for more than 1.7 seconds.Action to be Taken — The compressor will be stopped.Reset Method — Manual

Causesfollowing items:

— If this condition is encountered, check the  Compressor operating beyond the operation envelope.Incorrect MTA setting.Alarm 132-05 — Circuit A (A1.05)Alarm 133-05 — Circuit B (B1.05)

for Tripstart-up when the compressor is ON. This alarm will be gener- — The alarm criterion is checked duringated if the CPM board detects a high motor current comparedwith the MTA (must trip amps) setting for more than 450 ms.Action to be Taken — The compressor will be stopped.Reset Method — Manual

Causesfollowing items:

— If this condition is encountered, check the  compressor mechanical failure unloader slide valve failurecompressor motor failureAlarm 132-06 — Circuit A L1 (A1.06)Alarm 133-06 — Circuhttp://www.51wendang.com/doc/437ec10ed908de0667a81455it B L1 (B1.06)Alarm 132-07 — Circuit A L2 (A1.07)Alarm 133-07 — Circuit B L2 (B1.07)Alarm 132-08 — Circuit A L3 (A1.08)Alarm 133-08 — Circuit B L3 (B1.08)

for Tripstartup when the compressor is ON. This alarm will be gener- — The alarm criteria are checked duringated if:

The current unbalance on any of the 3 phases is greater than 48% for more than 1 second continuously during start-up.The current unbalance on any of the 3 phases is greater than48% for more than 2 seconds continuously during runtime.Action to be Taken — The compressor will be stopped.Reset Method — Manual

Causesfollowing items: — If this condition is encountered, check the  power failure

blown fuse or tripped circuit breakerpower wiring errors or loose terminals84

Alarm 132-09 — Circuit A (A1.09)Alarm 133-09 — Circuit B (B1.09)

for Tripcompressor is ON. This alarm will be generated if:

—http://www.51wendang.com/doc/437ec10ed908de0667a81455 The alarm criteria are checked when the The current is less than 15% MTA on all three legs for more than 1 second for wye-delta start units.

the current is less than 15% of MTA on all three legs formore than 1 second for direct start units.

to be Taken — The compressor will be stopped.Reset Method — Manual

Causesfollowing items: — If this condition is encountered, check the  power failure

blown fuse or tripped circuit breaker deenergized contactor faulty current toroid

pressure switch (HPS) trip (when auto reset HPS isused)

132-10 — Circuit A (A1.10)Alarm 133-10 — Circuit B (B1.10)

for Tripcompressor start-up. This alarm will be generated if the current — The alarm criterion is checked duringin Delta mode is not more than 25% greater than the current inY mode within 550 ms.

to be Taken — The compressor will be stopped.Reset Method http://www.51wendang.com/doc/437ec10ed908de0667a81455— Manual

Causesfollowing items:

— If this condition is encountered, check the  power supply failure to the delta contactor faulty wiring to the delta contactor faulty CPM boardfaulty current toroid

132-11 — Circuit A (A1.11)Alarm 133-11 — Circuit B (B1.11)

for Tripcompressor shut-down. This alarm will be generated if the cur- — The alarm criterion is checked duringrent is greater than 15% of the MTA on at least one phase for10 continuous seconds.

to be Taken — The compressor will be stopped.Reset Method — Manual

Causesfollowing items:

— If this condition is encountered, check the  faulty or welded contactor faulty wiringfaulty CPM board

132-12 — Circuit A (A1.12)Alarm 133-12 — Circuit B (B1.12)

for Tripcompressor shutdown. This alarm will be generated if after — The alarm criterion is checked duringthree attempts to thttp://www.51wendang.com/doc/437ec10ed908de0667a81455urn off the compressor outputs and the cur-rent is still greater than 15% of the MTA on at least one phasefor 10 continuous seconds.

to be Taken — The compressor will be stopped.Reset Method — Manual

Causesfollowing items:

— If this condition is encountered, check the  faulty or welded contactorfaulty wiring

132-13 — Circuit A (A1.13)Alarm 133-13 — Circuit B (B1.13)

for Tripcompressor start-up. This alarm will be generated if the CPM — The alarm criterion is checked duringboard detects a phase reversal from the current toroid.Action to be Taken — The compressor will be stopped.Reset Method — Manual

Causesfollowing items:

— If this condition is encountered, check the if power supply lead at the terminal block is not operating at the correct phase

power supply is crossed when going through the currenttoroid

132-14 — Circuit Ahttp://www.51wendang.com/doc/437ec10ed908de0667a81455 (A1.14)Alarm 133-14 — Circuit B (B1.14)

for Tripcompressor is ON or OFF. This alarm will be generated if the — The alarm criterion is checked whether theMTA setting is out of the allowed MTA range.

to be Taken — The compressor will be stopped.Reset Method — Manual

Causesfollowing items:

— If this condition is encountered, check the  incorrect MTA settingsfaulty CPM board

132-15 — Circuit A (A1.15)Alarm 133-15 — Circuit B (B1.15)

for Tripcompressor is ON or OFF. This alarm will be generated if — The alarm criterion is checked whether thethe CPM board S1 and S2 setting does not match softwareconfiguration.

to be Taken — The compressor will be stopped.Reset Method — Manual

Causesfollowing items:

— If this condition is encountered, check the  incorrect CPM board settingsfaulty CPM board

132-16 — Circuit A (http://www.51wendang.com/doc/437ec10ed908de0667a81455A1.16)Alarm 133-16 — Circuit B (B1.16)

for Tripcompressor is ON. This alarm will be generated if the CPM — The alarm criterion is checked when theboard S1 setting has changed.

to be Taken — The compressor will be stopped.Reset Method — Manual

Causesfollowing items:

— If this condition is encountered, check the  incorrect CPM board settingsfaulty CPM board

132-17 — Circuit A (A1.17)Alarm 133-17 — Circuit B (B1.17)

for Tripcompressor is ON. This alarm will be generated if the CPM — The alarm criterion is checked when theboard detects a power failure.

to be Taken — The compressor will be stopped.Reset Method — Manual

Causespower interruptions.

— If this condition is encountered, check for85

Alarm 132-18 — Circuit A (A1.18)Alarm 133-18 — Circuit B (B1.18)

for Tripcompressor is ON. This alarm willhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 be generated if the CPM — The alarm criterion is checked when theboard detects a software error.

to be Taken — The compressor will be stopped.Reset Method — Manual

Causesfollowing items: — If this condition is encountered, check the  electrical noisefaulty CPM board

132-19 — Circuit A (A1.19)Alarm 133-19 — Circuit B (B1.19)

for Tripcompressor is ON. This alarm will be generated if the CPM — The alarm criterion is checked when theboard detects a software error.

to be Taken — The compressor will be stopped.Reset Method — Manual

Causesfollowing items: — If this condition is encountered, check the  electrical noisefaulty CPM board

Test — must be on for Service Test.

power and control circuit power

various devices within the chiller, such as compressors, min-The Service Test function is used to verify proper operahttp://www.51wendang.com/doc/437ec10ed908de0667a81455tionimum load valve solenoid (if installed), cooler pump(s) and re-mote alarm relay. This is helpful during the start-up procedureto determine if devices are installed correctly. See Fig. 59 for30XW wiring diagram.

TEST WITH NAVIGATOR  DISPLAY  — Touse the Service Test mode, the Enable/Off/Remote Contactswitch must be in the OFF position. Use the display keys tomove to the Service Test mode. The items are described in theService Test table. There are two sub-modes available. Test EnableServicesors and minimum load control. In this mode the compressors, T.REQ allows for manual control of the compres-will operate only on command. The capacity control, headpressure control, and EXV control algorithms will be active.There must be a load on the chiller to operate for an extendedperiod of time. All circuit safeties will be honored during thetest. pumps, oil solenoids, unloader solenoids and status pointsQuick Test Enable, Q.http://www.51wendang.com/doc/437ec10ed908de0667a81455REQ allows for test of EXVs,(alarm relays, running status and chiller capacity). If there areno keys pressed for 5 minutes, the active test mode will bedisabled.

enter the Manual Control mode with the Navigator display, the Enable/Off/Remote Contact switch must be in theOFF position. Move the LED to the Service Test mode. Press to access TEST. Press  to access T.REQ.OFF. Press will flash. Enter the password if required.T.REQ value to ON andpress . Place the Enable/Off/Remote Switch in thearrow keys to move to the appropriate item. To activate an itemlocate the item, press  and the display will show OFF.

will flash. Use either arrow key toON and press . The item shouldand the display will show ONturning the Enable/Off/Remote Contact switch to Enable. Press and ON will flash. Use either arrow key to changeOFF and press . The item should beinactive.

enter the Quick Test mode, the Enable/Off/Remohttp://www.51wendang.com/doc/437ec10ed908de0667a81455teContact switch must be in the OFF position. Move the LED to

[此处图片未下载成功]

to access TEST. Use. Press  to. Press .QUIC value toON and press . Quick Test mode is now active. Fol-vate a component.

— Test the oil solenoid circuit A (see Table 54).Contact switch must be in the OFF position.

must be applied to the unit. Enable/Off/Remoteitem values from OFF to ON. These discrete outputs are thenTest the cooler pump(s) and alarm relay by changing theturned off if there is no keypad activity for 10 minutes. Test thecompressor and minimum load valve solenoid (if installed)outputs in a similar manner. The minimum load valve sole-noids will be turned off if there is no keypad activity for10 minutes. Compressors will stay on until the operator turnsthem off. The Service Test mode will remain enabled for aslong as there is one or more compressors running. All safetiesare monitored during this test and whttp://www.51wendang.com/doc/437ec10ed908de0667a81455ill turn a compressor, cir-cuit or the machine off if required. Any other mode or sub-mode can be accessed, viewed, or changed during the ManualControl mode only. The display “0” as long as the Service mode is enabled. The STAT item (Run Status VIEW) willsub-mode value must be changed back to OFF before the chill-TESTer can be switched to Enable or Remote contact for normaloperation.

: There may be up to a one-minute delay before theselected item is energized.

TEST WITH TOUCH PILOT  DISPLAY  —To enter the Manual Control mode with the Touch Pilot dis-play, the unit Operating Type must be Local OFF. Use theSTART/STOP button on the Touch Pilot display to stop themachine if necessary. To place the unit the Service Test mode,select and configure Main Menuword if required. Configure the desired compressor output toService Test Enable STATUS Page Down to YES. Enter the pass- SERV_TSTON. Then press the START/STOP buhttp://www.51wendang.com/doc/437ec10ed908de0667a81455tton on the Touch Pilotdispaly and select Local on. Return to the SERV_TST screento start and stop compressors or manually operate the compres-sor slide valve.

Local OFF. Use the START/STOP button on the Touch PilotTo enter the Quick Test mode, the unit Operating Type mustdisplay to stop the machine if necessary. To place the unit inQuick Test mode select DownMain Menu STATUS PageEnter the password if required. Configure the desired output to QCK_TST1 and configure Quick Test Enable to Yes.ON, percent output or stage to confirm operation of thecomponent.

Table 54 — Testing Circuit A Oil Solenoid

FOR FIG. 59

[此处图片未下载成功]

ALMALTCBCDFSCPMCPMPCWFSDPTECEXVECTEMMEXV

————————————

Breaker

Flow Switch

Protection ModuleCondenser Pump RelayChilled Water Flow Switch

Pressure and TemperatureEconhttp://www.51wendang.com/doc/437ec10ed908de0667a81455omizer Electronic Expansion ValveEntering Cooler TemperatureEnergy Management ModuleElectronic Expansion Valve

———————————

-Installed OptionHot Gas Bypass

Water TemperatureMain Base BoardMinimum Load ValvePlugPump

Gas TemperatureLoadshed

Pressure TransducerTerminal Block

[此处图片未下载成功]

88

PPENAIXD—AT OUC PILOTHDIS LPYAT ALBSETh eTochuP loit d spiay labtel sae rfromtate dn ilaphabetcial rodr ebsedao n he tpointna m edecristpin.oT h lenien muber crorepsndo ts oth leni eumner fbormt h toept e houcT hPlotis recne A .rcso refseencer t toeh CC Ntblesa n ippAenixdC s proviiedd.Plea e srefr te Aoppnedi C xfr ranoe andgco fingurtiona efaudt inlofrmtaion.OUTCHPI LT DESOCRIPTOI 1 ElNecS atg eofrb cauk p3Way VlaveP sitiono 3 aWy ValveP oitson Ciicruti CArcuit iB iCcuirt C W3yaV lvea taSus Ctircit uA Cirhttp://www.51wendang.com/doc/437ec10ed908de0667a81455citu CBriuic tC4 awyV lave iCrcituA 4 w ayV alve iCrcui t B 4Wa Ryfeigrraen Vatlv eCrcuiitA CicrituB C ircuti CA ticavt eAtcie vapaciCt Overridy AectiveDem na diLmi VtalA cutlaCa apciytA cualt apaciCty Lmiti cAtaluC hlier lurCert Anctul aCilleh rCurentr iAr oCndEn etr alvV eAAi r Cnd oEnertV lav B Air CendoE netrnigV alv A irA oCdnEnteri gn VavlB ir CAodn eaLivn gValv A irA CnodL eavni Vgal BvAi CorndLe vinga Vavel AAir ondCLeav in Vglva Be iA rColoe Rdecalm iSle Aarl E

rioirty laAr Rmeal yuOtput Alamr elRyaStat u Alsar Roumintg ontrClo laAm Srtae tlAar Smsyte Namm Aleert eRla Oytuup tleAtrRel a Sytatus Atuo haCngeoevrA ctiv Aeto uhCnaegovreS leectAut oSt rta Whe nMS Los tAUXB ora#d 1Par Nutmbe rUA XoaBdr 2 P#rt aNubmreAUX Bo rda# 3 aPr Ntmueb rAUXBo rad 4# PrtaNu mer bUAX oBadr 5#Pa rtN umbreAv raeegCt rlW atr eeTp mLEEGN DRO— Re a OnlydRW— Read/W rite OUTCHPIL TOP INO TNMAE ehsb_ck a_3W_QVL Vc_fvlv_ fc_val_v bf_vchttp://www.51wendang.com/doc/437ec10ed908de0667a81455lvc F_CV_LVA _F_VLV_B FCCVL_V_C _QR_A VQ_R_B VV_ARRV B_ R_V ccCbrnodaov r_eap DEcM_ILMc pat ca__pil mTTOC_RU TORT_UCRR QH_EAR_AQ_H ERAB _rh_ea_a rhe__b aQHR_AL_ Q_HRAAL_ Bhrla__a r_lahb_r ecl_po EQP_TYtPQ_A LARM ALAMRUO TLRM_CATN AL AMLMRNAM Q_ALE_TRALERT Moed12 _uaots_e lato_smuAU X_RDB1AUX _BR2 AUD_BXRD3A UXBR_D 4UAX_RB5D crt_avgl OTUHCPI LTO APHTM AINME UNCoMEANI MNU_QTST MA2INM NEIN AENUIA NMNUEAINMM NULMANI EMNMALN MINEAIM NMNE_KTT2SM IA MENN_ 2MAN MINU_ MDIAN ENMU_M IN AENMU_ MAIDNMENMINAME NIN AMENAMI MNENUANI MNUEMAMN IENMUME NUTAMNIMEN US_TSCT MAI2 MENUNS_TCS2 MAIT MNEUNIAN ENMU://www.51wendang.com/doc/437ec10ed908de0667a81455ustMMAN MEIN_KTS2 TAIN MENM_TTS2MA NIME NUSLAIM MNEUIAMNIM NUESMYAIN MNENENUMS-KTST1 AIMNMENUMNANI EMNMMIAN MENIAMN MENUFAMNI ENM_TS1T MAINM EUNSNMIN AENUMMAINE EMNMINA MEUAIMNM NEUM_P MAINNMENU aintMB_PN DAMINM EU_NPM INAMENU Mai_PNM IAN ENU_PNDMAI NM EUNMa

:EI n palcsewh eerd upicltaedp oni tnae mesdrcpitinos ewreu eds,hte heaerds erw edaeddto he toinp ntmea dsecirtipo nto diferefntiae thtme.F or xameple, th eedsrcption iCmporseorsOu tut ip ussd ehter temies of cirruictsA B,,and C .I nthi tsale, tbehd ecrspitonsiinc ule CirdA,Ci B,r ndaCir .CLINE35 1114 24 34 152 535 3 141 2 442 231 20 2 81 90 13 2 3 157 5 4 82 71 27 0http://www.51wendang.com/doc/437ec10ed908de0667a81455 1 42 8281 13 594 9 13 12 8184  6 578 2 RAD/EWR TI ER RWW O RR RO ROORO ROR RWW OR ORR O W RROR OORR ORO RO RW RWRO R OR RW WRO O RWRR RW RWORW RO RW RW OR ROR WR WR ROO R OR ORO O CCNRTA LB ENMAEC nfoiugraitn Toblesattsu Dispayl aTbel_ST2 TSatutsDis laypTa beslLSatus Distlpy aaTblesOStatusD silpy aaTbelut DsipsaylT alebSOtats DiuspaylTa lesbSLttas Diuslpa TybaleLtSatsu iDspal yableTsQCK_STatts uDipslay aTble_ST2TS atut siDpslayTa lbes_D CtSats uiDslpa Tybaes_CDS ttus aisDpay Tlbales_ CoDfignrautionTab el

Maitennanc Dieplay sTblesSatts uDsiplyaT ablseGEManitnancee DiplsyaT albsMCianteannc DispelayT albsMintananceeD iplas TabylsCtSatsuD silay paTbleItStuas Diplsay Tabels_ST2 TtatusSDisp ly aTbaes_ST 2Status Diplsya aTlbeSMtaut sDsiplyhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 aTalbstaSuts Dsilap Tabyle_2 taSus tDislpayT albe_sSTT S2taut siDslaypTa lbseRASatust ispDal TablysSeMricev oCnigfruatinoT ablseYCofniuragtinoTab lesALASatustDi spay laTbesl_STT1S attsu DsiplayTa lbeCoNnfguriatoinT baelS0atut Disspay lTbaleCNofnguirtaino TablseSRtatusDisp al yTbleasQC_TTS St1auts Dsilapy ablTesSTATStatuNsDi psal yabTlseCEonfigraution TblesaUSSerEvce ionCfguraitoi Tabnles1Miatennacn Diselpay ablesTB_NP aMnietnnca Diselpay Table_sNP MaitenannceDi plsayTa belsB_PN OMantenianecDis lap TyabelsBOA_ NaintMneacenDisp lya TbaeslB_PN MintanaecneDis lpa yablTseLOA

[此处图片未下载成功]

8PPENDAIX— AOTCH UPLIO  TDISPAL YTABLS E(cnot)TOUH CIPOLTD SCERPIITNO BlalV alevC oslni gutOCi crit uA Criciut BC iructiC B allV alveO epingn uOt Circuihttp://www.51wendang.com/doc/437ec10ed908de0667a81455 A tiCcrui Bt CirciutC Ball Vlvea ositiPn oiCcuri tA Ciruci BtC icurt Ci Bua drat eriBe fnow Swilct hSP BinreF eezr eSteopnitB rodacsa atckonwleder gBs CuC NChiler lSart/ttSp Coihller apCcatyi in-100vCh ille CrapcatiySi gan lChliel rCurert Limnit Chiller Crurnt Lieim Chtillr ienSer eis hilCle rOccupid?eChi llerR edyaO tpuu ChtilelrRu nnni Ogtuut CpWSH emTperatre uiCcurt CiH ater Teem pircCit Loadiung eSquenc ComemFa ilur Retrey Tmi eomC Ap uMt Tsip Arps momp A C1 ConSif gSwtci (h-&gt;1) C8op mBMus tTrip Am spCo p mB 1S oCnifgS itcw (h-&gt;18) Com p CusM Tritp Apms ompCC S1 oCnigfSwi tc (8h-&gt;1)C omrepsso ArDis abelC opresmor sAH uosr ompressoCr AoHurs CmpoersosrA O tupu Cotpmersor A SsarttsC mporsesor AStrta sCoprmseor BsDi aslbeC ompressro HBuos rComrpsseo Br HorusCo pmersors BOu putt oCmrpessr BoSta rtsC oprmessr oBSt atr soCprmesso rC Diables Cmorepsso rC ouHr Csmorpesos C HrurosC opmessror OCutpt CoupmresosrC SatrstC oprmssoer http://www.51wendang.com/doc/437ec10ed908de0667a81455CSt arts ELGND RO E—Re adO ly RW—nR aed/Wriet OTUC HPILTOPO NT NAIE IMO_CL_S AISOC__LB SIOCL__ ISCO_P_AOI S_OP_B IOOSO_PC _SO_IERF IAOSREF_B IS_REOF BCua drta flow_es lopwetss BroapdcstaB s uCHIL_S_S _CAQO CTAT_010PC RU_LRM CIURR_LMIl _seril eCIH_OLC CQR_EDAY _QRUN HWCTEMSPT HE_A_TC ela_cdr RETRiYT_Mcpa_mta cc pa_1_sc cpb_matc pb_s1cc _ccp_mtac pc_c1s_ cu_cp_nah r_p_c Ha_RP_AC Q_CP At_sc_a sp_tp_a cnu_p_bc h_rc_pbHR_CP _BQ CPB s_tc_pb s_t_c_p bnuc_p_ chr_p_ccHR C_PC _QCPC_ t_cspc_ ts_c_c pOUTH CPLIOTP AT HAINM EMN_ MDIAN MEN_MAI NME NUSt_CDMAI NEMUNS_D MCAI MNENU_AIM MENN_DC MINAME N_M AI MENNUStat_ MDINA EMNU_ DMIA MNENU-DIMA I MNEUCMIA NEMN\parMAIN 1ENU-I MAIND MEUNCrDIM IA NENMMENUut_TS1MA N MINU://www.51wendang.com/doc/437ec10ed908de0667a81455NM IA MENUMAIN CMENMIA MENN_LS MVAIN EMNINAMEN_TTS1 AMN IMNU_ MA1I MENNMEIN AMEUNSTAINM MNEMARNIME NUCoMFAN MINUY AINMME UMAIN ENUMY AIN MMNEM AN MIEUYAIN MENURMAI NM NUES_NUALB AIN MENUMAI MNENRAIMNME NU_RTTSM AI NENUMANI EMNUMAINR MEU_UPNBLAM AN IENMANI MNEUStMRIA NMNE_RTSTM ANIM NUN MNEHMINA MEN_NABLU MIA NEMUNSerMRIN AENUUAIM NMEU_TS MTIAN EMNOMIN AEMURILN 2E2 2 22223 2 3 3 221 1 212 9 32 01 7 56 443 1 241 2http://www.51wendang.com/doc/437ec10ed908de0667a81455 4 614 2 404 38 312  6 3 7101 12 7 3 3 8 34 9 5 105 64 1 7 7 1218 REA D WR/TE IRO O RR RO OOR ORRO RO R OR ROWR WR OR ROO WRRO R ORO RWR O W RRW RO R OWRRW R W R RW RW WR WR WWRRW RO W RW ROR R RWWR O R RWW R ORWRW O RRW R WR OCCN ATBEL ANEM Satts Duislap TybaeslC_ SDattus Dsiplay Tbales_D tSatsuDi slayp aTlbes_ SDatts DusipaylTable sCIRC_D tatus DSislapyTa bls_S tatu Dispsaly ablTesS_attu sisplayDT ales_A DtSaustD islpy Tabales_taSts uDspial yabTeslC_C DCnoigufrtaion ables!P_XXA QerviceSC onifuragiotnT baesS1ericveC noifgruaiot TablnseSEC1nfoguriaiotnT baels!Ct5_XADQ XoCnifguraiotnT alebs!CtlrD_DAXQX SttasuDi plasyTa besatts uispDal Tyalbe_1Statu s iDpsal yTalesbMaintneacne Diplsy aablTseLOASatut siDpsal Tyabelofniugartio TnabeslM_Stat usD sipay TlbaesTSatust Dipsay laTbel_KTThttp://www.51wendang.com/doc/437ec10ed908de0667a81455S St1tus DaiplaysT bale_ST Stat1s DusplaiyTableDi plsa TaylesboCnifgurtaoni TblesaRoCfigunartinoTable sAL0 1Servic eonCigfruatin TaboleRSe vrcieC noifugaritno TableYeSricv eCnfiguratioo nabTelsA erSviec oCnfiurgtaoni Tales2SrveiceC nofguiatrin Toblas2ServiecC nofgiratuion abTles2eSricveC nofigrutiao_ABN LSrveiceC nfoiguariot Tnbalesut sDislpyaTa beslSatts uiDslpyaT albse_TVTS Service Cofingratuio nabTlesSOatust DiplsayTab leTerviSce Cnfoguiatrin_BA LSevrceiC noigfrution aabTleStatuUs Dsilpy TablesOStatsuDi plsya Talbse_Servce Confiiguarton iaTbelsUtStaus isplDayT blaeSRrvieecC nfigourtian_UPNAL BervicS CoenfigruatoinT baleSattusDi pslyaTa lbettau Displsy TablesaS_VST STreivc Ceonfgiuratio Tnbael://www.51wendang.com/doc/437ec10ed908de0667a81455UsPDHOURTSttua siDsplya abTelsSR90

[此处图片未下载成功]

APENDPI XA—TOU H CILOT  PDSPLIAY ABTLE S(cotnTOU)H CIPOTL ESCRIDTPIN COoloe Prup RmunS tats CouoerlP upm Rosattoni Coloe rumpP Sesuenqce oCoinl gIec Septoint Cooing RlapmL odiang Colingo Rsee Dtg. Vaelu eCoolignR ese SetecltCooling etSpoit 1n Cooilg Setnpint 2 ooolCni/grFeeoColT imoetu CPum p1 Ctl elDa ydays( )PuCm p Ct2 Dllaey (day)sCurr nt eAlamr1 Crurnt elaAm 2 ruCrrne Alatm r3C rurent Aalmr4 urCerntAlar m 5Curr netAt 1 0%0 oLd AaC ruertnA 1t0% L0oadB Curre t nA t00%1L odaC CrruentA t30% Loa dACur ertnAt 3 0 Load%B urrCne tAt30% Lod CaCur ret Connrto Clurrnt eoColnigP oerwCu rrnteF lul RseetValu eCurrne tull FesetRV lueaC rurnt Lemiita t 010 C%rrunetL iit mSelct eCurrne Mtode (=o1cup.c)Cu rert Mnode 1(o=cucp) Cu.rrnteNo Rees Vtlau CerruentN oReestVa leu Crreut nOcuc pePird#o uCrrentOc cp Pureodi# urCrne Octucpei Tidme uCrrnt Oceuciped Tme Currine Ptash 1ehttp://www.51wendang.com/doc/437ec10ed908de0667a81455Comp  CurrentA Phaes Co1pm B uCrenrt Phae s1 CmopC Curr nt Pehas 2e oCpmA Curr netPha se2 Comp CBurentrPh ase2 Co pmC uCrretn Pase 3h CopmA C urret nhPae s3C ompB C urrnt Peash e3 Comp C EGLEND OR— Rad enlOy WR—R ea/Wrdtie TUOCHP IOL TPOINTN MAECP MUDEF MPod_e07c uppmse_q ic_es cramp_sp cpr_egdc rse_ clsp 1spc2 cft_muotc pmp1_uc cpupm_c2a lrma_1alar _m2 aalr_3 almam_r 4lara_m 5ur10c_a0 cu100_brc ur010_c cur3__0 cura_03b_ urc_30_co _ntcl coor_plr wv_c_fu rv_hrf_ uurcrf_l cuurr_el MOsE DODEM v_r_nc v_ho_no PEr-RNOPER NO S-RTTITM SETTTIMR Ecp_cura cp1bcu_1 rcp_ccu1 rca_cpur 2cp_cubr cpc_cur2 cp2ac_r3u cp_bcru3c p_cuc3 rTOCU HPLIO TPTHA MANIM NUN MINUMENMUMEUAI NEMNUSNMINA MNEUSeAINMENgMINA MNUESeMTINA EMUNSMIAN EMUMOAINM EUMIA NMEN://www.51wendang.com/doc/437ec10ed908de0667a81455FGT AMIN MENUStaAIMNMENTAMIN ENMNMAIN MENUAIM MNENINME UMTINA EMUME NMCIA NENUMATN IMNUEMaFAIM MNNUNIM NEAINM MENMANIMEN USetMATI NMNEMNIN MEANUIA NMNEMAINE MEUNMSMAN MENIMSIN MANUEAMINMENU SeptiotNAIM NMNUPOS1M AIN MNEUMPOS 2MAI MNEUOP1S MINAM NEOOP2SMA N IENUMM_PRAS MAHNIM NUEM_RPAH SAIMN ENMU_HPASMA N MEINU_RPAH MSAI NMEU_AH MASI MNEN_PHA MSANIM NU_M AIN MEN_A MAIS MNNEU_A LSINE13 8 8  14 431 1 9 3 27 5 61http://www.51wendang.com/doc/437ec10ed908de0667a81455 41 15 671 1 18516 1 72 13 141 441 04 23 10 131 9 32 22 55 1 4  27 58 3 96 EAD/ RRWIT EO RORR W W RRW WRRW W RW RR OR WWR R ROO O RROR OR RO OR OOR O RRO R RO OWRRW R RWW O RORRW RW RO O RR OR RO OROR OOR RO O RO RR OROCC N TALB EANMESt tua sisDlpya TbaelSEattu Displas yablesTDCnoifguatiron TbaesSRtepint oCnoigufraiot nTbaeslSeTtpiont Cnfigoruaito nabTeslSetSointp Cnofgiuatrin oTblasfignuraitn oabTelStpoeni toCnfiuratgoinT ablesSNetponitCo fniguatroi nTbleaNSatus tDsilpy TaableevrceiC nfioguatiro nTalebsMAIrvieecCon fguiraito nablTesMAStautsD spialy ablTsTtaSustD sipalyT ablsesu Dipsla TyblesaGSatut sDsiply TablaeItSatusD iplsy aaTlebsMaitnnaene Dcsplayi aTlesMinaetnace niDplasy Tbaesltennane ciDsply TaabesMaiCntneanec Dipslay aTbesaMihttp://www.51wendang.com/doc/437ec10ed908de0667a81455tenannc eDspliy TablaseLtnnenae Dcipsla TaybelsLTtatSsuDisp la TyalebsSTATEGStaNtu siDplsy aabTelsFetpoSit nonfigCuartin oaTlbstpeoin Cotnfiguraitno Tbaesifgurtaoni TalbeCRnfiguraoitno ablesTMaRinetnnaceD spilyaTa lesS M1anientane Dicplasy TbaesPO2 SStepont Configiuraiot nabTlsSItepino tConigfrautoni aTbesMaIintennaecDi psla yaTlbsPOS Mai1tenanne Dcispayl abTlseO2O2P MSaitnnaenc eiDsplayT ablePO1S aMnteinncae Dislpya aTbeslO2 MaSnietnanc Deislpy Tabale_RHPSA MEiantnenac eisDlap Taybel_PUASHEMai tenance nDsplay Tabies_PHSAE Mintaenane Dcipsaly Tbleas_HAPSE Mainetance Dnsplayi aTleb_HPSEAM aintneacn DeispalyTabl es_PHCSEAM inaetance DnipsaylT albse_PHARESM ianetance Dinspaly ablesT_HPSE MAintanaecne Dspila Tables_UHPSEA91://www.51wendang.com/doc/437ec10ed908de0667a81455r

[此处图片未下载成功]

PPEADNX AI— TUCHOPILOT  DSIPAL TYBAELS (ocnt)OUCTHPILO TESDRICPITN OoCpmerssroOutput Cir ucti CAicuir B tirCucit CCopmrsesor Scutio nTep CmicuirtA C icrit u BCrcuit C CoidnnseerEn trieng lFud Cinodenes rlFw Soatut Csnodenser luiF Tdye Cpnoednsr Leavien gFlud iCndeoners Pmup#1 oCmmndaConden se Pumrp# 1Huosr oCndesnr Pume p#1Hour soCndnesr Pemp#u Comman2 dondCenser umP#p Hours2C ndensoerP mu p2# oHru sCnodener Psump1 Condense Prup m C2ndoesern Pmpu sotatRino ondCesne PurmpsS quence eCnoensed Wartr Veal Se loCtnor PlontiC ntroo loiPnt CotrnloT yepCo trnloldeTe p ErmorrC notorlel Wadtr eTme pool ChaCneogvr eSepttC ooerlEnter ng iFludi oCoel rEtnerig nlFiu dColoe rxchEagenD T Cri ACoo le ExrhacnegDT C i B Coroer Elxhancge DT irCC Coler Fool Swtpoine tut OoCleo rFowl wStci Coolehr lFuidTy e pooleC rHaeter Aticve Cooel reaHet CrmmaondC olore eatHr eelDa tpt SCooer Heltare utOutp oColer eHtare Sleet coClore eHaehttp://www.51wendang.com/doc/437ec10ed908de0667a81455trT mep oolerCLea ivn FlugdiCo lore Laevin Flgiu dColore incP Ctlh oinPtA Co olerP icn htCl Poni tB oCleor inPhcC l Ptoit n CCooel rPup#m1Com amd Coonle rPum#1 pHous rooCer Plmpu#2Command Colore Pmpu#2 ouHsr LGEND RE O— eaR Odnl RW y R—ed/Wriat eOTUC PILHO POTNTIN AM COEMPA CO_M_B CPOM_P CUCT_T_A SUCTS_TB_ SUT_

_C OCN_DWT EONDCLFO cWondt_y COpD_NWT LPUMHP1 hr__hup1mhr_ hpmu 1PUHMP2 hr_hp_um2h _hrupm Q2_HPP1 QMHP_P2MMod _e7 hp1ump_esq oncdv_a lCTLRP_N TCTL_RPNT tr_ctpy tep_eror CrTRLW_T autoc_p COOLs_ET WCOO_EWL piTcn_a pihnc_hb pinc_ch SE_FTOW LLOWF_W Sflui_tp Mode_06y OCOLHETA eatehrps Q_L_CTHhea _tesl THE_TAR EOOLCLWT COO_L_WTL ipnh_cps apinchs_p pbnih_scc CPpUMP1_hr_c pmu1C UMP_2P hrcpu_2m OTUHC IPLOTPA HTMAIN EMN_D MCAIN MNU_MAI MNNUEStatu\sIRCC_DC MAN MINU_AN AMAI MENN_ANB AMNI MNE_CN MAAI NMNEMAINNMENUAMINM EU://www.51wendang.com/doc/437ec10ed908de0667a81455rERSVCI1EMAI NENMUMNAI NMEUAIM MNENRAMN IEMNUStatRMAI MNEUNMANI MNNEUSMIN MAENUIN MENUSt-TSK1T AMIN MENUS_1 MATI NMENUMNEUMAIEN MNEAMN MENIUMaMAI NENUMATI NEMUNSMTIANMENMAN MINUEMINA EMNI NEMNIA NENUMANINME NUM_CTXR LMANIME U_XCTR MLIANMENU M_CTRL MAIN VENMUAMNIM NEUINA MEUE MAN MIENMINAM NEMANIME NUSeAIM MENNU-TST1MAIN EMUAIN MMENUMAGNI MNEUStEAINM EMNN ENUM_CTRL VAIMN ENMU-CTVLRM INAM NU_http://www.51wendang.com/doc/437ec10ed908de0667a81455CERL TMAI MNEUNNMAN MEINMRAN MIENAINM NUE2  221 144 4 31 54 41 6 33 21511 4 21 61 39 240 1 8 173 58 327 2 9 2 39 33 6 133 0 281 1 217 6217 3 62137 43 437 14 212 9 210 0 1ERD/A RITWE ROR ORO RO R ROOR OR RO RO RWO W RORR OR W O RRW RWRO WR R RWO O RORR O ORR WR OR ROOR ORO R OR O RWR ORORW W RRW R RO OORRO R O O RRO O RR OROC C NTALBE AMN EtatusS iDplasyT balseC_ taSust isDlapyTab le_RD tStua sDsiplyaT aleb_Status iDplsa Tyabes_ANS atustDi slapyT able_ANS tatu Disspla Tabyle_CNA SattsuD splaiyT alebStNaut DsisplyaT alesbNerSvie Ccofniugraiont TblesaSSt ats uisplay DabTletu sisDlaypT abelGSevrci Cenofiuratigo TanlbseSatts Diuplsya TabelsStaStsuD islay pTablesSerEivc eCnofgiuratin TableosUStaustDi psayl TbalseSTusD ipsalyTa lebhttp://www.51wendang.com/doc/437ec10ed908de0667a81455sQC-TKS1TStatu Dssplai yaTbels_S1 STattsuDi spaly TalbseMODEonCfiugartoi nTalbesRSrveie coCnifgrautionTableYManitenacn eiDpsalyT blasattu sisplDay Tblaetatus SDiplsa yaTbeslnentnce Diapsay Tabllettas Diupsay TlbaelsGEtpeint Coonifgrution aaTbelTtatus DSiplsa TybleatatSu sDipslayT albsMNintaeancenD isply TablaseE_CTRXL aMnientanceD silapy abTles_ LaMnientnaec ispDaly aTbes_TRLCS ttuasDis paylTab lesSNtStau sisDlpay abTlesSTAerSvceiCo figunrtaon iableTCSta tsu ispDlya TbalsStautsDisp ly aTbleaerSvceiC ofignuraion TablteC taStusDi spaylT baels_TST1 SKreivc CenofigrauitonTa blesSatut siDplsyaT bleaNSatts uDispayl TbaelsStaSust iDsplay aTlebEaintMnaence iDpsal Taylbe_CXTL MainRentnac Despiay lTblea_CVTRL MintenaacenD http://www.51wendang.com/doc/437ec10ed908de0667a81455ipsalyT albs_VTCRLSt tusa iDpsla Tyblesau sDislpyaTa lestatuS sDisplya aTlbeStatu sisplDy Taalbes92

[此处图片未下载成功]

APPEDNI X— TAOUCH IPOTL DIS LAY PABTEL (Socn)tTUOCH IPOLT DESCRPTIOINC rrenutSet pint ouCrretn nUoccpiude iTm CeurrnteUnoccu ipe TidmeCu rert Z Mulntpliei VrlaC usotme rShtudon wuO Dtyaligt havSE t nayD foW eek( 1=oMnda) Dayylghi Sat Entv Motn Dayhilgt ShvaEn tWeeko fM ntoh Dylaiht Sav LegainvgDa yfoW eek( 1Mo=dnya)D ayligh tav SLaeivgn MntohD yligat hSav eavLni geek oWfMo nhtDayli htg aSivgnS eectl DercitiponDe rostfAc tiv en COri AeDfost rcAivte nOC r i BDferot Asticv?e CicruitA Criuit B DecrfostDuratio n Cricut iA iCruict BDefors Ftn affOest aClA Defro stF a nfOfes taCl BDe rosft Fa nStrt aCa lA eDfosrtFa n tartSC laB eDfrots Nmberu Crcuit A iiCcurtiB D ferstoNum be Crrciut AiC rcuitiB Derofs tTmpeeature Crrciit uAC ircuit BDe lt -a efRrence Deleta Crchttp://www.51wendang.com/doc/437ec10ed908de0667a81455iit Au ircCui tBDe la: tOT -A Mena SS TCricuit AiCcrui B tDlta Te ull FResetV laeuDelta  TuFl leRets alue VDltae TNo Reset V auel Deta l ToNRe st VelueaDe andm iLmit ctAie Dvmand Limeit yTep Sleet DecriPID Ga ni VarfianD T GoCloS lenoiodC ricituA C rciuitB Cicurit CLGEEN DO—RR ad eOly nRW—eRad/rWti eOUCHT IPLOT OPINTN MA SPEENDTI MEE NDITM zE Q_mSUT sHatrdtowsta rtmn staorwtom tosdpwos tompno stpwoo mady_lse lDveDsec Mode19_ Mode20_mo d[e19 m]oed[0] 2edrf_ud adefr_dbude _ff_a oef_of_d bde_ca_fa dfe_cab n_bde_f_ anbd_feb_nb def_a n__bed_b DfFER_AT DERFTB d_elt__v daletv__b det_a deltlb d__tcrf_udt _rh_f dtu_cr_o ntdhr__o Mndeo0_4 iml_els h_dgd _CDGQT_A _CQDTGB_Q_ DCGT_ CTOCHUPIL OT PATH MIANMENUatsNIM ENUPOC1 MSAINM NEPOS 2MAN MINEUMIA NENUMSta_STT1MAI NM NEANI MNEUMSIAN EMNSAINM MNEUFAMN MINUhttp://www.51wendang.com/doc/437ec10ed908de0667a81455MIA MENUSAMNI EMNUIANM EU-rIDM AINM EUNSMDAI NMENUSINM ENUMMAINME UNNMEUNMINAMENUintaAIMNM EUNMTAN MIENUAIMNM NEUMMINAME UNM NEMAAI NMNENMAINM NUSMIN MAEUNSNI ENMUMMIA MNNUMATNI MNUMAI MNNEAINM EUIA MENNAMNI MNUE

etpSointMIANIM EUTMAN MINUESIMAINM NUESOMANIMENUnfogiUEMIANME NU1AMN IENUMS_CTTS1M ANIM ENUS_STT1MA NI EMNU_TCT1S RADE/ILN ERIWET3 1W 6 RR O 6OR 81RO 47R 10 RW W9 RW1 1RW 14RW 1 3 WR 51 W R7 W R RW 2http://www.51wendang.com/doc/437ec10ed908de0667a814550 1RO21 R 4O21 6 23 1 363 1 523 67 3 4 5 22 3 30 1112 88 227 215 428 12 8 92R ROORO RO RO RO ROR OR W RWRO O RRO OR O RORRO RO RWR WR W W RRORW RW WR R RO CCN TWABLENA E MStauts iDspla TybleaMNaitenannceDis lapyT albesPOS 1ainMtnanee DicspaylTables OCCDECFMOCCS 2Miatnenncae DipsaylT ablseLSCtats DiuspalyT bleas_TKS1 CoTnigufraion tTalbsefnigrauion tTalbseBRODSoCfignrutiao TanlbeCSnofiugaritn oTableCnfoiuragiot TnblesaConifuragitonT abelsnfiguoatior TnbleasBSCnfiguoraton Tibleas!tCrIlDXAXQ_ Satuts Dsilpa TyablstSaut DsspialyTa belsMSaiMtnneane ciDplsa yTbleaMintaeannceD silpyaTa lbsantinence DaspliyaT baleSaMinentacenD spily TaabelsDEaMitnenacn eDsplayiT blaestennacn Diepsly TablaeMainteance nDhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ipsal TablyesMaintMeancne isDlap yaTlbsSTreivecC nofgiurtiao TnbaleSNerice Cvofngiuraiotn Talesbttas DuispalyTabl satus tisDlpya aTlebMantenianecDisp lya TalbeMTainentnca Diseply TabalseDEFROMainMtenanc eDislay pabTesanteiannec iDplays ableTMaiMnentace niDpsaylT bleasRMianetnnae ciDslap yablTseDEMSepotni tCnofiurgatin TobaleeSpotint Confiugartoni aTlesbSeTpotitnCo fignurtaion ablTesSStpoientCo figuration nTbaeslStaTtsu Dspiay TablelsMConSfigratuoinT blesaUSE SRrevie cCnfogiurtiano aTlesbSE Satts DuiplasyT abel_CTST1 Satust isplDa yTalbseQCK-STT1Sta tu Dsislay Tpabls_TSe1

T

[此处图片未下载成功]

APENDIP X— TOUACH ILPT O DISPLAY TALBSE(con )tTUOH CIPLT ODSCEIPTRINO DG CoToing SloelnodiCircu t A Ciicrut i BiCcrui C tiscDhage GarsTe pm Criuci tA http://www.51wendang.com/doc/437ec10ed908de0667a81455CicrituB irCcit C uDsicahgr Presesru Cercuit A iiCrcut Bi Cicriu C tDfifreenial tWtar TemepDisc arhge A aG LsimitD icshrag Ae Tme Apveagre DishacgerA T empRa t eDishcrgae GaBsL iitmD siharcg B Tempe Avraeg Dieschare Bg Tmp Rate Dieschagr eC aG Lsiim DitchsargeC Tme ApvrageeDisc hare Cg eTm Rpte Daishacgr SuepehrateA D icsargeh upeSheat r DBsciharg Sepuereat ChDLY 3 -oCler Puop m1(d as)y LD 4 Y-C oloer Pmpu2 (day s)DL Y5- Cndeoners uPpm1 (da ys D)YL 6- oCndneers Pmu p2 (days)DL Y7- atWr Fietelr (ads) yDY L8 -pC AilO Filetr da(y)s LDY 9 C-pB Oi Fllteir d(ay) sLYD10 - pCC Oil iFlert da(sy )cEoonmierzA Sepst uNb mEcnomoierz SBtes NupbmEc nomoizreC SetspN um EbcnomizeorP ositio AnEconom zier osPtioni EBcoonimze roPsitionC cEnomizeroSH S teoinptA E ocnomizr eH Setpoint S Ac

SiH Stpoine BtE cnomizor SH eetpSiont BcEnooizer Sm SetpoHntiC E coonmzierSH Steopnit CE oncmizore SuperehtaA Eocnomzer iSperheuta BEc nomoierzS uprheeahttp://www.51wendang.com/doc/437ec10ed908de0667a81455tC cEnooizmerEXV Pso Cicurit CArcuii t CircuiB tCLE GNEDR O—R ae OdlynRW— eRd/Writea TUCO HILOTPPO INTNAME GSCAOLO GASAOOCBLGA SCOLC ODTG_ ADG_T DGTB_ DCPA _PD_B DP_Cdiff_ w tdstilm_ adtsm_a_sd t_m_arsd lit_bms td__b mds_mt_b srdlti_cm sdtm_c_sd _tmrc D_S_AHD HSB _SHDC_cpump _1 mpumpc2_ hmpup1mm hpu_m2_pm wilfe_tmo flia_m oftlit_m boilfct_mec ocnf_ aec_oncfb ce_ocfc EnX_VEC_ EXV_AEC_B EVXE__CCec hss_p ase_sh_pa eshc_sb peh_ssp_ ebshcsp_ces hsp_c_ ceo_has ceo_shbeco sh_ c_EQOCA Q_E_CO_B QE_COC_T OCU HIPLT POAHT AMI MENU_DC MIN MEANUM_ANIME N_C MDAI MNEN_AA MAIN NMNUESt_MAIN EMNUSt_ACNMAIN MENU_ MIN MANEU_N AAMNIM EUNS_N MAIN MNEMCIANMEN U_PILMITMA N MENUI-ILMIT MINAM EUNMaint\PRL_MIT MAIN IMEU_IMT AIN MMEUNMa_LIMMAIN IMEU_LIMI TMAN IEMNU_PILIM MTIhttp://www.51wendang.com/doc/437ec10ed908de0667a81455NA EMU-RILMIT MAIN MEU_IIT MAMINM EN_VCTLR MIN MEAN_XCRTL AMINM EUN_CVRL MTAIN EMUNTMIANME UNMMAN IEMNNAIMNMENTAMNIME UNMAIN AMENIANME NINME NUIA MENNUServYMA INME NM2IAN MEUMA N IMNU_TR LAMN MENUI_RLTM IAN MNEUMai_XCTL RMAI MENN_ AMNI MNUESeMA INME N_ MLIN AMNE1AIMNM EUN_CTRV MLIN AMNUEServ1 MEAINM NEUMai_TCLRMA NI EMNUM_TR LMIAN MNEU_CTRL VMIN MANE_ST1TM AI MENNU_TS1TMAI NM EN_ST LIN1E8  8 80110 0 133 3 3 1 3 27 5 61 1 9 013 10 1 7 011 11 132 1415 6 171 22 2324 25 2 93 32 271 312 2 53 3 2263 34 0 7 86R EA/ WDITE RORRO R OR RO OROR RO OO Rhttp://www.51wendang.com/doc/437ec10ed908de0667a81455O RRO ORRO R RO ORORO RO OR RORO O RO RR OR ORORO R OO RO RRW RW W RRORO RO O RRWRO WRR ORWRO RO RO W RWRRW C NC ABTE LNMEAS atts Duspliy aTbaesl_ Satts uisDlapy aTlbs_tStua sDsilpy Tablas_e SDttaus isDply aTaleb_A NtatSu DsipsalyT ablesCI_A StaNtusD siplya aTles_NASt autsDi playsT bals_ NtaSut Displsa yaTbes_BAN SttausD iplsy aTalbe_A MaNintnencea Diplsa yabTlseLinenatcn eDispay TallbseP-LRIMT IaMitneanne cDspial Tayleb_sILIM MTaitneancenD silpa TyabeslP-LRIIM TaintMneacenDispla yTa lbs_LIIT MaMnientanec Diplay Tsabel_IMT ainMentnaecD iplay sableTs_PLIMI MainTetannc eDislap yTbales_PILIMT ManteiancenDi psaly ablTsePR_LMaintnaecen isplay TaDleb_LIMITR Miatennnace iDslpya aTlbes_TCRL ainMetance Dnislpay Talbs_L MRaitnenanecDi spayl Talbs_RTLM iantennca eiDslap Tablysantein

isplayD Tbalehttp://www.51wendang.com/doc/437ec10ed908de0667a81455TaiMtennnae Dcsplai TabyleaMitenanne ciDplsay aTlbsintanaenc eisplaD Taylebintanaece Dnsipal yTalbseSniteancneDi plsyaTableMaintenTacne iDplsya abTlseServicS CenfogiuraitonT blaeS2reivecC ofniugartin oTblasSOreivec onfiguraCtio nTalesY Miantnaecn eDsilapyTabl e_RTL aMntienncae isDpay Talleb_CTLRM anteinacn Deispay lTbaes_XTRL MaCitnnanee cisDplya aTleb_ LSevrce iCofigurantio TnbaleCMaitennacn eisplDy aTabels_CTL ReSvirceConf guirtiao nTblasM1inteanacn Deislpy Tableas_RLSer vie CconfguiraitnoTabl e1aiMnteannceD silpyaTab es_RTLM antineacne Diplas Tyables_CTRVLM ianetnacneDisplay Ta lbs_TRL StatuC sispDly aaTbes_TT1SStat u Displas Taybes_lTTS1 Sttaus Dspliy aabTesl_TKST

[此处图片未下载成功]

PPEANDIXA—TO CU HPIOT  DLIPLASYTABL S http://www.51wendang.com/doc/437ec10ed908de0667a81455Econt()OUCH TIPLT DOESCRITIPNOEco nmizeor Gs TamepCir uic t AiCruic B CtiructiC conomizerEPressur eC icrut iACi cuit Br Crcuii C EtSH tCl Orvrerid Elee Scage tOA TTrhshoeld lectric HeEa tcAtve ilectEircal oxB ItenlrockElec tiral ceat HtSge aleEcrictalHea StatgesElec triac lPullodwn iTm eEelctriacl Puldolnw?Ele mentEm rgence Syto EpMMN CP2 BRaod ErnegryM aagnment eMdoue lnEterng ilFud iCotrol nEsitmaetd FreeCoo loPewr xEhacgenr rFsot actorF Cicurti CiAcrui tB Extenra lTmpeertuareE V A XMxaimu mStepsNum bE XV AuSperhetaSe ptint oEVXB axMimm Stups Numbe XVEB Su erheat Sptpoeni EXtV oaBr CidcruitA EXV oaBdrC ircit BuEX V Bora Cdicriu C EXt VC aMximmu Stpe sumb ENVX CupSrehae Setpoitn tXV MOPE Septoni EXVt verOide Cirructi AEX OvVrerdi eCicuri At XE OvVerrid Cireucti EXB VOverrdie iCcuitrB XEVO veridr Ceiruit cC XEV Oervider ircuitCC E V PosXitio Cnriuitc EXAVPositio Cincruit BE X VPsioton CiricuitC XE VositioP nirCuit cA ircuCit BC iruihttp://www.51wendang.com/doc/437ec10ed908de0667a81455tcC EX PVoitisonCi rcutiA C icuit B CirrciutC ELGNE RO D R—ea Odly RnW— eadRW/itre TOCH PUIOLT OPNI NTMEAECO_TP _A EOC_PT_BECO _TPC_EC NOP_A _EONCP_B _ECO_N_CP oerv_hs eeshth _Mde_15 oELE_COB EHSX_TEP Shses_el es_phulleh pslul EldeentmE MSOPTEM _NMRP Cem_nmcrpewt_o tpfc_ pw frrso_a tfortsb _OT eAvxama_ xsh_psa _xevb_amxs _hs_b EXpVB_DR 1XV_BRD2EE VX_BDR exvc3_mxa shs_pc_m p_so pcoe_c_o avo_xv_e oc_aecob o_vexv_b_ co_ceo_ oc_exv_vcE VXA_EX V_BEXV_C Q_ XVE A_QEXV BQ_EVC EXV_A EXXVB _EVX_ CTOUH CPILTO APT HAMI NENUM_AN AIM NENMU_BANMA I NMNU_N MAINAM NUE_ANIM IA NENMMAIN_MENU Stats_ANCMA N MENIMAI NENMgMAINME UNMEUNStaEAMN IMNUMAINEM EUNYAMN MENUICoN EMUMFIAN MNEU-AMN IEMNUSAINM EMUNM_IAN MNE://www.51wendang.com/doc/437ec10ed908de0667a81455vciAMNIM ENUSM1IAN MEUNOAMNIM NEUMAIN MMEUNMaTAINM ENM

MOANI MEUC AMNI EMNYAIN MENMMAINI MENUMa_ MNINA MNU_PD NMANIMEN UMain_P NAINM EMUNMINA MEN1MINA MEU1AIMN ENUM_RT MALN IENM_VCRT LAIM MENUN_VCRL MTINAME U_XTCRL MANI ENMUMa_LRMA I NMEUNMa_CVRTL AINM MNE_CTVLR AIM MENNUMai_VTCR MAILNME NUMai_CTR LMIANM NE_KSTT1 AMI NMEU_STT 1MAIN MNE_TSTC1M IA MENNU_ NMINAME U_ARN MIN AENUM_ANILINE 11 1 1115 5 5 2 324 6 161 1 91 366 2 8 32 4917  5 52 19 03 8 9 11 19 102 3 0 11 25 12 88 23 1 35622 2 1963 4 5 5 15115 R EAD/WIRETR ROORO RO OR R RO ORhttp://www.51wendang.com/doc/437ec10ed908de0667a81455WR OROR OW RW RR ORORO RO RW R WROR O ORRO WR R RWW W RRO RO R OWRRW RW R O R RO OORRO OR O RR OO RWR R RWW R RO ROO CC TNABL NEMA EtStas Dusilpa Taylbse_CAN tatSs Duislay Tpblas_CNA tSatsuDi slpya TalebsC_N StaAustDisp ay lTalebs_A StatusN Dsplay TabilesCI_St tau Dsspilay aTbls_AC NMaitnenncea iDslayp aTlesConfiCgruaiton TbaesStaltus Dipsay TableslSMtatu sDislpay abTeslEStatus iDplay TaslbseSSNerivce onfCgiuatrinoTa belnofiugatirn ToblaesMRintanence Diaplsy aTbaleTConfguiraiton Tblea!CstlIDrXA_QXS atus Dtspial TaylesMantenaicn Deiplsya aTblesB_ SerNvcieCo nfguirtaoi nTbalesFSrveie CcofniugrtioanTa besStaltus DspilyaTab elntennca eDislapy TbalseDManienante cDispalyTa lebSTatutsD splaiy TabelsTSevirceC ofngiuratio Tablesn2Serivce CofinguraiotnTab lsehttp://www.51wendang.com/doc/437ec10ed908de0667a81455SESer1ive Concifuratigo nTableServ2ie ConfigcurtainoT blaeE aMnitnaecne Diplsy aTabelMai_tneanne cDiplaysT baels_P MNinteanace nisDlpy TabaelsBOAR_PN erSvie coCnigurfaiont TalesbFARServi ec onCifuratigo nTables1erSivceC onfgiruaitnoT blesaE aMnietnanecD isplayTab ls_RTL ainMtnencea iDpsaylTabl s_CTER LMiatnennac eiDplay TsablseEX_TCL RaiMnetancne Dislpa yabTls_TRLC ainMteannecD silap TaylesbE_CTXRLMa nitenanceD ispay labTes_CVTLR aMnteninae Dcsiplya Tbaes_CVRL MaTitenance nDsilap TybaelsE_CXTRLM iatenancn Diesply Tabael_CTLRStatu sispDla Tyabes_TKST1S ttuas DipsaylTable_CSTT St1ats Dusiply TaalebsQCK_ST1St atsuDi psaylTa blseC_AAN Statu DsspilyaT blae_N taSts Duiplas yTbles_

N

AP

[此处图片未下载成功]

PNDIX EA— TUCO HIPOT LD IPSLYAT ALBS E(oct)nTUOCH PLIOTD SERCIPION ETXVPosi tin http://www.51wendang.com/doc/437ec10ed908de0667a81455oiCrciu tA irCcui t BirCcuti CFa ctroy PasswordF an# 1H urosC riuit cA Criuit c BCriuitc C Fan#1 oursH ircCitu ACir cuti CBicriut FCn a2 H#uos rCicurt iACircuit B Ciruci Ct aFn# 2Hurs oiCrcit u CAricutiB C icrit u FCn a3#ouHs CirrucitA iCcuri B tirCucti CaFn 3#Huro sCirucitA Cricui BtCircuit C Fan# 4oHusr iCrcut i ACirciut BCi rucitC Fa#4 nouHs Crricut iAC iructiB C ricut C Fia#5 nHorusC ricui t ACriciu tB Cicruit CF n#a5Ho urs irCuit A CircuctiB C rciit u CFa n#6 HurosCi crui A tiCcrituB C rcuiti CF n#6 Haurs Circuoi A Citruit B cirCcuti CLE EGD RO—N eaR Ondl RW y—R aed/Wite TrOUC HILOTP OPNTI NME EXA_AVE X_BV XVEC fac__aspsh _frnaa1hr_fan 1b r_fanch1hr_fan 1a hr_afn1 hrb_afn1c hr_afan2hr_fan b 2hrf_na2 hrcf_naa2 h_rfanb h2_rfacn2 h_rfna3a h_rfnb3ahr fanc_3hr _fnaa hr_3anbf3h _fanr3 hc_fanar h4rf_anb4 rh_fanc4 hrfa_a4n rhf_an4b h_rfacn 4r_fanah hr_5afn5 hb_rfnc5a rhfa_na 5h_ranbf5 hr_facn h5rf_an6 ahrfa_b6n rhf_nca 6hrfan_6 ar_hfnhttp://www.51wendang.com/doc/437ec10ed908de0667a81455a6 hrbfa_nc6T OCUH PIOL TATP MHAN IMENUME NM NUIN EMUNIME NAMN IENMMIANM NUESMIN AMNUEN IMNUI NMNUEIANM NEHAINM MNEUSMNAN MEIUIN MNEUSMSIA NENUMAMI MENNSMAN IMNUESerMNAN IEMNUSeMHAI NMNEMANNIMENU SSMIA NMENMAINUME NUSUMIA MENNUSeAMIN MENMNINAME UNMINAM NUESMAONI MNUEMIN MEAURMIANM EUNFMANI ENMAIN MENMFMIN MEAUAIMN EMUNAIN MMNEOAINM ENU://www.51wendang.com/doc/437ec10ed908de0667a81455ePDRHFNAM AN MEIUMIA MNNEUMNAIN ENMAN IEMNUNIME UNStSILN E0230 4019 818 2 8 1552 5 9 1 9296 1 6 26 10 2 03 70 71 72 11 2 113 8812 8 12 2 32 291 92 913 3 33 1022 03 0RAE/DWR TE IR RO ORO RWR W R WW RR OR RO OW RWR R RWORO RO RW RW RW ROR OR O RW RW WR O RR RO OWR W RW RORRO RO RW W RWR ORRO R CCN OTBALE NME SAtatusD sipaly TbaeslLSatuts DspilayT abelsOStaust Dipsal Tyblasec eonfCguiraitonT albseFAYSevicr eonfCiugariot nabTeslUPDHRFAerSviceC onifgrutaoniT abeslASreicevC nfiogratuionT ableSFattsuDis lpa TaybleSRattsuD iplsa TybalseSSatutsD isply aTalbeNeSrivecC nfiogratiun ToablseUPASrveice oCfignruatoin abTlesUeSricv Coefnigrutiaon Tblesattus ispDlay TabesStatu Dispsayl TbalesSUatut siDslayp ableTsrvicehttp://www.51wendang.com/doc/437ec10ed908de0667a81455eCo fingruaito nTalesbUice vonfiCugatrinoT albesSrveci Coneigfratuoni aTblsSNttau Disslpay TbalseStSaut DssilpayT baelsFANHOtSaus tisDlpyaTa lbesce Coiniguratifo TnblasevirecConf giruaitonT blasFSrevice Cofigunatrio naTlbesUtaus DtispaylT balsSatus tiDpsal TyabelSatuts DipslayTabl serSivec oCfnigrutian TableoFSrviceeC nfio

TalbesUPASrvicee Cofngiruatoi nTblaseStaAustD splia yaTblesFAD silaypTablestSatsuDis lapyTa leseSrviec oCfnigruaiotnTabl eseSvirce Cofinurgtain ToalesbeSrviecCo nfgiruaion tTalbeNSattsu ispDly TaableStRatusDis plyaTa bleSatus tispDaylTa leb

[此处图片未下载成功]

PPENDIX A T—OCUH PIOL  DTIPSALY TALEB S(oct)TnOUH CILOT PESCDRPIITN http://www.51wendang.com/doc/437ec10ed908de0667a81455FOan# 7Ho rus Ciruct Ai Cicriu BtCi ructiC F a#n 7Huro Circsiut CArciitu BCrcuit CiFan 8#H uosr iCcruitA C rciuitB Circit u FCa n#8H uosrC icuitrA Criucit BCricituC Fn a#9Ho urs Crcuiti A iCcuritB C icuit r CanF#9 ouHs Crirucit A iCructi B ircuCi t CFa#1n 0Huros iCcuir t CircuAtiB C rcuii CtFan# 1 0HuorsC rciuti A irCcuit CiBruitcC Fa nC cye Coultner iCrciu At iCcruitB CrciutiC Fn aOupttu OD# 1C ircui t CAiructiB Ci curi tC aFn Otpuut OD 2#irCcui A tirCciu t BiCcurtiC anF Ouptut DO# 3Circ uti ACirc itu CiBcrut CiFan O tpuu Dt#O 4Crcuii A Circutt i CiBruict CLGEED RO N— eRdaOn y RW l— ead/Rrite WTOUH CILPT POONTIN AEMhr fan_a7 r_hanfb7h _frac7nhr fan_a 7hr_afnb 7hr_afn7 chrf_aan8h r_anbf h8_frnca 8h_ranfa8h _fran8 bh_fanc8rhr _ana9 hfr_fab9nhr_ fan9c h_rafan9 h_farnb9 r_fanch h9fran1a0hr afb1n0 hfrnac01 rhfna10 ahrfan1b0 rfanhc1 0fnayc_ac ancyfc_b afcync_c fana1_ fn_a1 fbn_a1 fac_n2af anb2 _fn_ca f2an_3 faan_3bf a_cn 3af_na fa4nb_ f4ahttp://www.51wendang.com/doc/437ec10ed908de0667a81455_n4 TcUOHC ILOT PATPHM IN MANEAINM MEUNSI NMEUNSRAINM ENMUStMARNI MNUM ENUStIN AMNUNMIA NMNEUMFANI MNEAINMME NURAIM MNNUMAIN ENUSMIAN MNUESNMAIN MEUNServiAAIN MMENUMINA EMNMAIU NENUMSMHAI MNNEUSMAINS ENUNI EMUNSMAINMENMAFI NMENSMINA EMUSMAINMENU SttasSAMINM NUEMaINA EMUNMMARNI MNUEMMAINTMEN USM_AN MINUES_C MAID MENUNSta_DCMA IN MNUESt_DA MINAM EN_BD MIA NMEUMAI_N MEUN_ MDINAME N_DB AMNI MENUStat://www.51wendang.com/doc/437ec10ed908de0667a81455uCRC_ DMIAN MNUESt_D MAINAM NUES_DBM IAN ENM_CDL INE14 42 43 11 1 31 2512 55312 2 23 16 226 6 31 23333 1 7 7 23714 24 43 3 7 111 11 11 1 21 21 2 113 3 13 14 14114 RE A/ DWITERRW RW WRRO R OO RRWRW WR O RROR O WR RW RW R ROOR RW RW ORWR OR OOR R ORO R OOR OR R ROOR O R OR OR ROORO RO RO CNC TABELNA E SeMvice ronCigufartoni TblesSFreicevCo fingruatoni abTeslervSce Coinigfratiuno Talbettau Displsa yTbaleSSttuasD islap TybaeslFANaust ispDly aTbalesSeRvicre onfCguiraitonTab leseSrvce Confiigrutiano TableServiec o

aTblseUNtaSutsDi slapy aTbelRSatts uiDsplya Tblasetatus DiSslpya TalbesFANvirc Ceofingruaion TtbaeslUPrveiceConf guraiiton TalbesUSNevicreCon fguiartion aTlebsStaNtus Dislay paTlbeSRtaus DitspaylT bleasSUtaus Ditpsayhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 TalbelServiceRCo figuratnio nTblaesSAevrie ConfigcuratoinT ableervSce Conifgirutaino TblaesNSatustDi psaly ableTtau siDspal TablesyFANHOSSatus tisDlaypTab leSaiMntnance DiselaypT alesCMintanancee Dispaly TblesLMinateannc eiDspal yTablsSRttus Diaspay lableT_D SCatustD ispaylTable_D BtatusS isDlpay aTblse_ SDattu sDislpay ableT_DA taStsu iDslpay abTel_DSta ut sDsplayiT blase_S taus Dtislap TybleasC_AD Satuts iDpslayT abls_tatSus Dipslya ablTseC_ Status DDislpa Taylbe_ DtStua sDspiayl ablTseC_DB tStus aispDayl Tblas_D79

[此处图片未下载成功]

ENPDX A I—T OCU PILOT H DISPLY ATBLESA(c ot)nTUCO PILOHT DSCEIRTPINOF naO ututpD#5 COriuict AC riciutB iCruci CtF a nuOptu DOt 6# Cicuri tACircu tiB C ricituC F n auOtputD O#7 Cir uct iA iCructiB Circ itu FCn aOtphttp://www.51wendang.com/doc/437ec10ed908de0667a81455uut OD# 8iCcurit AiCrcut iBC rcuit iCF anSe qunece tSrated?CrciituA C rcuitiB aF nStagseCi crit Au irCuic tB Crciiut Fan StCagni gNmbureC icurtiA Cir cituB Ci curi Ct Fn Saagintg Nmber CiruucitA C rcuit i CBicrut iCFlo wCh ceekdi f C ump PfOf Fee Corlo ABa llVa lev reF Coeo A EXlVP oisiot Fnre eCoolB BllaV lvea reF eool B CEX PosVtiionFree oClo CndotiionsOK? Fer Ceoo Pulm pAH ousrF re eooCl Pmup BHour Fsee Coor lRqeeus? Fret eCooilgnA PupmHour Frsee oCling Actiove reFe ooCilgnA ticevC icruti AC rciiu tBCi curt iCF er eColino gB Pup mHuorsFree Co oilgnD sibaleFre eoClino Dgiasbl Sw Free Coeoinlg isDaleb? reeFC oolni Heatge rrFee Cooilgn OA TLiimt rFe CoeolignS elct eLGENE RO D—Re ad Only WR— ead/WRrteiT OUH PCLIO PTOITNNA M Efa_na5 anfb_5f n_a5cf a_an fa6nb6 fan__c 6an_af 7fa_nb7fa _nc fa7_na fan7_b 7afnc_7def fa_a de_ffa__ bQFA__A NQ_FAN_ B_QFNA_ FACN_TS_ FAN_SA_T FBNA_ST_ FANC_S_A TAN_SF_TBFA _SNT_Cp mupl_c Qo_FCBVL_AQ _FCXEV Q_AFBChttp://www.51wendang.com/doc/437ec10ed908de0667a81455LVB Q__CFEXVB f_recad yrh_fmc_ah r_fm_c bfcr_qes thrfcp_a_ Mod_1e3 FC_ON_AFC ON__BF _CO_CNh _frcp_b FC_SBDL EFC_SW F_DSCBELQ F_CH_R fTreeo_t fraeecoloTOU H PICLOT APH MAITNMENU S_ADMA I MENU_MAI N MNUEStatus\CIRCCD M_IAN ENUMS_RDMA NI ENU_ DMAIN MNUE_D MIAI MNNE_DM AN IEMN_BD AMNIME N_DM ANIM NEU_D MAAINM NE_CD AMN MEIN_ MADNI MEUMAIN TENUMMAMN IMEUNSta-TSKT 1AIMN EMU_CSTT1 MAI NEMN_ST1T MAN IENUM_A MDANI ENMU_ AMN MEIUN_CDM AI MENNMAOI NMENUSNM NUESAN MINEAN IMEN_TQT2 MASN MIEUN_aSTT M2IN AMNE_TSCT2M IAN MNE_2 MTIANME UNI EMNUStatuANI MEU://www.51wendang.com/doc/437ec10ed908de0667a81455FHOUNRSM IN AEMUMAINME UNAAMI MENNOAMN MEINUSAMNI ENMUStatuNI ENMUMOIANM NEUSMNAINM EUIAMI NMEUNAMIN ENUMMOIAN ENMU_CST2 MAIN METUNCoMRIAN EMNNEI 1 15515 16 61 6 171 17 1 17 71 177 7249 0 111 9 19 19113 2 3331 18 1761 91 7 8 1 29 4 1 1242 223 5 216 2 513 3 11 ERD/A RITW EO ROR RO ORR OR RO OR ROOR OOR R OO RRORW R WRWRO R OORR RO ORO W RORRO RO RO R ORO R O R RW OO RRO R OOR R RWW O RRORO WR RWC C NTBAE LNMAE Staus tDispaylT albesCI_DASta tu Disspay lTbale_DS ttau sisDlap yTable_ DSatut Dssiplay Tabes_CD tSatusDis payl ablTs_BD tatuS sispDayl Tbael_ StDtau DsspiaylTa leb_D SAttausD iplaysT ables_DBStat su ispDal Tyablse_ DtStus aDiplasy TalbesCIR_D CtatusSDi plsy aaTles_D tSauthttp://www.51wendang.com/doc/437ec10ed908de0667a81455 DisslapyTa ble_C DaiMtennnce aiDplsa yTblaeMMiatennnace Dsplay TialbsetsuD iplas Tyaleb_TKTS 1tStusaDi slpay Tblae_KSTT1 Sttas Diupsay Tlalbe_ST1 TtaSts Duipsay Tlabes_D ASatts uiDspal Tayles_ DSatus tDipsla yaTbel_D CtSaust Dislayp aTblesFRESatust Dislpya aTbesSttasu DsplaiyTab elConfiguLarion TtblaestatusS DsiplyaTa lesb_TS2 StaTtusDi pslyaT blea_T2 SStaustDis laypT abelsQ_ST2 StTtuas Dspiay Tables_KTS2TStatus iDplsy aaTblsLSatut Dsipsla yablTses Diplasy TalbseFARtatSus iDsplya aTblseFRLSrevci eoCnigurationfT blaeStNtas Diuplsa yablesSEtatsu ispDlay aTblseutsDi pslyaT baelsSatut Dssipla yTablsSrveice CofinuragitnoT abelatsuDi psly TablaeSTattsuDispl ay abTeslSTATStGtausDispl y aaTbleattus Dislphttp://www.51wendang.com/doc/437ec10ed908de0667a81455yaT alebsQ_T2 CSnoigufatrin oTalbseUSeEvicre oCfignuraitno abTel

[此处图片未下载成功]

PAPENDX I A T—OUC PHLIO T IDPSAYLTAB LES(c nto)TOUC HPLOTI DESRCPITIONFrost nIegratot Garn Ciriciu tA Circit uB eaHd rPss epeeS dircCitu ACir cit Bu iCcuitr HECAT RCELAIMC IRUICT AHET RACEAIM LCIRUIT B CHaetR ecaim leSeltcHe at eclaRi mSlecet eatH/ool CSeect Hlea/toCl oSatust eHaitg Cnahngoeerv Sept Heating toLwE TWL ocout Hekaitgn OT AhTesholr Hdateni gRmap oLdingaHea tni Rgsee tegD. VlaueH aetig Rneste elSec tHatein gSeptonit 1H aeting eStoinp t2H ghi DT CGrcuitiA HihgD GT Crcuit BiH gh iGTDC ricituC Hi hg Pesr OevrirdeCi rA HghiP ersO ervidr eCi B Hrih Prge sOverrdeiCir  HCih Pgressreu hrTsheodl Hih giTesr iDslpaySe el coHlidy auDraion t(ays) dolidaH Sytar Dat Hoyildy Satra Motnht ot HGs Bapasys Sleect Haed Pres scAtutoa rPo siCruict A Cicuir BtCi cuirtC H eate Brlla alVevC irciu t CAicrut Bi iCcuit CrH toGahttp://www.51wendang.com/doc/437ec10ed908de0667a81455s By assp Otpuut Circit uA iCc

C riuci Ct HotGas BypassC ircut iA CrciiutB Ci ruct C iPHupm1 Ctl Dlae yd(asy) PuHm p C2lt elDy a(ayd)s RHCo densernH atere ceI Dnoe StorgaeSwit c hcIe Mdo Enabee Icl Medo en Eiffct LeEGND REO— Read On ylR W—eaR/Wditre OUTHCP IOL POTNTIN MA fr_inEta fr_int__b Q_FVNAA Q_VFNA Q_VFANCB—— ECL_SREL REC_SLETH CS_ELHEAT COL hauOo_tspMo ed16_he ta_h trhamps_ pr_hed gh_res hsl1 phps 2Mode_42 ode_M2 M5doe_26M oed_72M ode_28Mo ed_92h _th hipghdsip HL-LENOHO L-AY DHOLM-ON hbgp_sel hd_po_as h_dop_sbh _pdo_sc _BQL_A Q_BVLVB Q__BL_C VGBH_PAHGB _B HPGP_B QCHG_P_B AQ_HBP_B G_HQBPGC hp_mp1u_c phmup_c Q2C__HD TCEISW _ie_cnfg Mcod_1e T8UCO HPLITOP AT MAINHME UNMMANI ENMUAN IEMU_T 1MANIM NE_TS1 MAINME UNSta_TS1TMA I NMEUNIMIN AEMUCAMNIMENU tStusaREMIINA MNUMTIA MENNUNUESthttp://www.51wendang.com/doc/437ec10ed908de0667a81455aMIINA EMNUSIMAI MNNEUMAEN IMNEANI ENMNAIN MENMTAMN IENMUAMNI EMUNMATI MNNEUMTINAMENMIA NENMMADNIM ENAN IMENMAIN ENMUANI MNEUSMAIS MENUNM1INAM ENUCAMI MNNEU_1 M0IANME UN_0O1M AI MENUN_Y1 0AIM NMNEMAN MIEN_N AAMNI ENMUSM_AIN MENU_NA MINA MNEU_TQS1TM AN MEIUNSta_TSuT 1AIN MMENUS_CTT1S AIN MENU_DIA MENU_B DMIANME UNStat_ MIA NMNE_TST1 CMIN AMEN_CTT1S MIAN MNUE_T1 MAIS MENNAIMNMENUviceANI ENU_ MA2N MEIUN://www.51wendang.com/doc/437ec10ed908de0667a81455AEGENT AIMN MEUNMAUN IENMDILNE1 4 3 12 13 11 9 41 9 1119  830 7 13 226 2 520 1718 25 2 267 8 292 3 10 61 38 2 11 41 1661 19 6263 3 99 9 0 27234 7 812 11 42 1 9READ/WITE ROR R ORW W RW RR ROO O RR RW WROR WO RWRR W R WRW R WRW O RROR O OR R RO ROW RW W RW RW RW RRORO RO RW R RWW ORRO R ORW R WW RR RWWRW R RO RWOCC TNABE LAMN EaiMntnaneecD islpy aTbaesanteinnce DaiplsyaTabl ettuasDis pal yabTle_1 TSttausD ispayl TbaeslQCK_1tStusaDi slpyaT baesl_ST 1tSaus tDspilayT blesaSLatuts isDpal TyblesaRtStusa DipslyaT albesRSattus iDspay TlablsStatusDis lpya TbleasGETSattu DisplsayT blesteopnt iCnofguiatron TiabelsSETPItStas uiDplsy Tabaesonfiguatior TanblesEetpSinto CnfogirutioanTabl setpSion tConfguritaionT albesCnfogirautionT baelseptoni Ctonifugariot TnabeslSetpoOit Confihttp://www.51wendang.com/doc/437ec10ed908de0667a81455guratnon TabilesSETPOIttus Disaply aTbaelsMOSSattsu isplDyaTab lseMODStatusS isDlpayTa lebStatus SDspial yTblaeStauts ispDaly TbaeslMODtSa

spliayTab lesMrvieceC nfoigurtaino TbleaSe1vicer Confguiraton TialesRCnfoiguatron iaTlbesH_Y0 1oCnifgurtiano aTlebs_0Y1 onfigCrautio TablensHO_10 SericveCo nfiurgtaon TibaleRStatus DipslyaTa leb_N SAtats DusiplayTable_ANS atuts Dipsly aTblesa_AN SCttusa iDpslya abTels_TCTS1 tStus DiapslayTa lebsQC-KTS1T taSts Disulpay TablesQ_KSTT1St tua Displsa yabTel_DC taSustD ispal yTabels_DBS ttasuDispl ay abTel_D Satut DisplaysTab ls_ST S1tatusD iplsyaTa blse_TS1 tatus DSisplya abTes_STT1S reicveC ofniguatiron ablTserviSce onCfiurgtiaon TblesaMSFatts uiDpsal Tabyle_STT2 SttuasDis pla Tyabesonifgrutiaonhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 aTlbeRStaustDi spaylTa belS99

[此处图片未下载成功]

APEPDNXI A—TO CHU PILO  DISPLTYAT ABELS( cno)tOTUC PHIOT LDESRICTIONPI ntPID G ia nVrifaa Lng aCapaity Lcmii Valut eLg ainiMmu Rmuninn gimT Lega tSartD lea yLg atSatrTi em rLgaU in tPupm oCtnol Lranguae gelecSton Liea Lagd SelcetLead P ulldwno TimeL ae dulPldwo?nL eadU in its teh:L aedL/a dhCaneovger?eaLd/aLg alanceB Deta LledaLa/gH uros DetalLimit 4-20A Smigna limLi Switcth1 S attsuL miit witchS2 S attu LoasdU/lnoda Fatocr oLaciton oLw uSciotn iCruit AcLo wSuctio Cnrcuii t LowB uStioncCi criut LowC SuerhpaetC ircuti ALowS ueprheatC riucti BLo wS uerphet Caricuit CL WTOA- TDeltam FAro%0 DeamndLim it A For m00% 1Deamnd Lmit MichiaenO pretiangHo usrMac hin OpeeraingtHou rsMac hne iStrta sMahicenSt rts Numbera MsaterCon rtloT pe MyastreC ntrool TypeMa setrS laevA citve asMtr/Seavl etCrl AcitveMa tes/Srlva eErrro Matsr/Selae Selevt caM xvAaialbl Caeapicty? MHCXExhttp://www.51wendang.com/doc/437ec10ed908de0667a81455c hagne rSelect Metri cDspily onaST UDM inteu Lesf ftor tSatrM oedlNu bemrMu ts TiprA ms Mpsu tTip rApm Msus trTpi mpsA Man eSS CaTculltion CarcuiitA C iructi B oMot rCruerntC iructi CAircitu B iCruit Cc ELGND ERO—eadR Olyn W R—Re d/Wraiet OTCH UPIOT LPONIT NMAE h_dig LAGL_MI aglm_in ils_trtd _slr_ttiml a_pgmp LuNGAAUEGlea dse_ll eadp_u ll_lullp eldasel_ l_lhancgl lbal__ dl_lhr_d LIMA_AL LNI_MS1 WIL_SM2 smWz LcotainoMod e_12 oMed22_Mo d_e23Mod e3_ 0oMde_1 Mode_323f _dcetl lami_e zlim_xm r_mhch HR_aMCA sH_tamchst _amchms _ctrlms_ crl toMe_11 dm_sctaiv m_serrrom s_el cspa_mx mcahx_es lIDSPNITU mn_lefti MdeoNum lcp_mtaa cpb_mtam cpm_mtac msst_mda_ss _tdm_bCU RRN_E CUARRE_NB CURRN_E CTOUC PIHOTL PAH MATNI MEUEMAI MNEUTAMIN EMNUConf_MAI NEMUN_MSAINMM NE_SLV MAN MENU_TSV MLAIN MNUMAFNI ENM_SLVT AMIN MNUE_SSVLMAI NENUMMaint://www.51wendang.com/doc/437ec10ed908de0667a81455M-SMTLV SAMN MIEU_TSSL MAIVN EMU_LVM ANIM EU_LS MVAI NENUM_MTSLV SAIN MMEUNSAMN IMNUEAINM NUMAIN MNEAI NMNEU-I DMIA NMENUStatu\sOMDSE MANI EMNUEMIA NMNEUStaEAMIN ENMUStatusMASN IMEUN

IN ENMUNMEUMAI NEMNEAMI NMNUERMAIN EMUNSINMENOMAN MIEUMRAN MEINUAMN IMNU_SSVLM AINM ENUM-MMSTLV SMAIN MEUNAN MEINU-MMSTLVS MAI MNNU_MMSTLS MVAINME UNC_LSV AMN IMNE_TSLSV MAI NMEUNN IMEUIA MENNIMAI NEMN-M INAM ENU_PN MIN MENUA_DN PMIA NMNEUMaint_RN MAIN PENMUMaMMIA NENM://www.51wendang.com/doc/437ec10ed908de0667a81455MMAI MENUNS_N AMAINMEN_AN MAIN MNU_AN CLINE7 222 0 871 1 2 12 28111 5 1 16 9042 8 9 91 222 3 2243 13233 3 2 28 9 1 5 6 7 2 31 2412  313 51 17 41 2 6 12 01027 88 8 ERA/ WDITRER WR O W RRO R RWWR WW RR WR ROOR OWRRO O ROR R ORO R RO RO OORR OORR ORO R W R RW RWOR W RO WR ORR ROORO R RWO WRR W OR ROR O O RO ROR R RO RO OR CONCTA BE LANE SeMrice Convfiguaritn TobaeslS attu sDspiay laTlbsCofinuragiton Tbleas_SLVS aMitennnca eisplDyaT ableCnofguritianoT ablse_STV ConLfiugariot nTalebsMST_Confiugrtaon TialeboCnigufraton iTblaseMST_Cofignrationu Tblas_TSL VMintaeancneD spliyaT baelsaintMennae Disclap yablesTMaVniteanne cDsilayp TblaeifuratgionTa lbe_SL MVaintnaecn Despial Taybeslatts Duspilay Tabletus Dasilay pTalbseTSatus tDiplsy aabTelaintnanee cDipshttp://www.51wendang.com/doc/437ec10ed908de0667a81455lyaTa bleonfguriaito naTlbe!trlIDPD5_XAXtaStsu iDpsalyT blesattus Dispaly TbaesSOtaustD islpa TyabelStatSus iDspal yTbaesEtSaut sDipsay lablTeSSttasu DislpyaTab leSSttus Daspliay TabesConfguirtionaT ablesURonCifugatrion aTlbesSrvice eoCnigfuraitn oTableRtSaut Dsspliy aablTesSOevice CorfinugationrTabl seUPSRattsu isplayD TbaeslSCoHfnguiatroi Tanlesb_SLS MaiVntneanec isplayD TblesSttaus ispDly Tablaesitennnace Dsplai yaTlbeaMntiennaecDi slpayTa lesoCnigfrationuTa bls_SLV MTanietnace Dnspilay abTesevrcie oCfinuratgoin aTlbseFnofigrautio TnblaeSattusDi psay TlbaelCInofiguationr ableTs!ClrtIDP5_DXXAQ Mantienane cDipsaly aTbelsBOA_ MNanitnaecn Dieplsay Tabes_DPN aMitennanceD islpya TabeslBO_P NaMntenincea DsipaylT bael://www.51wendang.com/doc/437ec10ed908de0667a81455EFROSTsMM intanence Disalay pTalbeSatuts Dislpya abTlseCI_AA SNtats uiDplays aTles_N tatSs uisDlay Tabpls_

[此处图片未下载成功]

PAEPNID X—ATO UH CIPLOT D IPLASYTA BESL(c nto)TOUHCP LITO DSCERITPIN MOtoor eTmepratue riCruit cACirc ituB C icrut C Nexti Sqeunce eAlloewdi nirCcuti ACrcuiti BO ilH etae riCrciut ACriuict B irCcituC OliHe tea ruOput Cirtcit uA Circit B Ciucuir tC OilLev e InpultCi ruct A CiircutiB C ricut i CilO Prseurs Ceriucti AC ircuit CBiruitc

OilP essrue riDffreene Ccicrit u CircuAti BiCcuirtC Oil Sleooni Cidruci AtC iruci t CirBuictC iO SlolnoideOu tuptCi cuirt ACir cit uBCir uictC O pitml FanaCou ntC ricitu ACicuit Br CriuctiC Overidr eSate CticrituA irCcit u PerBcnet Toat lCpacaiytC ircuitA Circ uti CBirucit C Pup Dimfefentira lPress .irCuict AC rciit u CBriuctiC P up mnIlet PrssureeC rciiu AtCi rciutB LGEEDNR O— eadRO lynR W—R ed/ariWt eOUTH PCILO TPONI Nhttp://www.51wendang.com/doc/437ec10ed908de0667a81455TMAECP_ TPM_AC P_TM_B CP_TMPP_Cd efs__a def_see_b _HQ_T Q_ATH_B _QH_T OICL_TH_A IO_HT_B OIL_LTH_C OILL__ AOI_L_B LILO_LC_OP_ OPAB_ OPC_DO P_ AOD_P BOPD_ Q_CILSOA Q_OI_LSB __QILS_CO OL_ILSA_O L_SILB O_IL_S_L fanCcp_ao fncoapb fan_op_cc vor_d_ae veord_b _ACP_A TCAPB_T ACC_TPfc _dp_a f_dc_b pc_dp_f fcci_pn_ ac_ifn_pbT UOCHPILOT PATH MAN IMNUE_AC NMINAM EUNStat_CAN AIM NEMN_N AAINMME NUMINA EMNMINA ENU_T1 SAIM NENU-TSKT1 MANIMENUttausQ_S1TMAIN MNEU_ MIAN MEU_M AN IEMNUS_CDM ANIM NU_A DAIM MENNU_ MADI MENN_D MIANM EUNS_ANM IN MEANUS_ANB MAN IMEU_NA MAI NMEN_A MNAIN EMUNSta_A MAINN EMUNS_N MAANIM NE_1M ANIME N_TTS1M ANIM NUE_CTS1 TMAN MENU_A MAhttp://www.51wendang.com/doc/437ec10ed908de0667a81455DN MENU_ID AMIN ENMUSt_ AMN MINUEMRAMI MENNMIA MENNMIANME UI NEMNUMMAINME UMA_IN MNE_AN MIN MEAUNS_ACN MAI MENUMOIN MAENMAIN ENUMSAIM NMENINAMENLLNIE9 9  29 002 5 221 2 955  75 77 6 66 7 77 1 632 0 636  468 12 8 5 22 2 12 29 39 917 2 RE7DA/RWIE RO RTO R RO ROO RWR RWWR O ORR RO ROO ROR OR OOR O RORR ORWRW R WRO R OR RO RO ROOR OR OR ORO O RRO R RO OR RO OCC TNABLE NMA StatuEs iDplay Tsblea_Satuts isDlpya Tblea_NAS attusD spliya aTles_AC NMiatnenacen Dspily TaalesbDaMntineane DcisplayT balesDMSttusa Dsilap TyabeslQ_TKST1S atutsDis pal yaTlebs_S1 TSttus aDspilayTab es_St aust ispDlyaTa bls_CDSt tas uiDslpayT albe_S attusDi slayp aTbesl://www.51wendang.com/doc/437ec10ed908de0667a81455RCC_D taSuts Dsipaly TblaesCI_AD tSatu Dsspliy aaTbesl_DSta tusDi slpya abTlse_CDSt tua sispDly aabTlseC_AAN Sttas uDspliy TabalesCIR_ACNS attu siDslpya Tbaels_ taSut siDslap Tyalbe_ NtatusSDisp ly aTales_N StAaut siDspalyTabl e_N StAatu Dsisply aTabel_T 1Staust ispDal Tabyel_ST1 TtatSu DsipslyaTab ls_1S tatsu iDpslya abTlse_R SDatut siDslpy aTable_tStuas Dsiplya Tablse_D MiantennaceDis lap yTalebsaiMntenncaeD ispayl aTbelinaetanne DciplsayT ableTMinatnanec DespliyaT baelantienacen iDplsyaTa lbsStaT

slap yTabeslC_AANSta ust ispDay TlbleasCIRCB_NSatus tDislapyT abeslC_Sta ustD iplsyaT albesFStaLtsu isDlpa TyalbesSLattusDi plsay Tabels Diupsayl TbaelsFtatSu sDspily Tables

AP

[此处图片未下载成功]

http://www.51wendang.com/doc/437ec10ed908de0667a81455PEDNIXA— TUOHCP IOLT DIS PLAYTABLES cont)(OTCU PILHO DESTRCPIIOTN uPp Imnle Pterssreu irCuit c ACricut Bi iCrcut iC Pup mOultteP ersurseCi criutA Crcuit Bi Crcuiti C BN aFnson V aifra nCir AB NFns oa nVraifna CirB N FBns ao Varifan nCi CrN extOc cupied DyaNex t OccupideDa NexytO cucped TiimeNext Oc cupeid Tim eNxt Sessioen lAowed lI neNt Uxncoupice daD yNet Unoxcupiec DaydNex t Uncocupide imT Neext UocncpueidTi m eNgit Chontrlo apaciCy tiLmit iNhtg oCtrol End Honur Nihtg oCntrl oSatr Hotu Nigrh towL Nosie cAive tAO BToracadt Bus#s AT BOoardcat sEleentm# OA TF llu eRes tValueO A FulT Rlsete Vale uATON oRset ValueeO A TNo eRst Vaele uLEGNEDRO— eaR dOny lW R—R ed/ariWteT OCHUP LOI PTOIT NAME Nfc_ip_a fcn_ip_bn fc_np_c fi_ouc_a fpc_op_b uf_oup_c cavrfan_a vrfaan_ vabfrnac _XNTOCDYANXTO DACY NTOXCTI MXNOCTTI Mfcne_x tXTNUDAY NNXUNTADYN XUTNIT NXTMUTIN nM_hlmii nh_etn ndh_tasr tMod_e0 9oatubns omtlocad oatcra_f outhra_uf oatcr_onoa ht_nhttp://www.51wendang.com/doc/437ec10ed908de0667a81455roTO CH PIULTO ATH MAIPNM ENAIM MNNEUMANIME UMAIN MECUNAMN MENUISEAMNI EMNUSMAIO MNNUEAMIA NMEUMEUOMAIN MEUNMaP1SOM AN IMEUOS MAI2NM ENCO1P SMIAN ENUSM AN IEMNINAM NEUMaPO1 SAINMMENUaitnOPOS2M IA NENMUMPO1 SMAI MNNUOPS2 MIN MENAUCoRAIMN ENUIN MENUMASN IMNUMAIENM ENUMAI MNNUMAIS MNNETMIA NMNEMANIME NUPAIN MMEUEN 71 2737 18 28 38 657  7 78 8 69 9 01 0 4114 03 90 145 6 20  19 RE5D/ WRITAERO RO RO R OO ROR RW R RW WROR O R ROORO R OROR OR RW ROWRW RO RWhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 R WW RR WR WR WCN TCBLEANAME Sta ustD sipal yabTlseautsD iplasy aTbelOtatSsuD iplaysT ablesFREttua sDsilaypTa bestatSs Displua yTalbseSLttasu iDpsalyT abelSeOrvcei oCfniguaritno abTelYServie coCfnguriaito nabTlsSreive Ccnoifurgatoni aTlebRMinaentanc Diesplay abTesOS Ma1intenacen Diplsy TablaesOCCDOP2SM inaetannecDi psal yTablseOPOC1S MantineanceD ipslya TblaesOPO2SSta ust Dispal yTalebsFOMainentacn Dieslpy TaalbesOCCPOC1SM aitnnance eiDpsla yTabesS 2aintMnaenecD ispaylT blaesOCO1P SMiantnaecen iDspayl abTesS2Co figunartin oablesToCfniugarton TailebsConRigfuratoni aTlebttau Disslay paTleb

ablsCofniurgtaon Tialesbepotnt iCofinugraiot nTalesb://www.51wendang.com/doc/437ec10ed908de0667a81455 etoiptnC noigfrutioanTa blesNSetpion tConfguiatirnoT baleSeTtoipt nConfgiruatio nTabelsS102

[此处图片未下载成功]

PAEPDNX I A—TOU H PCILTO ISPLAYDTA LBES( cnto)OTCUH PLOI TDECSRITIPN OOcupceid rFo mOccpiuedO verire dwiSct Ohccpuie Td oilO Flitre ACtrl days)(Oi lilter FB Ctr (ldas) yiO lilFetrC Ctrl( aysd On/)Of f R-emot Switec hPO ARWN - R1erfigraen Charge tO WPARN 2-Wat er oopLSiz Oeepraitg Tnpey pOiotalnSpace tmepP sa forsA llU sreC noig fPecrent oTalt CpacatiyPe irod# DWO( TWTMFSHS )Pnch oiffste crciuitA Pi cn hoffstecircuit  PiBnch offstec riuit CcP owe Dronw1: day-mo -near Poywe rownD1:ohu-rmnute iowPerDo w 2:n da-monyye-ar oPwe Dronw2: ohru-mnite PuoewrD wno:3 ad-yomn-yareP weo Dorw n: h3oru-mnuti PoeerwDow n 4 da:y-om-neya Prweor oDn 4w:ourhminu-e Powte Dron 5w:ad-ymn-oyea rPweorDown 5 ho:ruminu-t Poeew rreqFeunc y6H0ZSe lL EGNE DO—RRea OndylR W R—ad/eWrtie TUCO HPLIT POIOT NNAEM http://www.51wendang.com/doc/437ec10ed908de0667a81455CCOOT#DOCC_ VSW ONUCOTOD oi#flila o_lfil_i obliifl_c NOOFF_S cWharge_mw lop_o mPOR_TEP YSPAETMPCa ll_pas CAsPT D_WO p_#fstoa_ _pofs_btp_ ostfc_da te_f1o tmi_ofe1 dta_efo2 tim_ofe2 adt_oef3 time_o3fd ate_o4f itmeof_ 4adt_efo5 tmie_fo f5eqr_6H0T UCOHPI OLTPATH MA IN MNES 0MIAN MNUMEIANME NUS1 AMN MIENUGMINA EMNUMFIA NEMNUSeMAI NMEUNMEIN AENUMAIT MNEUMIN MANEUStM EUMAN IEMNU AIM MNEUNSEMNUS1MA NI EMNMAI NM EN1MIANM ENUSEMA N MEIUNM_OR PMAIN MNU_PROM AI NMEU_TPOR MANIM EN_ORM ANI MNU_POS RMIA MENN_OP RMANI EMUNMa_AOPRMAI N MEUNM_PRO MAI MENU_OR PMAN IMNUEMa://www.51wendang.com/doc/437ec10ed908de0667a81455AS_TPROMA I NEMNUSeE N 301 41 0 11 1 2 627 2 39 4 240 12 23114 3 4 7 8 11 2 15 1161 92 30 ERAD/ WRTE IRO R RO OWR WR RWRO RO RO R OOR WRRO RO R RWWR RW ROORO R ROORO R OO ROR ROR CCWNTA BL EAMNEConf iugrtaionTa besC1 SSatts DuspliyaTableonCigurftaon iTblaeP1S Serivc Ceofigunraitno TalbsvirecCon fguratiino TabeslMASerivec onfiguCartin oablTetasu isDply TablasNaiMntneacn eDiplsayT baelMaTinentnac eisDlpay ableTStatTs uDispaly TbaelsGtSauts DsplayiTa lbseoCnfgiratuon TabilseUtatusDi slpa yabTelsGENUofignratuoni abTleC1 ServiceSC nfogiurationT alesb1eSvirec oCfngiuariot TanlbsE erSivec onCigufraton TiabeslSE1aMntinaenecDisp lya abTels_O RaMniteannec Dsilpy Taabes_POT MRinateannce iDsplya Tabel_PSROM ianteannec Dipsly TaalbesLA_OPRMa nienantceDi slpa Tabyhttp://www.51wendang.com/doc/437ec10ed908de0667a81455esl_LOPR Maitnneace nispDayl TabesLAS_POT MRainteannec iDslap Tyabls_OPRM iatenancne iDslap yabTeslLA_PORS aMniteanne Displca yabTle_TORPMai netancen DiplaysT abes_OPRS ervic eConigfratuoinTables FACTOYR

[此处图片未下载成功]

APENPIDX A— TOUCH PLIO TD SPILYA ATLBS Econ(t)OUTH CPILTOD ECRSIPITN OPowerO n1: d ay-mon-eay rPwor Oe n:1 hou-mrnuiteP weo Or n: day-m2no-yer aowerP O 2n:hour mi-nteu Pweo Onr3:da ym-no-eyar Poew Orn3: h uo-mrnutie oPwr enO4:d ya-mo-yenr Paowr Oe n4 hou:rm-nuitePowe rn O5: dya-on-ymear ower On P5: ohrumi-nuetP wer oSpplu yVotlgaePr e unovcupiecdDa y rev PnuccoupediD a yrevP uocncuipd eimTeP evru noccuiep Tdmi Prepo PD IaGin aVrifna umPpAuto oRationt eDayl Pup mePirdico Sattr Pup Smitcink grPotecitonPump dwnoP rsesuer ir C AumpdPon wPressre CiruB uPpdownmSa urated tTpmA uPmdowp SnautaredtT p mB Quic kHS Efr oeDrfos Qticu kTes tnaEle QbuikcTe stEn blea Rmap oaLinghttp://www.51wendang.com/doc/437ec10ed908de0667a81455d ctivA Remp Loaaing delect SeRdya r oRnuning Sttau sReaalm Triem eRl VcalveMax Po stiio necRlVa lv eMni Positon iRcleimaActi ve eRcalmiCo densen rFlowR celima Cndoense Hraetr RecelimaCo densnre Pupm LEGED RN—OR eda Oly nW—RRead W/rie TtOUH PILOT POINTCNAM date_on1 tiEe_om1 nadet_n2 toime_no da2t_eon3 imte_n3 oadteo_n t4mi_one4date_ no5ti e_on5mv otaleg PVRNDUY PRAVUNAY PRVUNTDIM RVPNUTIMh _pd pgump_de lode_0M p8up_merp P_P_A DDP_P_ hr_sat_aB r_sathb e_h_sdfe QrTS_RQ QT_TSRQT odeM0_ 5rmp_sale ERAD RYEALAR_M mxa_3w mni_w 3odeM_1 C4ODNLFWO ond_cthrH UPM_P1T OCH UPLOT IAPH MAIT NMENUM_IN AMEN_R OMIA NENUMM_R OMAIN EMUN_TOPR AIN MENUM_LPROMA INM NEU_O MAIR MENNUMa_SPO MAIRN ENMUM_PORSMAIN ENM_OP RMIAN ENUMM_PSROMAI NME UYAIMNM ENUMaint\OCDCFECPOOS 1MAN MENIP2O SAMIN MEN://www.51wendang.com/doc/437ec10ed908de0667a81455CO1POS M1AN IMENUPO2S MIN AENM1MAN IMENUAMINME UNStaSAMI NEMUNNIMENUIMAN IENUIMAI MNENUMAN MEIUNIN EMNUMAINMEN US-TKTS MA1N MEIUN_2TM IN MEANUSAIMNMENUUAIN MENMNI MNEAMI NEMUN1AMI NEMUNSeAIMN ENMMSAN MINUEMMIA NENMINMENLAIEN 1 5 269 0113 1 41 718  114 1 112 2 6 14 9 11 51121 1 23337  1 615 304 2 0 191 5 3 4 RE2A/ WRIDETRO O RORRO RO OR RO ORRO R ROWR OR ORO O RR RWW O RWR R RO OO RORR RW RWW O RWRR OW RWR R WOR R OR RO OCN TABLEC ANMEM anteiancenDis laypT abls_TPO MRainteannecDis pay lTbaeslL_OP RMaitnenace Dinslpy TabalesL_PORTM inaentacne isDlap Tyabes_PORA MainenatnecDi psly aaTblse://www.51wendang.com/doc/437ec10ed908de0667a81455SL_TOP RaMnitneace niDspay Tablels_LPO MRinaetnncea DsplaiyT abels_OPRMa itenanne Dicslpy TablesaLA_PR OaiMnteannceDis lpa yTblas_POR Mantineace DisnlpyaTable_AOPRS evire Ccnfiougraion TatlbseFRaiMtennnaecD spila TayblsPO1C SManienatcn DiespalyTa besPOS2Ma inetnnace isDpalyTab elsS1M aitennnaceD silap yablesS2 erSvci eConigufatiro nableTsSECnfiourgation aTlebEStaus tDiplasy TalebECnfioguatior TnblaesSatutsDisp lay TalesSMatts DusilaypT abeslRLtStas Dusilayp abTelsatts Displua TaybelCnoigfurtaoi nablTeatsuDi psal yTalbse_TST S1atus tisDlapyT abel_CTS2 StaTts Duiplsa TyalebsMOCDofniugatron TibleaSEatut sDspliay TablesSifgruatio TanbleS rviee Configucariot TanbeslSESErveiceC onifgrutioanTa blesSE Sttus DiaslaypThttp://www.51wendang.com/doc/437ec10ed908de0667a81455a lesbSDtauts Dislpy aablTeu siDpsaylTab eslRESIatut Dispsly TabaelsM104

[此处图片未下载成功]

APPNDEX IA— TUOH PICOTL IDSLPYATA BLSE(con t)TUCH POLIT DOESRIPCIONTRec liam DedabndaR cleima nEtreni gluFdi Rceliam FludiS eptiot RncelaimL eavin gFliud Rclaiem RCN2 PoBrd Racelam Setipiont ReclimaSt tua sirCuci tA ecRaiml tStus aiCcrut iBR ecalmiValve Posi tionRe erencef umNebr Rfergerinta harCegCt r lRmote eeatH/ColoS wtic RhmoteeI nterlcok Sattu sReomt eeRlcaimS iwth Recome Setpointt Sitcw RehqesuetdElect rc itagS eReset Amout Resetn niE fefc tResteMa nteniance lAer teRetsS/epntt 4-20m SAgln eveRsr Aearmls elaRyR taote Cndenseo Prmusp? oRtte aoColr Pumesp?Run Stat u sRnnuin Sgatts Refurencee eDla tCrciutiA iCcurt i BeRrfiegarntPu mp OtuCir ucit ACriuct iB CicrutiC R nniug OuntputCi cuit A rCriuct B Ciicuri tC StuaraetdC ondnseni Tgpm Cicuri t CArciit u CBiruict CS autartedS ctuin Temp oirCuci http://www.51wendang.com/doc/437ec10ed908de0667a81455A tiCcuirtB CriciutC ircuiCtC EGLEDN O R—eRa dnOl yW— RRed/WriateT UCO PIHLT POONITNAME h _rdadbe HR_ET WRP HSR_LW RTC_NERC Prs prstah_a trhsta_bt rh__pvos RfNue mhcrgea_ HCc_S REM_LWOK RCCL_SEWS TEPSW_ eh_satg reesteM do_e0 S_RE3STESP_ ESRTEal_rever R OTHPUPM RTCPOUPMST AUS RTUNINNG dle_r_t deat_lrb _C_PMPF_ ACF_MPP_BF C_MP_CPQ_RU _N QA_UNRB_ _RUN_QC SCTA _CTS_ BCT_C SST_AS STS_ SSB_CTQ S_IL_C1 OTCHUPI LO PATHTM INAM ENPAIN MEMNAMI MNEUNAAMI MENNUSMEUNMa_ MANIME NUSeTAINM MEUNMIN AMNUIA MENNMAIN MEMU-MAIN ENMTMIANM EUENUAINMM NEUAINM EMUN MENIN MANUAMNI ENUMIN AMNUN MIENUStIN ENMRAhttp://www.51wendang.com/doc/437ec10ed908de0667a81455MNIME UINME UNStTAIMNME UNIMIA MNNEI MNNEUMMAI NEMUNIMEN UMENU tatusSFAIN MMNEI MENNUSt_TSK1T AINM MNUE_ST1MA N IENUMS_TS1 MAITNM EUNStatu_NAM IA MNNU_N MAI NMNUE

_CNAMAIN ENU_AA NMANI MNU_RN AMIAN ENU_ NMIA MNNEUS_1 LINTE 37 5 76 10 36 10 2 0 8 36 315 5  23 7 461 4 143 5222 4 1 132 2 9612 6 3643 44 451 2 211 23 1311 313 EAD/ RWIRT REW R ROO R ROO WR O RO RRO OR R RW ORORO R O OR R OR RO ROO R ROWRO OR R ROORO O RRO RORW W RR WRO O RR OORR ORORW C CNTAB LE AMEN etSopit nCnoigfrauitonT blesttusa ispDly TaalbestaStsu isDpayl TalebSttau Disspal Taylbseanietannc eisDpla yTaleb_NPSet pinto onCfguraitio Tnblas://www.51wendang.com/doc/437ec10ed908de0667a81455T tStusaDi splay abTestatsuDi plsay TalbsSatus Ditplsa TyalbseRECofiguraniot Tabnles!ClrtD_5XXQ AeSvriec CofnguritioanT balsetas Dispula yTalestaSts uDiplays Talbetus Diapsla yaTlesStatus DNsilaypT blaesSMainentnce aDislayp TableaMinentanec isDpaylTab eltsu Dsiplay aTblesnentacenD sipla yaTlbeus tiDslay pablTesConigufraitn TaolbsESttau sDsiplayTa blstsuD ipsla yTbalseSatus tiDsplya ablesTSttusa Dipsly aTablesinteannaecDi sply TaabelsDMaTnitnencae isDpal yabTeslDStatsuDi plsay TbaestuasDi psay TalbelsFLtSautsDis pal yaTlebaut sDspily aaTlbs_TKS1T tSats DuipslayTab le_TT1SS atus tisDpal yTalbe_1St tausD splayi Tbals_A NSttasuDi psaly aTbeslC_NS ttas uiDplasy aTlbhttp://www.51wendang.com/doc/437ec10ed908de0667a81455e_CAN Satut sDsplaiy aTlbs_NAS attu sDsipal Taylesb_INASt tasu isDpay lTbalseCI_CNA tStas DisuplyaTabl esQ_TTS

[此处图片未下载成功]

PPAEDIN AX— TOUC HILOP T DSILAY TPABLES cont)(OUCT PILOHT DSCREPIITNOSCT Cadndiate Circut iA Cricui Bt Criuict CSTCCon roltP iot nCiruitcA Circu i tBC rciit C Sluid ealvV 1e iCcrit A uiCruic BtCirc it uCSli d Velaev C2rcuit iA ircCuitB Cricuit CSliedV lvea 1utOut pirCcit u CArciiutB iCcurt CiSl id eaVlve2 utpOu tCiruit cAC ricuitB C rciutiC uStcionPr ssuree iCrcui A tiCructi CBriuci t S1CCo nfi Sgwtci h8(- 1&gt;) 1 CoSnfig Swicht( -81)&gt;1SC nfiogS itwhc( 8-1&gt;)Sec nodSe ptinot i nseU Sriel aNmberu Srevce iesT Entable erviSing clAetr eStponitCo trnl oeStopni tOccpued? Siepoitt nesect ShutdlonwI dicatnro SatetS ave ldAdressSla v ehilCle rStat Sleav ehCliel roTtlaC ap Salv legastta lSid Veale vaCpcatiy AS ldieVa vl eapaciCytB S lied Vavle apaCctiyC So tfSthttp://www.51wendang.com/doc/437ec10ed908de0667a81455 arterSe elt SofctawrePa tr Nmbur Sepcea T Fll uesetRVa le uSpcaeT NoR eetsV aleu SagtdeLoa dngi SeqenceuS tatr f Eiror rHihgr eStarup Dtely in affEectSt o pPmu pDuirng tSadbyn ELEGNDRO  R—aed nOl RW—y Rae/Wdrte iTOCUHP LITO PONT INME sctA_fua_sct_ ufb sct_fu_c_s c_tpsa_ ctssp_b sc_t_spc_ QSL_I1A Q__SIL1_ QB_LIS_1C _QLI_S2 QA_SLI2_B Q_LI_SC 2LSDI1_A S_IDL_1B_ SLDI__1CSLID 2_A _LID_2_SBS IL_D2_CS _A SPPB _P_S Ccpas1_m _pbc_1_m scc_sp_m1 oMe_0d2S rielNo Qa_TSEQ R_alesrts _ptcl Sr_PCO spC_elsS UTDOWH Nsvlad_drs l_svtats v_capl tlgsata t_SLQA I

_SLBIQ _LISCso fstatrP rtauN smaprcf_u psca_rn osq_tey sptatrdt_ oMde_01p umps_by TUOH PICOT LPTHAM AI NMNEUMaiMRINAME UNRMAIN ENMLAIN MEMUNMAILN EMUAMI MNENIA MENUN_TST1CM INA ENM_ST1 TMIAN MNUE_T1 SAINM ENMUSt_TKST1 AMNI MNEU_TSTK 1MIN MAENUS://www.51wendang.com/doc/437ec10ed908de0667a81455_TCTS MAIN 1MEUN_D MAIC MENN_BDMAI NMEN_DC MAINME U_AD AMIN MEU_MANI MNUE_DM IANME UNS_A NMIANME U_AR MAINNM NEU_ NAINM MNE_N PAMN MEIUNMai_NMAIN M NU_DN PMIAN EMUAMIN MEUNCon-IDtMAIN MENU_TSTRM AINM NEUSCMAINME NUTAINMMEN UINA MENAMINM ENUStAIN MNUEC_iLVS MINA EMN_LMINA MEN_MTSLVS AMNIMENUaint_TSSV LAIMNMENU_sSTT AMIN MNEUSt-TT SMANIM EN_TSR MTINA ENUMSRMAIN ENM-ID AMNI ENUMNIN AMENMIANME UNEMANI MEUNCo_LSVMAIN M NUEAIMNME NULRNE 2 I 16 01 9 571 42 31 1 82 3253 3  3 4 4 444 413 7 21 315http://www.51wendang.com/doc/437ec10ed908de0667a81455 1 2 2 72625 27 1 6 7 11 4 6 8 843 1 211  14 9 261 EADR/W ITE RO RO RO RO RR RO OWRR WRWRW RW R W OR R OR OROR O RO R ORORO RORO R O R OR OR RWW RORO RW RO R WR OO RORR WRW RW R WRORW WRR WRW R OWRC CNTA LB ENMEAM iatennanc eiDspaly TbaeslFAMainRetancenD silpyaT alesaMntenaice Dinpsal TabylesFinteanacenD iplay saTbelsintneacneD spliy aaTlbseianenancteDisplay aTbelats Diupsay lablTse_ST1T tStuasDis paylT blae_TSs1 STtats Duisply Taabls_CST1 STatut Dispsla yTales_KTT1 SSattsuDi slay Tpbals_KTST1Sta ust Dspiayl Tblae_TT1 SSttua sDsilpy TabalseCI_A DSatus Dtipsaly Tales_I DStautsD iplasy aTlbse_IDSt auts iDspla Tayles_D StAaut Dssilpy Tables_C DStatu sispDly aables_ Satus tDspial TyblaesCIR_CNA Satust iDslap yTbales_BANS ttasuDi plsy Tablase_ANCM aitnenacenDi slap yTabls_PO NaiMnentncea iDsply Tabale://www.51wendang.com/doc/437ec10ed908de0667a81455A_DN PManteninae cDislpa Tybale_DP StaNtus isDpaylT albseoCnigurftaoi nTaleb!ltrI_X5AQ StaXut sDspliya TbalesSE_TSRTSe virc Cenfogiraution TalesbMtSaustD spilya ablTseTtatSus isDpal yTbaleTtatSs DiuslapyTa blstatuS siDpsla yaTlbesoCnfiurgatio nTbael_V LMinatnaenecD spiay TalblesMSTMintenaace nDispayl aTbelsMMEiatnnenaec Dsipayl aTblesEStats uDiplas Tybals_STTSta ts DisplauyT abls_STS attu sDsilap Tybles_T SeSrvcieC onfgiruaitn Tabolsnoifguration Talebs!tlrCIDPD5_ion Ctnofigurtaoin TabesSOeptoint Cnfiourgaiot nabTesTConfgirutaoniT

ablsCnofiguratio naTbles_TLVSSt aus tispDalyT albeoCnfguiarton Tailbe

[此处图片未下载成功]

APPNEIDXA—T UOH CPLIT  OISDPAYL ABTES (Locn)TtUOHCPILO TEDCSIPTIRONSub C ndensero eTp mCir ASubC ondnees http://www.51wendang.com/doc/437ec10ed908de0667a81455rTem pCr iB Sucobloin gTmpereaurt Ae Sucboling Tomperetauer BS utioncA T mp eAervge Suatcion BTe m Apverge aSctuin CoTem pA ervag Seutcino H CSntrol Po tASu citno HSCo tnrlo t PBSu ction SHCo nrol PttC Sctioun upeSherat AucSitn Suoerheapt SuctioBnS uepreah tCS wtchi imLt Sietpiot 1 SwnichtL miitS etopitn2 S wtic hLimt Siteoinpt 3Sstye maMngar ecAtve TiCM BoaPr dCopmA CTM PoBra Codpm TBPCMB oar Compd CT mie Odvrerdier Hurs oTmediO ervrder Hoius riTem-Overrdie dDuartoin imed-OTvrerdeiD urtioan TimdeO-verrde ii Enfect Tfmed-Ovieriderin E ffct Toetal ansFN B CrciituA C icuir B tiCruic CtUnit CpacityaMo de lUin ti saMset or rSalv enUtiO ff t onODe aly nUitTy e (pHet Pumpa=2)Use asswPro Vdalv ecAutaotsr eHatesrW atreC on Entde VralvA Wat re oCd nnteE ralvVB Wtae Cornd Entr eVlve A Waaer CondtE nert VavelB Wa etr oCd neaL ValvveB Watr eondC eavLngi Vavl A eWtar eonCd eavLin gaVve B Walte rDela T Wtter Excaahgnr ePup m1Wa etrExcha nger Pmup http://www.51wendang.com/doc/437ec10ed908de0667a81455W2aer tilFtre tCrl(da s) yatWr Loop Centool Wrtae Purm p1#Ho rs Water uPump#2 oHrs uWter Vaa Colndesinn Stp gWtrea Con Leavd alve A VyW Delta Start SeleectLE GND ER— ORae dnlOyR W—ead/WriRe TOUCt PHLOI TPINOT AMN Erh_sbtu arhsu_tb bh_rsbua ch_surbc sst_b_am sstm__ ssbt__m cs_sh_pas _hs_pb h_sp_csSH _ SHAB S__HC im_slp1lim sp2_ il_smp 3Mdo_e10c a_vepr cps_bver cpsc_vers ORV_XETO VRE_TX OEV_HRSO E_HRV SVERLASO TVEROASLTnb_fa n_anb f_anb _bn_anf_ ucnisite zstslv mff_on_o duin_ttpy seu_psas F_CHRTQ HR_WEA_ Q_RHE_BW hr_e_a wr_he_w Q_bRHWLB hr_lw__ ahrl__wb edla_t t_QMPP Q_1PMP2 fiwte_l cloop_wch _cpurm hr1_pcmu2w _cs_spt _HRLW_QA wey_delt TUCO PHLIT POTAH AMIN EMNIA NMENUStNMENUINM EUMAMIN MEUNM_ITM IN AMEN_IMTIM AI MENNU_ILIMT AMNIM EUN_CTRV LMAN IMEU_CTVL RMIA MNEUNMa_RLM AINM EUN_CTL MARN MENU://www.51wendang.com/doc/437ec10ed908de0667a81455_TRL AMN MIENU_CTVRL MAN IEMUNAINM MNEUSAIM MNNUEMAIN MTENUSMIAN MNEUMa_P MNIA MENNU_RP NMIANMEN U_rtainoTa lesSMA NI MNES MIN AENMCPO1S MANIME UP2OS MIA MENUNO1S MPIN AEMNSAIM NENMY AMNIME NUSR MAI MENUNSMIA NMNEMNNU-MSMSLTVM IA MNEUMEIA MNNUESMAYI MENUM1IA MNEUMNUE_TST M2IAN MNE_STT 2AMN IENMUStMAMIN MENMAMINME U_ 2MAI MNENUStMMANI ENUMStAMNI EMUNMMIAN ENU_KS

MA I NENU_STT1 AIN MMNUAIM MNEN://www.51wendang.com/doc/437ec10ed908de0667a81455iecAIN MMENUSMNENUServAIN MMENTMINAM NEUS_TKT2S MAN MENUE 122 214 2 448 1 25 12 9 1 14 181 3 343 35 1 1111 5 91 1 14 4 3 1431 561 22 6 24 11 5 0916 2 16 10 2884 7 38 934 1 14 3386  RE9DA/ RITE RW ROOR O RO RO O RR RO OR ROORO O RRORW R W R WORRO R O OR OR O RRO O RO RROR RW RW RW WRO R WRWRW RO W RRW OR R RO RW RO ROORW R RWWR WRW RW RW R RW CCWNT ALE BAME StatNusDis plya aTbesStLatu DssilaypTa lbstaStu Displasy TablseRECStatus DislpyaTables ERCALI MMintanaenceD sipaylTabl e_LPIIT MainteManne Discply Tabalse_IMITLMai tnneanecD splayi Talbs_LMII TaMinentacen iDpsaly aTble_XTRLC Mintenaace nDsiplyaT albseE_CVRTL aiMtenancne Diplay sablTs_VCTL RainMteancne Dipsayl Tblea_CVRLTM aitnnance eDiplays aTbls_TCL MRanietanne cDsilap Tybale_CERTLSetp oni tConifgratuionTables ESPOTIN TSteoint Cpnhttp://www.51wendang.com/doc/437ec10ed908de0667a81455figuraoitn TobaeletpSiontC nofigurtaion aTlestatu Disslpay TabelsMOainMenatcne DipslyaT albs_PR MaNntieanne cDisply Taable_PR MaiNtnenanc eDsilap Tyalbse_DNP onfigurCaiotn TblesaS CCofniuratgoniTab lesOCCC2 MSianetnnca Dieslay pTbaesPC1OS aiMtenancen isDpal yTbaelsOPS 2aMnitenncaeDis paylTa beslODP1O MSiatenannce ispDla TyblaesPCOS2Se vriecC nfoguiationr TabeslYSer vcie oCfignrautionTa blsY eSrice Covfinuragtin oTabels2eSrivec onCifugrationTab lsainMtennaecD spliyaT alebsMSVCofinguatrio nTalebeSrivce Cofngiuratoin TblesaFACTYSerice Cvnofiuratgin Tabloe1Stats Duislap yablesLSatut siDpsaylTables_CSTT2S ttau sisDpalyTa lbs_CTST Status 2isDpla TybaesltatSs DisupaylT baelSattu Dsispla Taylbs_KTT2 SStats Diuspay lTalesMSathttp://www.51wendang.com/doc/437ec10ed908de0667a81455tus Dsipay TlableMMintananee cisDlay pabTeslLtatusDi plsya Tbaes_TTS 1Sttuas DiplsayTa bls_ST1 TSrviee Ccnoifugatrin oaTlbesMrvci Ceonfigrautin TaboeseSvrcie onfiCgrautino TblaesReSvrice oCnfigruatoi naTbesRSteopni tCofiguratnoinT balstu sDsipla yablTesQC-TKTS2Serv iceC onigufariontT balse

R07

[此处图片未下载成功]

APPENDIX B — NAVIGATOR  DISPLAY TABLES

— RUN STATUS

DISPLAYEntering Fluid TempLeaving Fluid TempActive SetpointControl PointUnit Run Status

.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)

-1000-1000-1000-100Off

/YESLocal OffLocal OnCCNRemote0-1000-1000-1000-1000-320-1000-40000-40000=Normal1=Partial2=ShutdownDSBL/ENBLDSBL/ENBL0=Cooling1=Heating2=StandbyNOhttp://www.51wendang.com/doc/437ec10ed908de0667a81455/YES00:00-23:591=January2=February3=March4=April6=May6=June7=July8=August9=September10=October11=November12=December1-3100-990-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*

TABLESTATEGENSTATEGENGENUNITGENUNITGENUNIT

POINTCOOL_EWTCOOL_LWTSPCTRL_PNTSTATUS

.434335, 5735,43,46,5722-25

EWT LWT SETP CTPT STAT OCC CTRL CAP CAP. A CAP. B CAP. C CAP. S LIM CURR CUR.L ALRM EMGY CH.SS HC.ST RC.ST TIME MNTH

Unit Control TypeGENUNITGENUNITCHIL_OCCctr_type22-2522-25

Total CapacityPercent Capacity Cir APercent Capacity Cir BPercent Capacity Cir CCapacity Indicator

Demand Limit ValActual Chiller CurrentChiller Current LimitAlarm State

Stop

Chiller Start StopHeat Cool StatusReclaim Select StatusTime of DayMonth of Year

(%)XXhttp://www.51wendang.com/doc/437ec10ed908de0667a81455X (%)XXX (%)XXX (%)XX

(%)XXX (amps)XXX (amps)

/AN/A

_TCAPA_TCAPB_TCAPC_TOVER_CAPDEM-LIMTOT_CURRCURR_LIMALMEMSTOPCHILL_S_SHEATCOOLreclaim_selTIMEmoy

notsupported.Not supported.

.XX

DATE YEAR HRS.U STR.U HR.P1 HR.P2 HR.P3 HR.A HR.B HR.C ST.A ST.B ST.C

of MonthYear of Century

STARTS/HOURSMachine Operating HoursMachine Starts

Pump 1 Run HoursWater Pump 2 Run HoursCondenser Pump 1 HoursCOMPRESSOR RUN HOURSCompressor A Run HoursCompressor B Run HoursCompressor C Run HoursCOMPRESSOR STARTSCompressor A StartsCompressor B StartsCompressor C Starts

(hours)XXXX

(hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXXXXXXXXXX

/AN/A

://www.51wendang.com/doc/437ec10ed908de0667a81455orcibleforcibleforcibleforcibleforcibleforcibleforcibleforcible

_machst_machhr_cpum1hr_cpum2hr_hpump1hr_cp_ahr_cp_bhr_cp_cst_cp_ast_cp_bst_cp_c

supported.

supported.

*As data in all of these categories can exceed 9999 the following display strategy is used:From 0-9999 display as 4 digits.From 9999-99999 display xx.xK

99900-999999 display as xxxK.

APPENDIX B — NAVIGATOR  DISPLAY TABLES (cont)

— RUN STATUS

RUN HOURSFan 1 Run Hours Cir AFan 2 Run Hours Cir AFan 3 Run Hours Cir AFan 4 Run Hours Cir AFan 5 Run Hours Cir AFan 6 Run Hours Cir AFan 7 Run Hours Cir AFan 8 Run Hours Cir AFan 9 Run Hours Cir AFan 10 Run Hours Cir AFan 1 Run Hours Cir BFan 2 Run Hours Cir BFan 3 Run Hours Cir BFan 4 Run Hours Cir BFan 5 Run Hours Cirhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 BFan 6 Run Hours Cir BFan 7 Run Hours Cir BFan 8 Run Hours Cir BFan 9 Run Hours Cir BFan 10 Run Hours Cir BFan 1 Run Hours Cir CFan 2 Run Hours Cir CFan 3 Run Hours Cir CFan 4 Run Hours Cir CFan 5 Run Hours Cir CFan 6 Run Hours Cir CFan 7 Run Hours Cir CFan 8 Run Hours Cir CFan 9 Run Hours Cir CFan 10 Run Hours Cir CCOMPRESSOR DISABLECompressor A DisableCompressor B DisableCompressor C Disable

MAINTENANCERefrigerant ChargeWater Loop SizePump 1 (Days)Pump 2 (Days)

Pump 1 (Days)Cond Pump 2 (Days)Water Filter

A OIl Filter (days)Comp B Oil Filter (days)Comp C Oil Filter (days)SOFTWARE VERSIONSCSA-XXXXXXXXXXXXXXX-XX-XXXXXXXX-XX-XXXXXXXX-XX-XXXXXXXX-XX-XXXXXXXX-XX-XXXXXXXX-XX-XXXXXXXX-XX-XXXXXXXX-XX-XXXXXXXX-XX-XXXXXXXX-XX-XXXXXXXX-XX-XXXXXXXX-XX-XXXXXXXX-XX-XXXXXXXX-XX-XXXXXXXX-XX-XXXXXXXX-XX-XX

(hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (http://www.51wendang.com/doc/437ec10ed908de0667a81455hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (hours)XXXX (hours)

-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*0-999999*NO/YESNO/YESNO/YESNO/YESNO/YES

supported.Not supported.Not supported.Not supported.Not supported.Not supported.Not supported.Not supported.Not supported.Not supported.Not supported.Not supported.Not supported.Not supported.Not supported.Not supported.Not supported.Not supported.Not supported.Not supported.Not supported.Not supported.Not supported.Not supported.Not supportedhttp://www.51wendang.com/doc/437ec10ed908de0667a81455.Not supported.Not supported.Not supported.Not supported.Not supported.

TABLEFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSFANHOURSCP_UNABLCP_UNABLCP_UNABLSERMAINTSERMAINTSERMAINTSERMAINTSERMAINTSERMAINTSERMAINTSERMAINTSERMAINTSERMAINT

POINThr_fana1hr_fana2hr_fana3hr_fana4hr_fana5hr_fana6hr_fana7hr_fana8hr_fana9hrfana10hr_fanb1hr_fanb2hr_fanb3hr_fanb4hr_fanb5hr_fanb6hr_fanb7hr_fanb8hr_fanb9hrfanb10hr_fanc1hr_fanc2hr_fanc3hr_fanc4hr_fanc5hr_fanc6hr_fanchttp://www.51wendang.com/doc/437ec10ed908de0667a814557hr_fanc8

.

FR.A1 FR.A2 FR.A3 FR.A4 FR.A5 FR.A6 FR.A7 FR.A8 FR.A9 F.A10 FR.B1 FR.B2 FR.B3 FR.B4 FR.B5 FR.B6 FR.B7 FR.B8 FR.B9 F.B10 FR.C1 FR.C2 FR.C3 FR.C4 FR.C5 FR.C6 FR.C7 FR.C8 FR.C9 F.C10 A.UN B.UN C.UN CHRG WATE PMP.1 PMP.2 PMP.3 PMP.4 W.FIL A.FIL B.FIL C.FIL APPL MARQ NAVI EXVA EXVB EXVC AUX1 AUX2 AUX3 AUX4 AUX5 AUX6 CPMA CPMB CPMC EMM R.BRD

.UN

_cp_aun_cp_bun_cp_ccharge_mwloop_mcpump1_mcpump2_mhpump1_mhpump2_mwfilte_mofilta_mofiltb_mofiltc_mPD5_APPLSTDUNavigatorEXV_BRDAEXV_BRDBEXV_BRDCAUX_BRD1AUX_BRD2AUX_BRD3AUX_BRD4AUX_BRD5AUX_BRD6SPM_CPASPM_CPBSPM_CPCEMM_NRCPREC_NRCP

(days)(days)(days)

supported.

ENTER and ESCAPEsimultaneouslyto read versioninformation

*As data in all of these categories can exceed 9999 the following display strategy is used:From 0-9999 display as 4 digits.From 9999-99999 display xx.xK

://www.51wendang.com/doc/437ec10ed908de0667a81455rom 99900-999999 display as xxxK.

APPENDIX B — NAVIGATOR  DISPLAY TABLES (cont)

— SERVICE TEST

TEST MODEManual SequenceCompressor A Output

/ON

-Off-Enable Switch must be set to OFF PositionRemote-Off-Enable Switch must be set to ENABLE Position

TABLEN/AN/AN/A

POINTservice_testcomp_serv_a

.65, 86

T.REQ CP.A SLI.A CP.B SLI.B CP.C SLI.C Q.REQ EXV.A EXV.B EXV.C ECO.A ECO.B ECO.C FAN.A FAN.B FAN.C SPD.A SPD.B SPD.C HT.A SL1.A SL2.A HGP.A OLS.A DGT.A HT.B SL1.B SL2.B HGP.B OLS.B DGT.B HT.C SL1.C SL2.C HGP.C OLS.C DGT.C PMP.1 PMP.2 PMP.3 CL.HT BVL.A BVL.B BVL.C Q.RDY Q.RUN SHUT CATO ALRM ALRT

Valve Capacity ACompressor B OutputSlide Valve Capacity BCompressor C OutputSlide Valve Capacity CQUICK TEST MODECirhttp://www.51wendang.com/doc/437ec10ed908de0667a81455cuit A EXV % OpenCircuit B EXV % OpenCircuit C EXV % OpenCirc A ECO EXV %Circ B ECO EXV %Circ C ECO EXV %Circuit A Fan StagesCircuit B Fan StagesCircuit C Fan StagesCir A Varifan positionCir B Varifan positionCir C Varifan positionOil Heater Circuit ASlide Valve 1 Cir ASlide Valve 2 Cir B

Gas Bypass A OutputOil Solenoid Cir ADGT Cool Solenoid AOil Heater Circuit BSlide Valve 1 Cir BSlide Valve 2 Cir B

Gas Bypass B OutputOil Solenoid Cir ADGT Cool Solenoid BOil Heater Circuit CSlide Valve 1 Cir CSlide Valve 2 Cir C

Gas Bypass C OutputOil Solenoid Cir CDGT Cool Solenoid CWater Exchanger Pump 1Water Exchanger Pump 2Condenser Pump 1Cooler Heater OutputBall Valve Position ABall Valve Position BBall Valve Position CChiller Ready StatusChiller Running StatusCustomer Shutdown StatChiller Capacity in 0-10vAlarm RelayAlert Relay

(%)XXX (%)XXX (%)XXX (%)XXX (%)XXX (%)XXX

(%)XXX (%)XXX (%)://www.51wendang.com/doc/437ec10ed908de0667a81455ar/ONunchangedincreasedecreaseOFF/ONunchangedincreasedecreaseOFF/ONunchangedincreasedecreaseOFF/ON0-1000-1000-1000-1000-1000-1000-80-80-80-1000-1000-100OFF/ONOFF/ONOFF/ONOFF/ONOFF/ONOFF/ONOFF/ONOFF/ONOFF/ONOFF/ONOFF/ONOFF/ONOFF/ONOFF/ONOFF/ONOFF/ONOFF/ONOFF/ONOFF/ONOFF/ONOFF/ONOFF/ONOPEN/CLSEOPEN/CLSEOPEN/CLSEOFF/ONOFF/ONOFF/ONOFF/ONOFF/ON

/A

_ser_sid_acomp_serv_bcomp_ser_sid_bcomp_serv_ccomp_ser_sid_c

supported.Not supported.Remote-Off-Enable Switch must be set to OFF PositionNot supported.Not supported.Not supported.Not supported.Not supported.Not supported.Not supported.Not supported.Not supported.

/A

supported.Not supported.Not supported.Not supported.Not supported.Not supported.

supported.Not supported.Not supported.Not supported.

://www.51wendang.com/doc/437ec10ed908de0667a81455eforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcible

/AN/AN/AN/AN/A

,6564,656565

/AN/AN/AN/AN/AN/A

/AN/AN/A

.X (vdc)

/AN/AN/AN/AN/AN/A

APPENDIX B — NAVIGATOR  DISPLAY TABLES (cont)

— TEMPERATURE

TEMPERATURESCooler Entering FluidCooler Leaving FluidCondenser Entering FluidCondenser Leaving FluidOutside Air TemperatureLead/Lag Leaving FluidOptional Space TempCooler Heater TempCooler Heat Temp Cir CCIRCUIT A TEMPERATURESSat Cond Temp Circ ASat Suction Temp Circ ADischarge Gas Temp Cir ASuction Gas Temp Circ ASuperheat Temp Circ AEconomizer Gas Temp AEconomizer Superheat AMotor Temperature Cir ACIRCUIT B TEMPERATURESSathttp://www.51wendang.com/doc/437ec10ed908de0667a81455 Cond Temp Circ BSat Suction Temp Circ BDischarge Gas Temp Cir BSuction Gas Temp Circ BSuperheat Temp Circ BEconomizer Gas Temp BEconomizer Superheat BMotor Temperature Cir BCIRCUIT C TEMPERATURESSat Cond Temp Circ CSat Suction Temp Circ CDischarge Gas Temp Cir CSuction Gas Temp Circ CSuperheat Temp Circ CEconomizer Gas Temp CEconomizer Superheat CMotor Temperature Cir C

.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X ( F/ C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X ( F/ C)XXX.X

(dhttp://www.51wendang.com/doc/437ec10ed908de0667a81455eg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X ( F/ C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)

–40-245 F(–40-118 C)–40-245 F(–40-118 C)–40-245 F(–40-118 C)–40-245 F(–40-118 C)–40-245 F(–40-118 C)–40-245 F(–40-118 C)–40-245 F(–40-118 C)–40-245 F(–40-118 C)–40-245 F(–40-118 C)–40-245 F(–40-118 C)–40-245 F(–40-118 C)–40-245 F(–40-118 C)–40-245 F(–40-118 C)–40-245 F(–40-118 C)–40-245 F(–40-118 C)–40-245 F(–40-118 C)–40-245 F(–40-118 C)–40-245 F(–40-118 C)–40-245 F(–40-118 C)–40-245 F(–40-118 C)–40-245 F(–40-118 C)–40-245 F(–40-118 C)–40-245 F(–40-118 C)–45-245 F(–43-118 C)–45-245 F(–43-118 C)–40-245 F(–40-118 C)–45-245 F(–43-118 C)

TABLESTATEGENSTATEGEN

machine only

machine only

POINTCOhttp://www.51wendang.com/doc/437ec10ed908de0667a81455OL_EWTCOOL_LWTCOND_LWTCOND_EWT

supported.Not supported.

_ANCIRCA_AN

_HEATERT_HEAT_CSCT_ASST_ADGT_A

_ANCIRCA_AN

_T_ASH_A

_TP_AECO_SH_ACP_TMP_A

_ANCIRCB_AN

_BSST_BDGT_B

_ANCIRCB_AN

_T_BSH_B

_TP_BECO_SH_BCP_TMP_B

_ANCIRCC_ANCIRCC_AN

_CSST_CDGT_C

_ANCIRCC_AN

_T_CSH_C

_TP_CECO_SH_CCP_TMP_C

.

CEWT CLWT CD.LT CD.ET OAT CHWS SPT THHR THR.C SCT.A SST.A DGT.A SGT.A SUP.A ECT.A ESH.A CTP.A SCT.B SST.B DGT.B SGT.B SUP.B ECT.B ESH.B CTP.B SCT.C SST.C DGT.C SGT.C SUP.C ECT.C ESH.C CTP.C

://www.51wendang.comIR.BCIR.A

APPENDIX B — NAVIGATOR  DISPLAY TABLES (cont)

— SET POINTS

SETPOINTSCooling Setpoint 1Cooing Setpohttp://www.51wendang.com/doc/437ec10ed908de0667a81455int 2Ice Setpoint

No Reset ValCurrent Full Reset ValDelta T No Reset TempDelta T Full Reset TempOAT No Reset TempOAT Full Reset TempSpace T No Reset TempSpace T Full Reset TempDegrees Cool ResetCool Changeover SetptCool Ramp LoadingHEATING SETPOINTSHeating Setpoint 1Heating Setpoint 2Current to Reset ValCurrent Full Reset ValDelta T No Reset TempDelta T Full Reset TempOAT No Reset TempOAT Full Reset TempDegrees Heat ResetHeat Changeover SetptHeat Ramp LoadingMISC SETPOINTSSwitch Limit Setpoint 1Switch Limit Setpoint 2Switch Limit Setpoint 3Water Val Cond Stp

.X

(deg F/deg C)XXXX.X

(deg F/deg C)XXXX.X

(deg F/deg C)XX.X (mA)XX.X (mA)XXX.X ( F/ C)XXX.X ( F/ C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XX.X ( F/ C)XX.X

(deg F/deg C)X.X

–20-70 F(–29-21 C),Default = 44.0–20-70 F(–29-21 C),Default = 44.0–20-70 http://www.51wendang.com/doc/437ec10ed908de0667a81455F(–29-21 C),Default = 44.00-20,

= 00-20,

= 00-125 F(0-69.4 C),Default = 00-125 F(0-69.4 C),Default = 00-125 F(–18-52 C),Default = 14.00-25 F

(–18-52 C),Default = 14.00-125 F(–18-52 C),Default = 14.00-125 F(–18-52 C),Default = 14.0–30-30 F

(–16.7-16.7 C),Default = 0Default = 75.00.2-2.0  F(0.1-1.1  C),Default = 1.0Default = 100Default = 100Default = 0Default = 0Default = 0Default = 0Default = 14.0Default = 14.0Default = 0Default = 64Default = 1.00-100,

= 1000-100,

= 1000-100,

= 10080-140 F(26.7-60 C)

machine only

machine only

machine only

machine only

machine only

machine only

machine only

machine only

machine only

machine only

machine only

://www.51wendang.com/doc/437ec10ed908de0667a81455bleforcibleforcibleforcibleforcibleforcibleforcible

supported.

TABLESETPOINTSETPOINTSETPOINTSETPOINTSETPOINTSETPOINTSETPOINTSETPOINTSETPOINTSETPOINTSETPOINTSETPOINTSETPOINTSETPOINT

POINTcsp1csp2ice_spv_cr_nov_cr_fudt_cr_nodt_cr_fuoatcr_nooatcr_fuspacr_nospacr_fucr_degcauto_spcramp_sp

, 5735, 36,3835, 36,3835-38PAGENO.25, 26, 40,4625, 26, 40, 5725, 40, 5736, 3836, 3835, 3735, 37

CSP.1 CSP.2 CSP.3 CRV1 CRV2 CRT1 CRT2 CRO1 CRO2 CRS1 CRS2 DGRC CAUT CRMP HSP.1 HSP.2 HRV1 HRV2 HRT1 HRT2 HRO1 HRO2 DGRH HAUT HRMP DLS1 DLS2 DLS3 W.SCT

.X

(deg F/deg C)XXX.X

(deg F/deg C)XX.X (mA)XX.X (mA)XXX.X ( F/ C)XXX.X ( F/ C)XXX.X

(deg F/deg C)XXX.X

(deg F/deg C)XX.X ( F/ C)XX.X

(deg F/deg C)X.XXXX (%)XXX (%)XXX (%)XXX.X

(deg F/deg C)

://www.51wendang.com/doc/437ec10ed908de0667a81455eforcibleforcibleforcibleforcibleforcibleforcible

.1HSP.2v_hr_nov_hr_fudt_hr_nodt_hr_fuoathr_nooathr_fuDGRHhauto_sphramp_splim_sp1lim_sp2lim_sp3w_sct_sp

APPENDIX B — NAVIGATOR  DISPLAY TABLES (cont)

— PRESSURE

A PRESSURESDischarge Pressure Cir ASuction Pressure Circ AOil Pressure Circ AOil Pressure Diff AEconomizer Pressure ACIRCUIT B PRESSURESDischarge Pressure Cir BSuction Pressure Circ BOil Pressure Circ BOil Pressure Diff BEconomizer Pressure BCIRCUIT A PRESSURESDischarge Pressure Cir CSuction Pressure Circ COil Pressure Circ COil Pressure Diff CEconomizer Pressure C

.X(psig/kPa)XXX.X(psig/kPa)XXX.X(psig/kPa)XXX.X(psig/kPa)XXX.X(psig/kPa)XXX.X(psig/kPa)XXX.X(psig/kPa)XXX.X(psig/kPa)XXX.X(psig/http://www.51wendang.com/doc/437ec10ed908de0667a81455kPa)XXX.X(psig/kPa)XXX.X(psig/kPa)XXX.X(psig/kPa)XXX.X(psig/kPa)XXX.X(psig/kPa)XXX.X(psig/kPa)

supported.

TABLECIRCA_ANCIRCA_AN

POINTDP_ASP_AOP_ADOP_AECON_P_A

_ANCIRCB_AN

_BSP_BOP_BDOP_BECON_P_B

_ANCIRCC_AN

_CSP_COP_CDOP_CECON_P_C

PAGENO.58

DP.A SP.A OP.A DOP.A ECP.A DP.B SP.B OP.B DOP.B ECP.B DP.C SP.C OP.C DOP.C ECP.C

.CPRC.B

.A

— INPUTS

INPUTSOn Off SwitchCooler Interlock

Flow SwitchDemand Limit Switch 1Demand Limit Switch 2Ice Done

Setpoint SwitchElectrical Box SafetyPump Run FeedbackOccupancy Override SwitHeat Cool Switch StatusRemote Interlock SwitchOil Level Circuit AOil Level Circuit BOil Level Circuit C

Current Circuit AMotor Current Circuit BMotor Current Circuit C4-20 http://www.51wendang.com/doc/437ec10ed908de0667a81455mA Demand Signal4-20 mA Reset/Setpoint

/CLSEOPEN/CLSEOPEN/CLSEOPEN/CLSEOPEN/CLSEOFF/ONOFF/ONOPEN/CLSEOPEN/CLSEOFF/ONOFF/ONOPEN/CLSELOW/HIGHLOW/HIGHLOW/HIGH0-6000-6000-6004 to 204 to 20

TABLESTATEGENSTATEGENSTATEGENSTATEGENSTATEGENSTATEGENSTATEGENSTATEGENSTATEGENSTATEGENSTATEGENSTATEGENSTATEGENSTATEGENSTATEGENSTATEGENSTATEGENSTATEGENSTATEGENSTATEGEN

POINTONOFLOCK_1CONFLOWLIM_SW1LIM_SW2ICE_SWSETP_SWELEC_BOXPUMP_DEFOCC_OVSWHC_SWREM-LOCKOIL_L_AOIL_L_BOIL_L_CCURR_ACURR_BCURR_CLIM_ANALSP_RESET

.433939

ONOF LOCK COND DLS1 DLS2 ICE.D DUAL ELEC PUMP OCCS HC.SW RLOC OIL.A OIL.B OIL.C CUR.A CUR.B CUR.C DMND RSET

.I

.X (amps)XXX.X (amps)XXX.X (amps)XXX.X (mA)XXX.X (mA)

supported.Not supported.

APPENDIX B — NAVIGATOR  DISPLAY TABLES (cont)

— OUTPUTS

://www.51wendang.com/doc/437ec10ed908de0667a81455rA OUTPUTSCompressor A RelayOil Heater Circuit ASlide Valve 1 Cir ASlide Valve 2 Cir AOil Solenoid Cir AHot Gas Bypass Cir ACircuit A Fan StagesCirc A Varifan PositionCircuit A EXV % OpenCirc A EXV ECO % OpenDGT Cool Solenoid ACIRCUIT B OUTPUTSCompressor B RelayOil Heater Circuit BSlide Valve 1 Cir BSlide Valve 2 Cir BOil Solenoid Cir BHot Gas Bypass Cir BCircuit B Fan StagesCirc B Varifan PositionCircuit B EXV % OpenCirc B EXV ECO % OpenDGT Cool Solenoid BCIRCUIT C OUTPUTSCompressor C RelayOil Heater Circuit CSlide Valve 1 Cir CSlide Valve 2 Cir COil Solenoid Cir CHot Gas Bypass Cir CCircuit C Fan StagesCirc C Varifan PositionCircuit C EXV % OpenCirc C EXV ECO % OpenDGT Cool Solenoid CGENERAL OUTPUTSWater Exchanger Pump 1Water Exchanger Pump 2Condenser Pump 1Cooler Heater OutputBall Valve Position ABall Valve Position BBall Valve Position CCondenser Heat OutputChiller Ready StatusChiller Running StatusCustomer Shutdown Shttp://www.51wendang.com/doc/437ec10ed908de0667a81455tatChiller Capacity 0-10 vAlarm RelayAlert Relay

/ONOFF/ONOFF/ONOFF/ONOFF/ONOFF/ON0-60-1000-1000-100OFF/ONOFF/ONOFF/ONOFF/ONOFF/ONOFF/ONOFF/ON0-60-1000-1000-100OFF/ON

supported.

/ONOFF/ONOFF/ONOFF/ON0-60-1000-1000-100OFF/ONOFF/ONOFF/ONOFF/ONOFF/ON

/CLOSEOPEN/CLOSEOPEN/CLOSEOFF/ONOFF/ONOFF/ONOFF/ONOFF/ONOFF/ON

TABLECIRCA_DCIRCA_DCIRCA_DCIRCA_DCIRCA_DCIRCA_DCIRCA_DCIRCA_ANCIRCA_ANCIRCA_ANCIRCA_DCIRCB_DCIRCB_DCIRCB_DCIRCB_DCIRCB_DCIRCB_DCIRCB_DCIRCB_ANCIRCB_ANCIRCB_ANCIRCB_DCIRCC_DCIRCC_DCIRCC_DCIRCC_DCIRCC_DCIRCC_DCIRCC_DCIRCC_ANCIRCC_ANCIRCC_ANCIRCC_DSTATEGENSTATEGENSTATEGENSTATEGENCIRCA_DCIRCB_DCIRCC_DRECLAIMSTATEGENSTATEGENSTATEGENSTATEGENSTATEGENSTATEGEN

POINTCP_A

_HT_ASLID1_ASLID2_AOIL_SL_AFAN_ST_Ahd_pos_aEXV_AEXV_EC_Adgt_gascool_aCP_B

_HT_BSLID1_BSLID2_BOIL_SL_BFANhttp://www.51wendang.com/doc/437ec10ed908de0667a81455_ST_Bhd_pos_bEXV_BEXV_EC_Bdgt_gascool_bCP_C

_HT_CSLID1_CSLID2_COIL_SL_CFAN_ST_Chd_pos_cEXV_CEXV_EC_Cdgt_gascool_cCPUMP_1CPUMP_2HPUMP_1COOLHEATref_iso_aref_iso_bref_iso_ccond_htrREADYRUNNINGSHUTDOWNCAPT_010ALARMALERT

.

CP.A HT.A SL1.A SL2.A OLS.A HGB.A FAN.A SPD.A EXV.A ECO.A DGT.A CP.B HT.B SL1.B SL2.B OLS.B HGB.B FAN.B SPD.B EXV.B ECO.B DGT.B CP.C HT.C SL1.C SL2.C OLS.C HGB.C FAN.C SPD.C EXV.C ECO.C DGT.C PMP.1 PMP.2 PMP.3 CO.HT BVL.A BVL.B BVL.C CN.HT REDY RUN SHUT CATO ALRM ALRT

://www.51wendang.comIR.B

.A

(%)XXX (%)XXX (%)

(%)XXX (%)XXX (%)OFF/ONOFF/ON

(%)XXX (%)XXX (%)

supported.Not supported.Not supported.

.X

— CONFIGURATION

CONFIGURATIONTest Display LEDsMetric Display

Selection

/http://www.51wendang.com/doc/437ec10ed908de0667a81455ONUS/METREnglishEspanolFrancaisPortuguesTranslated

TABLE

POINT

NO.

TEST METR LANG

/Adisplay_testDISPCONFDISPUNIT

APPENDIX B — NAVIGATOR  DISPLAY TABLES (cont)

— CONFIGURATION (cont)

CONFIGURATIONUnit TypeUnit Size

Fan on Varifan Cir A

= Water Cooled4 = Heat Machine0 to 1800

(nominal size)0-8

cooled

TABLEFACTORYFACTORY

supported.0: No low ambient

head pressure control1:low ambient temperature head pressure control

supported.0: No low ambient

head pressure control1: low ambient temperature head pressure control

supported.0: No low ambient

head presshttp://www.51wendang.com/doc/437ec10ed908de0667a81455ure control1: low ambient temperature head pressure controlAcceptable values 200, 230, 380, 460, and 575YES

supported.

POINTunit_typunitsizevarfan_a

NO.

TYPE TONS VAR.A

VAR.B

Fan on Varifan Cir BX0-8FACTORYvarfan_b

VAR.C

Fan on Varifan Cir CX0-8FACTORYvarfan_c

VOLT 60HZ STAR Y.D. MTA.A R.MT.A MTA.B R.MT.B MTA.C R.MT.C C.SW.A R.CSA C.SW.B R.CSB C.SW.C R.CSC RECL BOIL EMM PAS.E PASS CO.HT CON.V HGBP MCHX HI.TI H.KIT PA.NB VLT RPM H.CON FLUD CFLU MOP HP.TH SHP.A SHP.B SHP.C HTR EWTO AU.SM LLWT LOSP FL.SP HD.PG HD.DG HD.IG F.LOA AVFA AVFB AVFC EWT.S MAXL

Supply Voltage60 Hz FrequencySoft Starter Select

Delta T Start SelectMust Trip Amps Cir ARead Must Trip Amps AMust Trip Amps Cir BRead Must Trip Amps BMust Trip Amps Cir CRead Must Trip Amps CS1 Config Switch Cir ARead S1 Config Switch AS1 Chttp://www.51wendang.com/doc/437ec10ed908de0667a81455onfig Switch Cir BRead S1 Config Switch BS1 Config Switch Cir CRead S1 Config Switch CHeat Reclaim SelectBoiler Command SelectEMM Module InstalledPassword EnableFactory PasswordCooler Heater SelectCondenser Valve SelectHot Gas Bypass SelectMCHX Exchanger SelectHigh Tiers Display SelectHydronic Kit SelectionCooler Pass NumberVLT Fan Drive SelectVLT Fan Drive RPMHigh Condensing Select

CONFIGURATIONSCooler Fluid TypeCondenser Fluid TypeEXV MOP SetpointHigh Pressure ThresholdCir A Superheat SetpCir B Superheat SetpCir C Superheat SetpCooler Heater DT SetpEntering Water ControlAuto Start When SM LostBrine Minimum Fluid TempBrine Freeze SetpointBrine Flow Switch SetpVarifan Proportion GainVarifan Derivative GainVarifan Integral GainFast Load SelectFan A Drive AttachFan B Drive AttachFan C Drive Attach

Probe on Cir A SideMax Condenser LWT 45DC

(volt)

, 230, 380, 460, 575NO/YESNO/YESNO/YES0 to 1http://www.51wendang.com/doc/437ec10ed908de0667a814555000 to 15000 to 15000 to 15000 to 15000 to 15000 to 2550 to 2550 to 2550 to 2550 to 2550 to 255NO/YESNO/YESNO/YESENBL/DSBL1 to 0150NO/YESNO/YESNO/YESNO/YESNO/YESNO/YES1-3NO/YES

_60Hsoftstarwye_deltcpa_mtaccpa_mtamcpb_mtaccpb_mtamcpc_mtaccpb_mtamcpa_s1_ccpa_s1_mcpb_s1_ccpb_s1_mcpc_s1_ccpc_s1_mrecl_optehs_selemm_nrcppass_enbfac_passheat_selcond_valhgbp_selmchx_selhighdisp

(amps)XXX (amps)XXX (amps)XXX (amps)XXX (amps)XXX (amps)XXX (amps)XXX (amps)XXX (amps)XXX (amps)XXX (amps)XXX (amps)

supported.Not supported.

supported.Not supported.

supported.NONot supported.NO

supported.

supported.NOhttp://www.51wendang.com/doc/437ec10ed908de0667a81455Not supported.NO

supported.NONENot supported.0

.0275.514.414.4

supported.14.4Not supported.2.0

.0NONO38

supported.1

.00.40.20

supported.NONot supported.NONot supported.NO

, 79

.X40-60 F(deg F/deg C)(4.4-15.6 C)XXX.X (psi/kPa)250-280 psi

(1724-1930 kPa)

.X ( F/ C)3-14 F

(1.7-7.8 C)

.X ( F/ C)3-14 F

(1.7-7.8 C)

.X ( F/ C)3-14 F

(1.7-7.8 C)

.X ( F/ C)0.5-9 F

(0.3-5.0 C)NO/YESNO/YES

.X–20-38 F(deg F/deg C)(–28.9-3.3 C)XX.X–20-50 F(deg F/deg C)(–20-10 C)

-60

.X–10-10XX.X–10-10XX.X–10-10

-4

/YESNO/YESNO/YESNO/YESNO/YES

_typcond_typ

, 43, 44, 58

SERVICE1SERVICE1SERVICE1SERVICE1SERVICE1SERVICE1SERVICE1SERVICE1SERVICE1SERVICE1SERhttp://www.51wendang.com/doc/437ec10ed908de0667a81455VICE1SERVICE1SERVICE1

_sphp_thsh_sp_ash_sp_bsh_sp_cheaterspewt_optauto_smlowestspflow_sphd_pghd_dghd_igfastload

, 2725

, 43, 44, 58

FACTORYewt_cirAmax_clwt

APPENDIX B — NAVIGATOR  DISPLAY TABLES (cont)

— CONFIGURATION (cont)

CCNA CCNB BAUD

CONFIGURATIONCCN AddressCCN Bus NumberCCN Baud Rate

-2390-2392400480096001920038400EqualStagedAutomaticCir A LeadsCir B LeadsCir C LeadsENBL/DSBL1 to 15

/DSBLNo Pump1 Pump Only2 Pumps AutoPMP 1 ManualPMP 2 ManualNo Pump1 Pump Only2 Pumps AutoPMP 1 ManualPMP 2 Manual24 to 3000NO-YESNO-YESNO-YES00.00-23.5900-00-23.590-100NO-YESNO/YES0 to 5000No ResetOut Air TempDelta T Temp4-20 mA InputSpace TempNo ResetOut Air TempDelta T Temp4-20 mA InputNoneSwitch

-20 mA InputDisableMasterSlave1-236

Lead Lag if Fail Runtime Sel40http://www.51wendang.com/doc/437ec10ed908de0667a81455-4002-303-180-150OFF if U stpON if U stp0-60NO/YES

TABLEN/AN/AN/A

POINTCCNACCNBBAUD

NO.

LOAD LLCS RL.S DELY ICE.M HPUM

Sequence SelectLead/Lag Circuit Select

_cirseq_typ

Load SelectMinutes Off TimeIce Mode Enable

Pumps Sequence

(Minutes)

PUMP

supported.Not supported.Not supported.

_seloff_on_dice_cnfghpum_seq35294047

PUMP

Pumps SequenceNO PUMPUSERpump_seq28, 29

ROT.P PM.PS P.SBY P.LOC LS.ST LS.ND LS.LT RV.AL OA.TH CUR.S CUR.F CRST

Rotation DelayPeriodic Pump StartStop Pump In StandbyFlow Checked if Pmp OffNight Low Noise StartNight Low Noise EndLow Noise Capacity LimReverse Alarms RelayHeat Mode OAT Threshold

://www.51wendang.com/doc/437ec10ed908de0667a81455rXXXX (hours)

.XXXX.XXXXX (%)XX.X

(deg F/deg C)

supported.

NONOYES00.0000.00100NO5 FNO2000NO RESET

_delpump_perpump_sbypump_locnh_startnh_endnh_limital_reverheat_thcurr_selcurr_fulcr_sel

, 5728, 29, 5828, 29

Limit SelectCurrent Limit at 100%XXXXRESET, DEMAND LIMIT, MASTER/SLAVECooling Reset Type

, 404035, 57

HRST DMDC DMMX DMZE MSSL SLVA LLBL LLBD LLDY LL.ER LAG.M LAGP LPUL SERI

Reset TypeNO RESETUSERhr_sel

Limit SelectmA for 100% Demand LimitmA for 0% Demand LimitMaster/Slave SelectSlave Address

/Lag Balance SelectLead/Lag Balance DeltaLead/Lag DelayStart if Error HigherLag Minimum Running TimeLag Unit Pump SelectLead Pulldown TimeChillers in Series

.X (mA)XX.X (mA)

.00.0

Lead1681040

if U sthttp://www.51wendang.com/doc/437ec10ed908de0667a81455p0NO

_SLVMST_SLVMST_SLVMST_SLVMST_SLVMST_SLVMST_SLVMST_SLVMST_SLVMST_SLV

_sellim_mxlim_zems_selslv_addrll_balll_bal_dlsrt_timstart_dtlag_minilag_pumplead_pulll_serie

, 40, 5540, 4140, 4130-3430-3430-34, 5630-34, 5630-34, 5630-3430-3430-34, 5630-34, 5630-34

(hours)XX (minutes)XX.X

(deg F/deg C)XXX(min)XX (minutes)

APPENDIX B — NAVIGATOR  DISPLAY TABLES (cont)

— TIMECLOCK

OF DAYHour and MinuteDAY, DATEMonth

.XX

.00-23.591=January2=February3=March4=April5=May6=June7=July8=August9=September10=October11=November12=December1-31

=Monday2=Tuesday3=Wednesday4=Thursday5=Friday6=Saturday7=Sunday00-9900:00-23:5900:00-23:59NO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YES00:00-23:5900:00-23:59NO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YES00:00-23:5900:00-23:59NO/YESNO/Yhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YES00:00-23:5900:00-23:59NO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YES00:00-23:5900:00-23:59NO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YES00:00-23:5900:00-23:59NO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YES

TABLEN/AN/A

POINTHH.MMMNTH

.

HH.MM

MNTH

DOM DAY

of MonthDay of Week

/AN/ADOMDAY

YEAR

PER.1

PER.1 OCC.1 PER.1 UNO.1 PER.1 MON.1 PER.1 TUE.1 PER.1 WED.1 PER.1 THU.1 PER.1 FRI.1 PER.1 SAT.1 PER.1 SUN.1 PER.1 HOL.1 PER.2

PER.2 OCC.2 PER.2 UNO.2 PER.2 MON.2 PER.2 TUE.2 PER.2 WED.2 PER.2 THU.2 PER.2 FRI.2 PER.2 SAT.2 PER.2 SUN.2 PER.2 HOL.2 PER.3

PER.3 OCC.3 PER.3 UNO.3 PER.3 MON.3 PER.3 TUE.3 PER.3 WED.3 PER.3 THU.3 PER.3 FRI.3 PER.3 SAT.3 PER.3 SUN.3 PER.3 HOL.3 PER.4

PER.4 Ohttp://www.51wendang.com/doc/437ec10ed908de0667a81455CC.4 PER.4 UNO.4 PER.4 MON.4 PER.4 TUE.4 PER.4 WED.4 PER.4 THU.4 PER.4 FRI.4 PER.4 SAT.4 PER.4 SUN.4 PER.4 HOL.4 PER.5

PER.5 OCC.5 PER.5 UNO.5 PER.5 MON.5 PER.5 TUE.5 PER.5 WED.5 PER.5 THU.5 PER.5 FRI.5 PER.5 SAT.5 PER.5 SUN.5 PER.5 HOL.5 PER.6

PER.6 OCC.6 PER.6 UNO.6 PER.6 MON.6 PER.6 TUE.6 PER.6 WED.6 PER.6 THU.6 PER.6 FRI.6 PER.6 SAT.6 PER.6 SUN.6 PER.6 HOL.6

of CenturySCHEDULE 1

1 Occ/Unocc SelOccupied TimeUnoccupied TimeMonday SelectTuesday SelectWednesday SelectThursday SelectFriday SelectSaturday SelectSunday SelectHoliday Select

2 Occ/Unocc SelOccupied TimeUnoccupied TimeMonday SelectTuesday SelectWednesday SelectThursday SelectFriday SelectSaturday SelectSunday SelectHoliday Select

3 Occ/Unocc SelOccupied TimeUnoccupied TimeMonday SelectTuesday SelectWednesday SelectThursday SelectFriday SelectSaturday SelectSunday SelectHoliday Select

4 Occ/http://www.51wendang.com/doc/437ec10ed908de0667a81455Unocc SelOccupied TimeUnoccupied TimeMonday SelectTuesday SelectWednesday SelectThursday SelectFriday SelectSaturday SelectSunday SelectHoliday Select

5 Occ/Unocc SelOccupied TimeUnoccupied TimeMonday SelectTuesday SelectWednesday SelectThursday SelectFriday SelectSaturday SelectSunday SelectHoliday Select

6 Occ/Unocc SelOccupied TimeUnoccupied TimeMonday SelectTuesday SelectWednesday SelectThursday SelectFriday SelectSaturday SelectSunday SelectHoliday Select

.XXXX.XX

://www.51wendang.com/doc/437ec10ed908de0667a81455cibleforcibleforcibleforcibleforcibleforcibleforcibleforcible

/AOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01SOCC1P01S

UNOCTOD1DOW1DOW1DOW1DOW1DOW1DOW1DOW1DOW1OCCTOD2UNOCTOD2DOW2DOW2DOW2DOW2DOW2DOW2DOW2DOW2OCCTOD3UNOCTOD3DOW3DOW3DOW3DOW3DOW3DOW3DOW3DOW3OCCTOD4UNOCTOD4DOW4DOW4DOW4DOW4DOW4DOW4DOW4DOW4OCCTOD5UNOCTOD5DOW5DOW5DOW5DOW5DOW5DOW5DOW5DOW5OCCTOD6UNOCTOD6DOW6DOW6DOW6DOW6DOW6DOW6DOW6DOW6

http://www.51wendang.com/doc/437ec10ed908de0667a8145542424242424242424242424

.XXXX.XX

.XXXX.XX

.XXXX.XX

.XXXX.XX

.XXXX.XX

APPENDIX B — NAVIGATOR  DISPLAY TABLES (cont)

— TIMECLOCK (cont)

1

7 Occ/Unocc SelOccupied TimeUnoccupied TimeMonday SelectTuesday SelectWednesday SelectThursday SelectFriday SelectSaturday SelectSunday SelectHoliday Select

8 Occ/Unocc SelOccupied TimeUnoccupied TimeMonday SelectTuesday SelectWednesday SelectThursday SelectFriday SelectSaturday SelectSunday SelectHoliday SelectSCHEDULE 2

1 Occ/Unocc SelOccupied TimeUnoccupied TimeMonday SelectTuesday SelectWednesday SelectThursday SelectFriday SelectSaturday SelectSunday SelectHoliday Select

2 Occ/Unocc SelOccupied TimeUnoccupied TimeMonday SelectTuesday SelectWednesday SelectThursday SelectFriday SelectSaturday SelectSunday SelectHoliday Sehttp://www.51wendang.com/doc/437ec10ed908de0667a81455lect

3 Occ/Unocc SelOccupied TimeUnoccupied TimeMonday SelectTuesday SelectWednesday SelectThursday SelectFriday SelectSaturday SelectSunday SelectHoliday Select

4 Occ/Unocc SelOccupied TimeUnoccupied TimeMonday SelectTuesday SelectWednesday SelectThursday SelectFriday SelectSaturday SelectSunday SelectHoliday Select

5 Occ/Unocc SelOccupied TimeUnoccupied TimeMonday SelectTuesday SelectWednesday SelectThursday SelectFriday SelectSaturday SelectSunday SelectHoliday Select

6 Occ/Unocc SelOccupied TimeUnoccupied TimeMonday SelectTuesday SelectWednesday SelectThursday SelectFriday SelectSaturday SelectSunday SelectHoliday Select

://www.51wendang.com/doc/437ec10ed908de0667a81455eforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcible

TABLE

POINT

.

PER.7

PER.7 OCC.7 PER.7 UNO.7 PER.7 MON.7 PER.7 TUE.7 PER.7 WED.7 PER.7 THU.7 PER.7 FRI.7 PER.7 SAT.7 PER.7 SUN.7 PER.7 HOL.7 PER.8

PER.8 OCC.8 PER.8 UNO.8 PER.8 MON.8 PER.8 TUE.8 PER.8 WED.8 PER.8 THU.8 PER.8 FRI.8 PER.8 SAT.8 PER.8 SUN.8 PER.8 HOL.8 PER.1

PER.1 OCC.1 PER.1 UNO.1 PER.1 MON.1 PER.1 TUE.1 PER.1 WED.1 PER.1 THU.1 PER.1 FRI.1 PER.1 SAT.1 PER.1 SUN.1 PER.1 HOL.1 PER.2

PER.2 OCC.2 PER.2 UNO.2 PER.2 MOhttp://www.51wendang.com/doc/437ec10ed908de0667a81455N.2 PER.2 TUE.2 PER.2 WED.2 PER.2 THU.2 PER.2 FRI.2 PER.2 SAT.2 PER.2 SUN.2 PER.2 HOL.2 PER.3

PER.3 OCC.3 PER.3 UNO.3 PER.3 MON.3 PER.3 TUE.3 PER.3 WED.3 PER.3 THU.3 PER.3 FRI.3 PER.3 SAT.3 PER.3 SUN.3 PER.3 HOL.3 PER.4

PER.4 OCC.4 PER.4 UNO.4 PER.4 MON.4 PER.4 TUE.4 PER.4 WED.4 PER.4 THU.4 PER.4 FRI.4 PER.4 SAT.4 PER.4 SUN.4 PER.4 HOL.4 PER.5

PER.5 OCC.5 PER.5 UNO.5 PER.5 MON.5 PER.5 TUE.5 PER.5 WED.5 PER.5 THU.5 PER.5 FRI.5 PER.5 SAT.5 PER.5 SUN.5 PER.5 HOL.5 PER.6

PER.6 OCC.6 PER.6 UNO.6 PER.6 MON.6 PER.6 TUE.6 PER.6 WED.6 PER.6 THU.6 PER.6 FRI.6 PER.6 SAT.6 PER.6 SUN.6 PER.6 HOL.6

.XXXX.XX

:00-23:5900:00-23:59NO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YES00:00-23:5900:00-23:59NO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YES00:00-23:5900:00-23:59NO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YES00:00-23:5900:00-23:59NO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YEShttp://www.51wendang.com/doc/437ec10ed908de0667a81455NO/YES00:00-23:5900:00-23:59NO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YES00:00-23:5900:00-23:59NO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YES00:00-23:5900:00-23:59NO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YES00:00-23:5900:00-23:59NO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YES

.XXXX.XX

SOCCP01SOCCP01SOCCP01SOCCP01SOCCP01SOCCP01SOCCP01SOCCP01SOCCP01SOCCP01SOCCP01SOCCP01SOCCP01SOCCP01SOCCP01SOCCP01SOCCP01SOCCP01SOCCP01SOCCP01SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02SOCC2P02S

://www.51wendang.com/doc/437ec10ed908de0667a81455OCCTOD7UNOCTOD7DOW7DOW7DOW7DOW7DOW7DOW7DOW7DOW7OCCTOD8UNOCTOD8DOW8DOW8DOW8DOW8DOW8DOW8DOW8DOW8OCCTOD1UNOCTOD1DOW1DOW1DOW1DOW1DOW1DOW1DOW1DOW1OCCTODUNOCTOD2DOW2DOW2DOW2DOW2DOW2DOW2DOW2DOW2OCCTODUNOCTOD3DOW3DOW3DOW3DOW3DOW3DOW3DOW3DOW3OCCTOD4UNOCTOD4DOW4DOW4DOW4DOW4DOW4DOW4DOW4DOW4OCCTOD5UNOCTOD5DOW5DOW5DOW5DOW5DOW5DOW5DOW5DOW5OCCTOD6UNOCTOD6DOW6DOW6DOW6DOW6DOW6DOW6DOW6DOW6

.XXXX.XX

.XXXX.XX

.XXXX.XX

.XXXX.XX

.XXXX.XX

.XXXX.XX

APPENDIX B — NAVIGATOR  DISPLAY TABLES (cont)

— TIMECLOCK (cont)

7 Occ/Unocc SelOccupied TimeUnoccupied TimeMonday SelectTuesday SelectWednesday SelectThursday SelectFriday SelectSaturday SelectSunday SelectHoliday Select

8 Occ/Unocc SelOccupied TimeUnoccupied TimeMohttp://www.51wendang.com/doc/437ec10ed908de0667a81455nday SelectTuesday SelectWednesday SelectThursday SelectFriday SelectSaturday SelectSunday SelectHoliday SelectHOLIDAYS*

1 ConfigurationHoliday Start Month

.XXXX.XX

:00-23:5900:00-23:59NO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YES00:00-23:5900:00-23:59NO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YESNO/YES1=January2=February3=March4=April5=May6=June7=July8=August9=September10=October11=November12=December1 to 311 to 99

.1 MON.1See

.1 DAY.1See

.1 DUR.1See

.1 MON.1See

.1 DAY.1See

.1 DUR.1

/YESNO/YESNO/YES0-65,5000-65,5000-65,5000-65,5000-65,5000-65,5000-65,5000-65,5000=Default

=Refrigerant Charge2=Water loop size3=Not used4=Pump 15=Pump 2

=Reclaim Pump (not used)7=Reclaim Pump (not used)8=Water Filter

=Compressor A Oil Filter10=Compressor B Oil Filter11=Compressor C Oil Filter12=Reset Alhttp://www.51wendang.com/doc/437ec10ed908de0667a81455l

=NODEFAULT=NODEFAULT=NODEFAULT=0DEFAULT=0DEFAULT=0DEFAULT=0DEFAULT=0DEFAULT=0DEFAULT=0DEFAULT=0DEFAULT=0COMMENT

TABLECCN POINTNO.forcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcibleforcible

_01OCC2P02S

UNOCTOD7DOW7DOW7DOW7DOW7DOW7DOW7DOW7DOW7OCCTOD8UNOCTOD8DOW8DOW8DOW8DOW8DOW8DOW8DOW8DOW8HOL_MON

.7

PER.7 OCC.7 PER.7 UNO.7 PER.7 MON.7 PER.7 TUE.7 PER.7 WED.7 PER.7 THU.7 PER.7 FRI.7 PER.7 SAT.7 PER.7 SUN.7 PER.7 HOL.7 PER.8

PER.8 OCC.8 PER.8 UNO.8 PER.8 MON.8 PER.8 TUE.8 PER.8 WED.8 PER.8 THU.8 PER.8 FRI.8 PER.8 SAT.8 PER.8 SUN.8 PER.8 HOL.8 HOL.1

HOL.1 MON.1

.XXXX.XX

HOL.1 DAY.1 HOL.1 DUR.1 HOL.1 HOL.2 HOL.1 MON.2 HOL.2 DAY.2 HOL.2 DUR.2HOL.16HO.16 HOL.16 MO.16 HOL.16 DA.16 HOL.16 DU.16 AL.http://www.51wendang.com/doc/437ec10ed908de0667a81455SV CHRG WATE PMP.1 PMP.2 PMP.3 PMP.4 W.FIL A.FIL B.FIL C.FIL RS.SV

Start Day

Duration in DaysHoliday 2 ConfigurationHoliday Start MonthHoliday Start DayHoliday Duration in DaysHoliday 16 ConfigurationHoliday Start MonthHoliday Start DayHoliday Duration in Days

_01HOLDY_01HOLDY_02HOLDY_02HOLDY_02HOLDY_16HOLDY_16HOLDY_16MAINTCFGMAINTCFGMAINTCFGMAINTCFGMAINTCFGMAINTCFGMAINTCFGMAINTCFGMAINTCFGMAINTCFGMAINTCFGSERMAINT

_DAYHOL_LENHOL_MONHOL_DAYHOL_LEN

MAINTENANCE CONFIGURATIONService Warning SelectRefrigerant ChargeWater Loop SizePump 1 (days)XXXX (days)Pump 2 (days)XXXX (days)Cond Pump 1 (days)XXXX (days)Cond Pump 2 (days)XXXX (days)Water Filter (days)XXXX (days)Comp A Oilhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 Filter (days)XXXX (days)Comp B Oil Filter (days)XXXX (days)Comp C Oil Filter (days)XXXX (days)Servicing Alert Reset

_alertcharge_awloop_cpump1_cpump2_chpump1_chpump2_cwfilte_cofilta_cofiltb_cofiltc_cs_reset

*Holidays range from 1-16. Item has same structure, with the only difference being the two-number identifier.

APPENDIX B — NAVIGATOR  DISPLAY TABLES (cont)

— OPERATING MODE

*

CONTROL TYPEOperating Control TypeSetpoint Select

CtrlTime SchedCCN ControlSetpoint OccSetpoint1Setpoint24-20mA SetpDual Setp SwCoolingHeating

ChgoverHeat Cool Sw0-320-320-320-320-320-32

TABLEN/AN/A

POINTN/AN/A

.24, 2525-27

OPER SP.SE

= Switch forcibleCtrl

= Setpoint Occ

HC.SE

://www.51wendang.com/doc/437ec10ed908de0667a81455Heat Cool SelectDefault = CoolingforcibleGENUNITHC_SEL25

MD01 MD02 MD03 MD04 MD05 MD06

*

MODESFirst Active ModeSecond Active ModeThird Active ModeFourth Active ModeFifth Active ModeSixth Active Mode

*Up to six current operating modes will be displayed.NOTE: See Operating Modes starting on page 56.

— ALARMS

.ALMALRM

*

ALL CURRENT ALARMCURRENTLY ACTIVE ALARMSCurrent Alarm 1Current Alarm 2Current Alarm 3Current Alarm 4Current Alarm 5ALARM HISTORYAlarm History #1Alarm History #2Alarm History #49Alarm History #50

/YES

TABLEN/AGENUNITGENUNITGENUNITGENUNITGENUNITALRMHISTALRMHISTALRMHISTALRMHIST

POINTN/Aalarm_1alarm_2alarm_3alarm_4alarm_5alm_history_01alm_history_02alm_history_49alm_history_50

.

.ALhttp://www.51wendang.com/doc/437ec10ed908de0667a81455M**

*Expanded display will be actual alarm description. History of up to five past alarms will be displayed.**History of fifty past alarms will be displayed.

APPENDIX C — CCN TABLES

DISPLAY TABLES

_AN

NAME

A ANALOG VALUESPercent Total CapacityDischarge PressureSuction PressureEconomizer PressureOil Pressure

Pressure DifferenceMotor Current

TemperatureDischarge Gas TempEconomizer Gas Temp

Condensing TmpSaturated Suction TempCompressor Suction TempEXV Position

Press Actuator PosCIRCUIT A DISCRETECompressor OutputSlide Valve 1 OutputSlide Valve 2 OutputOil Heater OutputOil Solenoid OutputOil Level Input

Cooling SolenoidHot Gas Bypass OutputFANS OUTPUTFan Output DO # 1Fan Output DO # 2Fan Output DO # 3Fan Output DO # 4Fan Output DO # 5Fan Output DO # 6Fan Output DO # 7Fan Output Dhttp://www.51wendang.com/doc/437ec10ed908de0667a81455O # 8Fan Staging NumberMISCELLANEOUSBall Valve PositionBall Valve Closing OutBall Valve Opening Out4 Way Refrigerant Valve*

B ANALOG VALUESPercent Total CapacityDischarge PressureSuction PressureEconomizer PressureOil Pressure

Pressure DifferenceMotor Current

TemperatureDischarge Gas TempEconomizer Gas Temp

Condensing TmpSaturated Suction TempCompressor Suction TempEXV Position

Press Actuator PosCIRCUIT B DISCRETECompressor OutputSlide Valve 1 OutputSlide Valve 2 OutputOil Heater OutputOil Solenoid OutputOil Level Input

Cooling SolenoidHot Gas Bypass OutputFANS OUTPUTFan Output DO # 1Fan Output DO # 2Fan Output DO # 3Fan Output DO # 4Fan Output DO # 5Fan Output DO # 6Fan Output DO # 7Fan Output DO # 8Fan Staging NumberMISCELLANEOUSBall Valve PositionBall Valve Closing OutBall Valve Opening Out4 Way Refrigerant Valve*

- 100nnn.nnnn.nnnhttp://www.51wendang.com/doc/437ec10ed908de0667a81455n.nnnn.nnnn.nnnn.nnnnnnnnnnnnn&#177;nnn.n&#177;nnn.n&#177;nnn.n0 - 1000 - 100ON/OFFON/OFFON/OFFON/OFFON/OFFLow/HighON/OFFON/OFFON/OFFON/OFFON/OFFON/OFFON/OFFON/OFFON/OFFON/OFF0-10OPEN/CLSEON/OFFON/OFFON/OFF0 - 100nnn.nnnn.nnnn.nnnn.nnnn.nnnn.nnnnnnnnnnnnn&#177;nnn.n&#177;nnn.n&#177;nnn.n0-1000-100ON/OFFON/OFFON/OFFON/OFFON/OFFLow/HighON/OFFON/OFFON/OFFON/OFFON/OFFON/OFFON/OFFON/OFFON/OFFON/OFF0-10OPEN/CLSEON/OFFON/OFFON/OFF

%psipsipsipsipsiAMPS&#176;F&#176;F&#176;F&#176;F&#176;F&#176;F%%UNITS%psipsipsipsipsiAMPS&#176;F&#176;F&#176;F&#176;F&#176;F&#176;F%%

NAMECAPA_TDP_ASP_A

_P_AOP_ADOP_A

_ACP_TMP_ADGT_AECO_TP_ASCT_ASST_ASUCT_T_AEXV_Ahd_pos_aCOMP_ASLID_1_ASLID_2_AOIL_HT_AOIL_SL_AOIL_L_AGASCOOLAHGBP_Afan_a1fan_a2fan_a3fan_a4fan_a5fan_a6fan_a7fan_a8FAN_ST_AISO_REFAISO_CL_AISO_OP_ARV_ACAPB_TDP_BSP_B

_P_BOP_BDOP_B

_BCP_TMP_BDGT_BECO_TP_BSCT_BSST_BSUCT_T_BEXV_Bhd_pos_bCOMPhttp://www.51wendang.com/doc/437ec10ed908de0667a81455_BSLID_1_BSLID_2_BOIL_HT_BOIL_SL_BOIL_L_BGASCOOLBHGBP_Bfan_b1fan_b2fan_b3fan_b4fan_b5fan_b6fan_b7fan_b8FAN_ST_BISO_REFBISO_CL_BISO_OP_BRV_B

STATUS

_D

_AN

_D

*Not supported.

APPENDIX C — CCN TABLES (cont)

DISPLAY TABLES (cont)

_AN*

NAME

C ANALOG VALUESPercent Total CapacityDischarge PressureSuction PressureEconomizer PressureOil Pressure

Pressure DifferenceMotor Current

TemperatureDischarge Gas TempEconomizer Gas Temp

Condensing TmpSaturated Suction TempCompressor Suction TempEXV Position

Press Actuator PosCIRCUIT C DISCRETECompressor OutputSlide Valve 1 OutputSlide Valve 2 OutputOil Heater OutputOil Solenoid OutputOil Level Input

Cooling SolenoidHot Gas Bypass OutputFANS OUTPUTFan Output DO # 1Fan Output DO # 2Fan Output DO # 3Fhttp://www.51wendang.com/doc/437ec10ed908de0667a81455an Output DO # 4Fan Output DO # 5Fan Output DO # 6Fan Output DO # 7Fan Output DO # 8Fan Staging NumberMISCELLANEOUSBall Valve PositionBall Valve Closing OutBall Valve Opening OutFree Cool A Pump HoursFree Cool B Pump HoursCircuit A Defrost NumberCircuit B Defrost NumberCircuit A Fan #1 HoursCircuit A Fan #2 HoursCircuit A Fan #3 HoursCircuit A Fan #4 HoursCircuit A Fan #5 HoursCircuit A Fan #6 HoursCircuit A Fan #7 HoursCircuit A Fan #8 HoursCircuit A Fan #9 HoursCircuit A Fan #10 HoursCircuit B Fan #1 HoursCircuit B Fan #2 HoursCircuit B Fan #3 HoursCircuit B Fan #4 HoursCircuit B Fan #5 HoursCircuit B Fan #6 HoursCircuit B Fan #7 HoursCircuit B Fan #8 HoursCircuit B Fan #9 HoursCircuit B Fan #10 HoursCircuit C Fan #1 HoursCircuit C Fan #2 HoursCircuit C Fan #3 HoursCircuit C Fan #4 HoursCircuit C Fan #5 HoursCircuit C Fan #6 HoursCircuit C Fan #7 HoursCircuit C Fan #8 Hours

-100nnn.nnnn.nnnn.nnnn.nnnn.nnnn.nnnnhttp://www.51wendang.com/doc/437ec10ed908de0667a81455nnnnnnnnn&#177;nnn.n&#177;nnn.n&#177;nnn.n0-1000-100ON/OFFON/OFFON/OFFON/OFFON/OFFLow/HighON/OFFON/OFFON/OFFON/OFFON/OFFON/OFFON/OFFON/OFFON/OFFON/OFF0-10OPEN/CLSEON/OFFON/OFFnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnn

——hourshourshourshourshourshourshourshourshourshourshourshourshourshourshourshourshourshourshourshourshourshourshourshourshourshourshourshoursUNITS%psipsipsipsipsiAMPS&#176;F&#176;F&#176;F&#176;F&#176;F&#176;F%%

NAMECAPC_TDP_CSP_C

_P_COP_CDOP_C

_CCP_TMP_CDGT_CECO_TP_CSCT_CSST_CSUCT_T_CEXV_Chd_pos_cCOMP_CSLID_1_CSLID_2_COIL_HT_COIL_SL_COIL_L_CGASCOOLCHGBP_Cfan_c1fan_c2fan_c3fan_c4fan_c5fan_c6fan_c7fan_c8

_ST_CISO_REFCISO_CL_CISO_OP_Chr_fem_ahr_fem_bub_def_aub_def_bhr_fana1hr_fana2hr_fana3hr_fana4hr_fana5hr_fana6hr_fana7hr_fana8hr_fana9hrfana1http://www.51wendang.com/doc/437ec10ed908de0667a814550hr_fanb1hr_fanb2hr_fanb3hr_fanb4hr_fanb5hr_fanb6hr_fanb7hr_fanb8hr_fanb9hrfanb10hr_fanc1hr_fanc2hr_fanc3hr_fanc4hr_fanc5hr_fanc6hr_fanc7hr_fanc8

STATUS

_D*

HOURS*

*Not supported.

APPENDIX C — CCN TABLES (cont)

DISPLAY TABLES (cont)

NAME

TypeControl Type

-Off-Local Off

(Navigator Display= SW1 Switch=Opened)L-On-Local On

-Sched-Local On/Off State based on Time SchedulesCCN-Unit is in CCN Control

-On/Off Based on Remote Contact (not applied to Navigator Display)

-Unit Operation in Lead/Lag and it is a MasterLocalCCNRemote0 = Off

= Running2 = Stopping3 = Delay4 = Tripout5 = Ready6 = Override7 = Defrost8 = Run Test9 = Test

/DisableYes/No0-150 = Cool1 = Heat2 = Stand-by3 = Both0 = Cool1 = Heat2 = AutoYes/NoYes/No0 = Normal1 = Parhttp://www.51wendang.com/doc/437ec10ed908de0667a81455tial2 = Shutdownnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnn&#177;nnn.nYes/NoSetpt 1Setpt 2Ice_sp4-20mAAuto&#177;nnn.n&#177;nnn.n&#177;nnn.n

/DisableYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/NoYes/No

NAMEOPER_TYP

STATUS

_typeSTATUS

Status

Chiller Start/StopChiller Occupied?Minutes Left for StartHeat/Cool Status

_S_SCHIL_OCCmin_leftHEATCOOL

/Cool SelectHeat Reclaim SelectFree Cooling SelctAlarm State

Alarm 1Current Alarm 2Current Alarm 3Current Alarm 4Current Alarm 5

Total CapacityActive Demand Limit ValLag Capacity Limit ValueActual Chiller CurrentChiller Current LimitCurrent SetpointSetpoint Occupied?Setpoint Control

_SEhttp://www.51wendang.com/doc/437ec10ed908de0667a81455LRECL_SELFC_DSBLEALMalarm_1alarm_2alarm_3alarm_4alarm_5CAP_TDEM_LIMLAG_LIMTOT_CURRCURR_LIMSP

_OCCsp_ctrl

*forcible

%%%ampsamps&#176;F

*forcible forcibleforcible

Point

Water TempExternal TemperatureEmergency Stop

Delay in EffectSecond Setpoint in UseReset in Effect

Limit ActiveRamp Loading ActiveCooler Heater ActiveCooler Pumps RotationPump Periodic StartNight Low Noise ActiveSystem Manager ActiveMaster Slave ActiveAuto Changeover ActiveFree Cooling ActiveReclaim Active

Heat Active

Low EWT LockoutCondenser Pumps RotationIce Mode in Effect

Active On Cir ADefrost Active On Cir BLow Suction Circuit ALow Suction Circuit BLow Suction Circuit CHigh DGT Circuit AHigh DGT Circuit BHigh DGT Circuit C

Pres Override Cir AHigh Pres Override Cir BHigh Pres Overridhttp://www.51wendang.com/doc/437ec10ed908de0667a81455e Cir CLow Superheat Circuit ALow Superheat Circuit BLow Superheat Circuit C

&#176;F&#176;F&#176;F————————————————————————————————CTRL_PNTCTRL_WTOAT

_01Mode_02Mode_03Mode_04Mode_05Mode_06Mode_07Mode_08Mode_09Mode_10Mode_11Mode_12Mode_13Mode_14Mode_15Mode_16Mode_17Mode_18Mode_19Mode_20Mode_21Mode_22Mode_23Mode_24Mode_25Mode_26Mode_27Mode_28Mode_29Mode_30Mode_31Mode_32

*forcible

*Not supported.

The forced value will be used.

APPENDIX C — CCN TABLES (cont)

DISPLAY TABLES (cont)

_TST1

NAME

Test EnableCircuit A EXV PositionCircuit B EXV PositionCircuit C EXV Position

A Economizer EXV PosCir B Economizer EXV PosCir C Economizer EXV PosCircuit A Fan StagesCircuit B Fan StagesCircuit C Fan Stages

A Head Press SpeedCircuit B Head Press SpeedCircuit C Head Press SpeedCircuit A Oil HeaterCihttp://www.51wendang.com/doc/437ec10ed908de0667a81455rcuit A Oil SolenoidCircuit A Slide Valve 1Circuit A Slide Valve 2Cir A Heater Ball ValveCir A Hot Gas BypassCir A DGT Cool SolenoidCircuit B Oil HeaterCircuit B Oil SolenoidCircuit B Slide Valve 1Circuit B Slide Valve 2Cir A Heater Ball ValveCir B Hot Gas BypassCir B DGT Cool SolenoidCircuit C Oil HeaterCircuit C Oil SolenoidCircuit C Slide Valve 1Circuit C Slide Valve 2Cir C Heater Ball ValveCir C Hot Gas BypassCooler Heater OutputWater Exchanger Pump 1Water Exchanger Pump 2Condenser Pump 1Condenser Pump 2*Chiller Ready OutputChiller Running OutputCir A Running OutputCir B Running OutputCir C Running Output*Chiller Capacity in 0-10vCustomer Shutdown OutAlarm Relay OutputAlert Relay Output

/Yes0 - 1000 - 1000 - 1000 - 1000 - 1000 - 1000-100-100-100 - 1000 - 1000 - 100Off/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/http://www.51wendang.com/doc/437ec10ed908de0667a81455OnOff/OnOff/OnOff/OnOff/On0 – 10.0Off/OnOff/OnOff/On

—%%%%%%———%%%——————————————————————————————volt———

NAMEQ_TSTRQQ_EXVAQ_EXVBQ_EXVCQ_ECO_AQ_ECO_BQ_ECO_CQ_FAN_AQ_FAN_BQ_FAN_CQ_VFANAQ_VFANBQ_VFANCQ_HT_AQ_OILS_AQ_SLI_1AQ_SLI_2AQ_BVL_AQ_HGBP_AQ_CDGT_BQ_HT_BQ_OILS_BQ_SLI_1BQ_SLI_2BQ_BVL_BQ_HGBP_BQ_CDGT_BQ_HT_CQ_OILS_CQ_SLI_1CQ_SLI_2CQ_BVL_CQ_HGBP_CQ_CL_HTQ_PMP1Q_PMP2Q_HPMP1Q_HPMP2Q_READYQ_RUNQ_RUN_AQ_RUN_BQ_RUN_CQ_CATOQ_SHUTQ_ALARMQ_ALERT

STATUS

*Not supported.

: Disable quick test: all the quick test parhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ameters shall be reset to 0.TABLEQCK_TST2*

NAME

Test Enable

Cond Enter Valve AAir Cond Leaving Valv AWater Cond Enter Valv AWater Cond Leav Valve AAir Cond Enter Valve BAir Cond Leaving Valv BWater Cond Enter Valv BWater Cond Leav Valve BHR Condenser Heater4 way Valve Circuit A4 way Valve Circuit BFree Cooling Heater

Cool A EXV PositionFree Cool B EXV PositionFree Cool A Ball ValveFree Cool B Ball Valve

/YesOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOff/OnOn/Off0 - 1000 - 100Off/OnOff/On

—————————————%%——

NAMEQ_TSTRQQ_HREA_AQ_HRLA_AQ_HREW_AQ_HRLW_AQ_HREA_BQ_HRLA_BQ_HREW_BQ_HRLW_BQ_CD_HTQ_RV_AQ_RV_BQ_FC_HTRQ_FCEXVAQ_FCEXVBQ_FCBVL_AQ_FCBVL_B

STATUS

*Not supported.

://www.51wendang.com/doc/437ec10ed908de0667a81455arNOTE: Disable quick test: all the quick test parameters shall be reset to 0.TABLESERV_TST

NAME

Test Enable*Compressor A OutputSlide Valve Capacity ACompressor B OutputSlide Valve Capacity BCompressor C OutputSlide Valve Capacity C

/YesOff/On0 - 2 Off/On0 - 2 Off/On0 - 2

———————

NAMEQ_STREQQ_CPAQ_SLIAQ_CPBQ_SLIBQ_CPCQ_SLIC

STATUS

*Yes = service test function enable. 0 = capacity frozen (unchanged).1 = capacity increase.2 = capacity decrease.

APPENDIX C — CCN TABLES (cont)

DISPLAY TABLES (cont)

*

NAME

PARAMETERSFree Cooling Disable ?LWT – OAT Delta

Cooling PowerEstimated FreeCoo PowerNext Session Allowed InCooling/FreeCool TimeoutFree Cool Conditions OK ?Free Cool Request ?://www.51wendang.com/doc/437ec10ed908de0667a81455Actuators Heaters ?CIRCUIT A

Cooling ActiveFan Staging Number3 Way Valve Position3 Way Valve StatusRefrigerant Pump OutPump Inlet Pressure Pump Outlet Pressure

Differential Pressure EXV PositionCIRCUIT B

Cooling ActiveFan Staging Number3 Way Valve Position3 Way Valve StatusRefrigerant Pump OutPump Inlet Pressure Pump Outlet Pressure

Differential Pressure EXV PositionCIRCUIT C

Cooling ActiveFan Staging Number3 Way Valve Position3 Way Valve StatusRefrigerant Pump OutPump Inlet Pressure Pump Outlet Pressure

Differential Pressure EXV Position

/No&#177;nnn.nnnnnnnnnnn

/NoYes/NoOn/Off

/No1 to 6nnn

/Closing/...On/Off&#177;nnn&#177;nnn&#177;nnnnnn.n

/No1 to 6nnn

/Closing/...On/Off&#177;nnn&#177;nnn&#177;nnnnnn.n

/No1 to 6nnn

/Closing/...On/Off&#177;nnn&#177;http://www.51wendang.com/doc/437ec10ed908de0667a81455nnn&#177;nnnnnn.n

—&#176;F&#176;F&#176;F

——-——%——kPakPakPa%——%——kPakPakPa%——%——kPakPakPa%

NAMEFC_DSBLEfc_deltacool_pwrfc_pwrfc_nextfc_tmoutfc_readyfc_reqstFC_HTRfc_on_aFAN_ST_Afc_vlv_aFC_VLV_Afc_pmp_afc_inp_afc_oup_afc_dp_aEXV_Afc_on_bFAN_ST_Bfc_vlv_bFC_VLV_Bfc_pmp_bfc_inp_bfc_oup_bfc_dp_bEXV_Bfc_on_cFAN_ST_Cfc_vlv_cFC_VLV_Cfc_pmp_cfc_inp_cfc_oup_cfc_dp_cEXV_C

*Not supported.

APPENDIX C — CCN TABLES (cont)

DISPLAY TABLES (cont)

*

NAME

Reclaim Select

Condenser PumpReclaim Condenser FlowReclaim Condenser HeaterReclaim Entering FluidReclaim Leaving FluidReclaim Fluid SetpointReclaim Valve Position

RECLAIM CIRCUIT AReclaim Status Circuit APumpdown Pressure Cir ASub Condenser Temp Cir APumpdown Saturated Tmp ASubcooling Temperature AAir Cond Entering Valv AWater Cond Enter http://www.51wendang.com/doc/437ec10ed908de0667a81455Valve AAir Cond Leaving Valve AWater Cond Leaving Val AHEAT RECLAIM CIRCUIT BReclaim Status Circuit BPumpdown Pressure Cir BSub Condenser Temp Cir BPumpdown Saturated Tmp BSubcooling Temperature BAir Cond Entering Valv BWater Cond Enter Valve BAir Cond Leaving Valve BWater Cond Leaving Val BUNIT DISCRETE INOn/Off – Remote SwitchRemote Heat/Cool SwitchCurrent Control

Reclaim Switch

Cooling Disable Switch*Remote Setpoint SwitchLimit Switch 1 StatusLimit Switch 2 Status

Override SwitchIce Done Storage SwitchCooler Flow Switch

Pump Run StatusCondenser Flow StatusRemote Interlock StatusElectrical Box Interlock*UNIT DISCRETE OUTCooler Flow Setpoint Out*Electrical Heat Stage*

Pump #1 CommandCooler Pump #2 CommandRotate Cooler Pumps ?Condenser Pump #1 OutCondenser Pump #2 Out*Rotate Condenser Pumps?*Cooler Heater Command*Shutdown Indicator StateAlarm Relay StatusAlert Relahttp://www.51wendang.com/doc/437ec10ed908de0667a81455y Status

or Running Status*Running StatusUNIT ANALOG

Entering FluidCooler Leaving Fluid

Entering FluidCondenser Leaving FluidCooler Heater Temp*Circuit C Heater Temp*Optional Space TempCHWS Temperature

/Setpnt 4-20mA SgnlLimit 4-20mA SignalChiller Capacity SignalMachine Operating HoursMachine Starts NumberCompressor A HoursCompressor A StartsCompressor B HoursCompressor B StartsCompressor C HoursCompressor C StartsWATER PUMPS

Pump #1 HoursCooler Pump #2 HoursCondenser Pump #1 HoursCondenser Pump #2 Hours*

/noOn/OffOn/OffOn/Off&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.nn

&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.nOn/OffOn/OffOn/OffOn/Offn

&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.nOn/OffOn/OffOn/OffOn/Off

/ClseOpen/Clse

, On Cool, On Heat, On AutoOpen/ClseOpen/ClseOpen/ClseOpen/ClseOpen/ClseOpen/ClseOpen/http://www.51wendang.com/doc/437ec10ed908de0667a81455ClseOpen/ClseOpen/ClseOn/OffOpen/ClseOpen/ClseOn/Off0-4/OffOn/OffOn/OffYes/NoOn/OffOn/OffYes/NoOn/OffOn/OffOn/OffOn/OffOn/OffOn/Off&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nn.n&#177;nn.n&#177;nn.nnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnn

&#176;F&#176;F&#176;F&#176;F&#176;F&#176;F&#176;F&#176;FmamavoltshourshourshourshourshourshourshourshoursUNITS

NAMERECL_SELCONDPUMPCONDFLOWcond_htrHR_EWTHR_LWTRSP

_v_poshrstat_aPD_P_Ahr_subtahr_sat_ahr_subcahr_ea_ahr_ew_ahr_la_ahr_lw_ahrstat_bPD_P_Bhr_subtbhr_sat_bhr_subcbhr_ea_bhr_ew_bhr_la_bhr_lw_bONOFF_SWHC_SWon_ctrlRECL_SWFC_SWSETP_SWLIM_SW1LIM_SW2OCC_OVSWICE_SWFLOW_SWCPUMPDEFCONDFLOWREM_ LOCKELEC_BOXSET_FLOWEHS_STEPCPUMP_1CPUMP_2ROTCPUMPHPUMP_1HPUMP_2ROTHPUMPCOOLHEATSHUTDOWNALARMOUTALERTREADYRUNNINGCOOL_EWTCOOL_LWTCOND_EWTCOND_LWTHEATERT_HEAT_CSPACETMPCHWSTEMPSP_RESETLIM_ANALCAPT_010HR_MACHst_machttp://www.51wendang.com/doc/437ec10ed908de0667a81455hHR_CP_Ast_cp_aHR_CP_Bst_cp_bHR_CP_Cst_cp_chr_cpum1hr_cpum2hr_hpum1hr_hpum2

STATUS

&#176;F&#176;F&#176;F%psi&#176;F&#176;F^F

&#176;F&#176;F^F

*Not supported.

APPENDIX C — CCN TABLES (cont)

TABLES

!CtlrID/PD5_XAXQ

NAME

NameDescription

Part NumberModel NumberSerial Number

NumberCCN Bus NumberCCN Element NumberCCN Baud Rate

/ALARMS01

Routing ControlAlarm Equipment PriorityComm Failure Retry TimeRealarm Time

System NameActivate

chars24 chars

chars16 chars20 chars12 chars24 chars0-2391-23996001920038400

-111111110-71-2401-2558 chars0=Unused

=Broadcast time, date, holiday flag http://www.51wendang.com/doc/437ec10ed908de0667a81455and OAT.

=For Standalone

. Daylight savings time &amp; holiday determi-nation will be done without broadcasting through the bus.0 to 2390 to 239Disable/Enable1 to 121 to 71 to 51 to 121 to 71 to 50-120-310-990-40/1

:00-24:0000:00-24:000/1

:00-24:0000:00-24:000/1

:00-24:0000:00-24:000/1

:00-24:0000:00-24:000/1

:00-24:0000:00-24:000/1

:00-24:0000:00-24:000/1

:00-24:0000:00-24:000/1

:00-24:0000:00-24:00

XW

-DIALOG 530XA XQ XWCSA-SR-20C47nnnn

NAMEDevDescLocationPartNumModelNumSerialNoRefNumCCNBCCNABAUDALRM_CNTEQP_TYPRETRY_TMRE_ALARMALRM_NAMccnbroad

_XAXQ2

—

/BROCASTS

BroadcastBus #Element #

SAVING SELECTENTERINGMonth

of week* (1=Monday)Week Number of Month LEAVINGMonth

of week* (1=Mohttp://www.51wendang.com/doc/437ec10ed908de0667a81455nday)Week Number of Month Holiday Start MonthStart Day

(days)

Override Hours

1 DOW (MTWTFSSH)Occupied FromOccupied To

2 DOW (MTWTFSSH)Occupied FromOccupied To

3 DOW (MTWTFSSH)Occupied FromOccupied To

4 DOW (MTWTFSSH)Occupied FromOccupied To

5 DOW (MTWTFSSH)Occupied FromOccupied To

6 DOW (MTWTFSSH)Occupied FromOccupied To

7 DOW (MTWTFSSH)Occupied FromOccupied To

8 DOW (MTWTFSSH)Occupied FromOccupied To

Disable37510750000

:0024:001111111100:0000:000000000000:0000:000000000000:0000:000000000000:0000:000000000000:0000:000000000000:0000:000000000000:0000:00

_selstartmonstartdowstartwomStopmonStoptdowstopwomHOL_MONHOL_DAYHOL_LENOVR_EXTDOW1OCCTOD1UNOCTOD1DOW2OCCTOD2UNOCTOD2DOW3OCCTOD3UNOCTOD3DOW4OCCTOD4UNOCTOD4DOW5OCCTOD5UNOCTOD5DOW6OCCTOD6UNOCTOD6DOhttp://www.51wendang.com/doc/437ec10ed908de0667a81455W7OCCTOD7UNOCTOD7DOW8OCCTOD8UNOCTOD8

/HOLDY_nnnn = 01 to 16OCCDEFCS/OCCnP0nSn = 1 or 2

*Day of week where daylight savings time will occur in the morning (at2:00 am). Daylight savings time occurs on Sunday (7) morning, 1 hour shallbe added when entering and 1 hour subtracted when leaving.

Date once selected (from 1) shall occur in the week number entered. 1: If dayof week selected is 7 (Sunday) time change will occur the first Sunday (weeknumber 1) in the month. 5: If day of week selected is 7 (Sunday) time changewill occur the last Sunday of the month (week number 4 or 5).NOTE: nn is software version.

APPENDIX C — CCN TABLES (cont)

TABLES (cont)

_TABn(n = 1 to 8)

NAME

n table number 1Display n var number 1Display n table number 2Display n var number 2Display n table number 3Display n var number 3Display n table http://www.51wendang.com/doc/437ec10ed908de0667a81455number 4Display n var number 4Display n table number 5Display n var number 5Display n table number 6Display n var number 6Display n table number 7Display n var number 7Display n table number 8Display n var number 8Display n table number 9Display n var number 9Metric Display on STDULanguage Selection

/No0=English1=Espanol2=Francais3=Portugues4=Translated0=Disable1=Master2=Slave

=Local Control2=Remote Control3=CCN Control1 to 236

=Always Lead1=Lag Once     Failed Only2=Lead/Lag     Runtime Sel40 to 4002 to 300 to 60

=Stop if Unit Stops1=Run if Unit StopsYes/No

NAMEtab_nb_1var_nb_1tab_nb_2var_nb_2tab_nb_3var_nb_3tab_nb_4var_nb_4tab_nb_5var_nb_5tab_nb_6var_nb_6tab_nb_7var_nb_7tab_nb_8var_nb_8tab_nb_9var_nb_9DISPUNITLANGUAGE

_SLV

SLAVE CONTROLMaster/Slave Selhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ectMaster Control TypeSlave AddressLead Lag Select

_selms_ctrlslv_addrlead_sel

/Lag Balance DeltaLag Start Timer

Pulldown TimeStart if Error Higher

Minimum Running TimeLag Unit Pump ControlChiller in Series

No

^Fmin

_bal_dlstr_timlead_pulstart_dtlag_minilag_pumpII_serie

APPENDIX C — CCN TABLES (cont)

TABLES (cont)

NAME

Loading Sequence

-30=Auto,1=A Lead2=B Lead,3 =C LeadNo/YesNo/Yes1-150-4 0-4

=No Pump

=One Pump Only2=Two Pumps Auto3=Pump#1 Manual4=Pump#2 Manual24-3000No/YesNo/YesNo/YesNo/Yes0-40-4

=OAT*, 0=None 2=Delta T,

=4-20mA Control4=Space Temp0-2

=None

=Switch Control2=4-20mA Control0-200-20No/Yes0 to 2000-4-3214.4-2720-300No/Yes00:00-24:0000:00-24:000-100No/YesNo/Yeshttp://www.51wendang.com/doc/437ec10ed908de0667a81455No/YesNo/Yes

NAMElead_cir

Loading SequenceRamp Loading SelectUnit Off to On Delay

Pumps SequenceCooler Pumps SequenceNoNo100

_typramp_seloff_on_dhpumpseqcpumpseq

Auto Rotation DelayPump Sticking ProtectionStop Pump During StandbyFlow Checked if Pump OffAuto Changeover Select*Cooling Reset SelectHeating Reset Select*48NoNoNoNo00

_delpump_perpump_sbypump_locauto_selcr_selhr_sel

Limit Type Select0lim_sel

For 100% Demand LimitmA For 0% Demand LimitCurrent Limit SelectCurrent Limit at 100%Heating OAT Threshold*Free Cooling Delta T Th*Full Load Timeout

Both Command SelectNIGHT CONTROLStart HourEnd Hour

LimitIce Mode Enable

Alarms RelayCooler pump off in heatCond pump off in cool

No200051830No00:0000:00100NoNoNoNo

&http://www.51wendang.com/doc/437ec10ed908de0667a81455#176;F&#176;Fmin

_mxlim_zecurr_selcurr_fulheat_thfree_dtfc_tmoutboth_selnh_startnh_endnh_limitice_cnfgal_reverstopheatstopcool

%

*Not supported.

Only condenser pump sequence 1 is supported.NOTES:

.Flow checked if pump off needed when a command is sent to the primary

to prevent cooler from freezing in winter conditions. Command willset the cooler flow switch to closed while the controls stop the coolerpump. The controls may then generate an alarm. If this decision is active,the cooler flow switch is not checked when the cooler pump is stopped.2.If cooling reset select set point has been selected the set point based on

-20mA input signal through ComfortLink  control, then a 4-20 mA reset

shall be ignored. Configuration 3 (4-20mA Control) and 4 (SpaceTemperature) shall require an Energy Management Module.

.Configuration 2 (4-20mA Control) shall require ahttp://www.51wendang.com/doc/437ec10ed908de0667a81455n Energy Management

. Configuration 1 Switch Demand limit provides 3 step demand limitif an Energy Management Module is present. Otherwise, only one step isallowed.

.Reverse Alarms Relay configuration will be deenergized when an alarm

alert relay is present and will be energized when no alarm is present.

APPENDIX C — CCN TABLES (cont)

CONFIGURATION TABLES

NAME

Setpoint 1Cooling Setpoint 2Cooling Ice SetpointOAT No Reset ValueOAT Full Reset ValueDelta T No Reset ValueDelta T Full Reset ValueCurrent No Reset ValueCurrent Full Reset ValueSpace T No Reset ValueSpaceT Full Reset ValueCooling Reset Deg. ValueCooling Ramp LoadingHEATING*

Setpoint 1Heating Setpoint 2OAT No Reset ValueOAT Full Reset ValueDelta T No Reset ValueDelta T Full Reset ValueCurrent No Reset ValueCurrent Full Reset ValueHeating Reset Deg. Valuehttp://www.51wendang.com/doc/437ec10ed908de0667a81455Heating Ramp LoadingAUTO CHANGEOVER*Cool Changeover SetptHeat Changeover SetptMISCELLANEOUSSwitch Limit Setpoint 1Switch Limit Setpoint 2Switch Limit Setpoint 3Reclaim Setpoint*Reclaim Deadband*

Val Condensing Stp

–20-70–20-70–20-7014-12514-1250-250-250-200-2014-12514-125–30-300.2-2.080-14080-14014-12514-1250-250- 250-200-20–30-300.2-2.039-12232-1150-1000-1000-10095-1405-27

to 120

.044.044.014.014.00.00.00.00.014.014.00.01.0100.0100.014.014.00.00.00.00.00.01.075.064.0100100100122.09.086

&#176;F&#176;F&#176;F&#176;F&#176;F^F^Fmama&#176;F&#176;F^F^F&#176;F&#176;F&#176;F&#176;F^F^Fmama^F^F&#176;F&#176;F%%%&#176;F&#176;F&#176;F

NAMEcsp1csp2ice_spoatcr_nooatcr_fudt_cr_nodt_cr_fuv_cr_nov_cr_fuspacr_nospacr_fucr_degcramp_sphsp1hsp2oathr_nooathr_fudt_hr_nodt_hr_fuv_hr_nov_hr_fuhr_deghramp_spcauto_sphauto_splim_sp1lim_sp2lim_sp3rsp

_dehttp://www.51wendang.com/doc/437ec10ed908de0667a81455adbw_sct_sp

*Not supported.

DISPLAY TABLES

_PN

NAME

Board Circuit AEXV Board Circuit BEXV Board Circuit C*

Board #1 Part NumberAUX Board #2 Part NumberAUX Board #3 Part NumberAUX Board #4 Part NumberAUX Board #5 Part NumberEMM NRCP2 BoardReclaim NRCP2 BoardTCPM Board Comp AMust Trip Amps

Config Switch (8 to 1)TCPM Board Comp BMust Trip Amps

Config Switch (8 to 1)TCPM Board Comp C*Must Trip Amps

Config Switch (8 to 1)Current Phase 1 Comp ACurrent Phase 2 Comp ACurrent Phase 3 Comp ACurrent Phase 1 Comp BCurrent Phase 2 Comp BCurrent Phase 3 Comp BCurrent Phase 1 Comp C*Current Phase 2 Comp C*Current Phase 3 Comp C*CIR A DEFROST CONTROLExchanger Frost FactorNext Sequence Allowed inDefrost Active?

TemperatureDefrost Duration

Sequence Started ?Override State

SST CalculationDelta: OAT http://www.51wendang.com/doc/437ec10ed908de0667a81455- Mean SSTReference Delta

- Reference DeltaFrost Integrator GainDefrost Fan Start Cal ADefrost Fan Offset Cal A

B DEFROST CONTROLExchanger Frost FactorNext Sequence Allowed inDefrost Active?

TemperatureDefrost Duration

Sequence Started?Override State

SST calculationDelta: OAT - Mean SSTReference Delta

- Reference DeltaFrost Integrator GainDefrost Fan Start Cal BDefrost Fan Offset Cal B

-60000000000nnnn0-60000000000XXXXXXXX0-600000000000-6000-6000-6000-6000-6000-6000-6000-6000-6000-100nnn

/False&#177;nnn.nnnnnnn&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.nn.n0.000.000-100nnn

/False&#177;nnn.nnnnnnn&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.nn.n0.000.00

NAMEexv_brdaexv_brdbexv_brdcaux_brd1aux_brd2aux_brd3aux_http://www.51wendang.com/doc/437ec10ed908de0667a81455brd4aux_brd5emm_nrcprec_nrcpcpa_verscpa_mtamcpa_s1_mcpb_verscpb_mtamcpb_s1_mcpc_verscpc_mtamcpc_s1_mcpa_cur1cpa_cur2cpa_cur3cpb_cur1cpb_cur2cpb_cur3cpc_cur1cpc_cur2cpc_cur3frost_adef_se_amode[19]DEFRT_Adefr_duadef_fa_aover_d_asst_dm_adelt_adelt_r_adel_v_afr_int_adef_ca_adef_of_afrost_bdef_se_bmode[20]DEFRT_Bdefr_dubdef_fa_bover_d_bsst_dm_bdelt_bdelt_r_bdel_v_bfr_int_bdef_ca_bdef_of_b

STATUS

amps0amps0ampsampsampsampsampsampsampsampsamps%

&#176;F

&#176;F^F^F&#176;Fpsipsi%

&#176;F

&#176;F^F^F^Fpsipsi

_PHASE

*

*Not supported.

: Tables for display only. Forcing shall not be supported on this maintenance screen.

APPENDIX C — CCN TABLES (cont)

DISPLAY TABLES (cont)

*

NAME

A SCT Control PointCir A SCT CandidateCir A Fan Cycle Chttp://www.51wendang.com/doc/437ec10ed908de0667a81455ounterCir A Optimal Fan CountCir B SCT Control PointCir B SCT CandidateCir B Fan Cycle CounterCir B Optimal Fan CountCir C SCT Control PointCir C SCT CandidateCir C Fan Cycle CounterCir C Optimal Fan CountPower On 1: day-mon-yearPower On 1: hour-minutePowerDown 1:day-mon-yearPowerDown 1:hour-minutePower On 2: day-mon-yearPower On 2: hour-minutePowerDown 2:day-mon-yearPowerDown 2:hour-minutePower On 3: day-mon-yearPower On 3: hour-minutePowerDown 3:day-mon-yearPowerDown 3:hour-minutePower On 4: day-mon-yearPower On 4: hour-minutePowerDown 4:day-mon-yearPowerDown 4:hour-minutePower On 5: day-mon-yearPower On 5: hour-minutePowerDown 5:day-mon-yearPowerDown 5:hour-minuteCAPACITY CONTROLAverage Ctrl Water TempDifferential Water TempWater Delta TControl PointReset Amount

Temp ErrorActual Capacity

Capacity LimitActual Chiller CurrentChiller Current LimitCurrent At 30% Load ACurrent At 30% Load BCurrent At 30%http://www.51wendang.com/doc/437ec10ed908de0667a81455 Load CCurrent At 100% Load ACurrent At 100% Load BCurrent At 100% Load CCurrent Z Multiplier ValLoad/Unload Factor

Capacity OverrideEHS CAPACITY CONTROL*EHS Ctrl Override

Electric StageElectrical Pulldown?EXV CONTROL

Position Circuit ADischarge Superheat ASuction Superheat ASuction SH Control Pt ACooler Exchange DT Cir ACooler Pinch Ctl Point AEXV Override Circuit AEXV Position Circuit BDischarge Superheat BSuction Superheat BSuction SH Control Pt BCooler Exchange DT Cir BCooler Pinch Ctl Point BEXV Override Circuit BEXV Position Circuit C*Discharge Superheat C*Suction Superheat C*Suction SH Control Pt C*Cooler Exchange DT Cir C*Cooler Pinch Ctl Point C*EXV Override Circuit C*ECONOMIZER CONTROLEconomizer Position AEconomizer Superheat AEconomizer SH Setpoint AEXV Override Circuit AEconomizer Position BEconomizer Superheat BEconomizer SH Setpoint BEXV Override Circuit BEconomizer Position C*Ehttp://www.51wendang.com/doc/437ec10ed908de0667a81455conomizer Superheat C*Economizer SH Setpoint C*EXV Override Circuit C*

&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.nnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnn&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.nnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnn&#177;n.n&#177;nnn.nnnnnnn

/Falsennn.nnnn.nnn.nnn.nnn.nnn.nnnnnn.nnnn.nnn.nnn.nnn.nnn.nnnnnn.nnnn.nnn.nnn.nnn.nnn.nnnnnn.nnn.nnn.nnnnnn.nnn.nnn.nnnnnn.nnn.nnn.nnn

%%^F^F^F^F%%^F^F^F^F%%^F^F^F^F%^F^F%^F^F%^F^F

&#176;F&#176;F&#176;F&#176;F&#176;F&#176;Fddmmyyhhmmddmmyyhhmmddmmyyhhmmddmmyyhhmmddmmyyhhmmddmmyyhhmmddmmyyhhmmddmmyyhhmmddmmyyhhmmddmmyyhhmm&#176;F&#176;F^F&#176;F^F^F%%ampsampsampsampsampsampsampsamps0/0

NAMEsct_sp_asct_fu_afancyc_afancop_asct_sp_bsct_fu_bfhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ancyc_bfancop_bsct_sp_csct_fu_cfancyc_cfancop_cdate_on1time_on1date_of1time_of1date_on2time_on2date_of2time_of2date_on3time_on3date_of3time_of3date_on4time_on4date_of4time_of4date_on5time_on5date_of5time_of5ctrl_avgdiff_wtdelta_t

_PNTresettp_errorcap_tcap_limTOT_CURRCURR_LIMcur_30_acur_30_bcur_30_ccur100_acur100_bcur100_czmsmz

_capover_ehseh_stageehspulldEXV_ADSH_ASH_Ash_sp_apinch_apinch_spaov_exv_aEXV_BDSH_BSH_Bsh_sp_bpinch_bpinch_spbov_exv_bEXV_CDSH_CSH_Csh_sp_cpinch_cpinch_spcov_exv_cEXV_EC_Aeco_shaecsh_spaov_eco_aEXV_EC_Beco_shbecsh_spbov_eco_bEXV_EC_Ceco_shcecsh_spcov_eco_c

STATUS

_POR

_CTRL

*Not supported.

APPENDIX C — CCN TABLES (cont)

DISPLAY TABLES (cont)

NAME

is Master or SlaveMaster Control Type*Master/Slave Ctrl ActiveLead Unit is the:Slave Chiller State

://www.51wendang.com/doc/437ec10ed908de0667a81455E

/Master/SlaveLocal/Remote/CCNTrue/FalseMaster/Slave0=Chiller is off

=Valid Run State in     CCN Mode

=Unused for this control3=Chiller is in local mode4=Power fail restart in     progress

=Shudown due to fault6=Communication failure0-100%1-30minutes&#177;nnnnnhoursYes/NoYes/Nonn

/False

=Unit not configured     as a slave chiller1=Slave pump

error     (ms_error=1)

=Unit configured as     slave chiller with     lwt_opt=no (entering     water control) with     pump control     (lag_pump=0)

=Unit configured as slave     chiller with lwt_opt=yes     (leaving water control)     with pump control     (lag_pump=0)

=Unit Configured as slave     chiller with lwt_opt=no     (entering water control)     with no pump control     (lag_pump=1)

=Unit configured as slave     chiller with lwt_opt=yes     (leaving water control)     with no phttp://www.51wendang.com/doc/437ec10ed908de0667a81455ump control     (lag_pump=1)

NAMEmstslvms_ctrlms_activlead_selslv_stat

STATUS

Chiller Total CapLag Start Delay**

/Lag Hours Delta*Lead/Lag Changeover?**Lead Pulldown?Master/Slave Error

Available Capacity?  Slave Lagstatslv_captl_strt_dll_hr_dll_changll_pullms_errorcap_maxlagstat

*Always CCN for the slave chiller. Slave chiller chillstat value

**This decision is consistent for master chiller only. It shall be set by default to 0 for the slave chiller.  This item is true when chiller has loaded its total available capacity tonnage.TABLE

NAME

Occp Period #Timed-Override in EffectTimed-Override DurationCurrent Occupied TimeCurrent Unoccupied TimeNext Occupied DayNext Occupied TimeNext Unoccupied DayNext Unoccupied TimePrev Unoccupied DayPrev Unoccupied TimeDischarge A Temp AverageDischarge A Temp RateDischarge A Gas Limithttp://www.51wendang.com/doc/437ec10ed908de0667a81455Suction A Temp AverageDischarge B Temp AverageDischarge B Temp RateDischarge B Gas LimitSuction B Temp AverageDischarge C Temp AverageDischarge C Temp RateDischarge C Gas LimitSuction C Temp Average

to 8Yes/No0-4

:00-23:5900:00-23:59Mon-Sun00:00-23:59Mon-Sun00:00-23:59Mon-Sun00:00-23:59

&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.n&#177;nnn.n

&#176;F^F&#176;F&#176;F&#176;F^F&#176;F&#176;F&#176;F^F&#176;F&#176;F

NAMEPER_NOOVERLASTOVR_HRSSTRTTIMEENDTIMENXTOCDAYNXTOCTIMNXTUNDAYNXTUNTIMPRVUNDAYPRVUNTIMsdt_m_asdt_mr_asdtlim_asst_m_asdt_m_bsdt_mr_bsdtlim_bsst_m_bsdt_m_csdt_mr_csdtlim_csst_m_c

STATUS

_LIMIT

: Table for display only. Used for Cooling and Heat Pump Compressor Envelope.TABLE

NAME

Maintenance Alhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ert1 to 11: reset individually12: reset all

WARNINGS1 — Refrigerant Charge2 — Water Loop Size

SERVICING DELAYS3 — Cooler Pump 1 (days)4 — Cooler Pump 2 (days)5 — Condenser Pump 1 (days)6 — Condenser Pump 2 (days)7 — Water Filter (days)8 — Cp A Oil Filter (days)9 — Cp B Oil Filter (days)10 — CP.C Oil Filter (days)

NAMES_RESET

STATUSforcible

/Low/DisableNormal/Low/Disable0-1000/Alert/Disable0-1000/Alert/Disable0-1000/Alert0-1000/Alert

-1000/Alert/Disable0-1000/Alert0-1000/alert0-1000/Alert

_mwloop_mcpump1_mcpump2_mhpump1_mhpump2_mwfilte_moilfa_moilfilb_moilfic_m

APPENDIX C — CCN TABLES (cont)

CONFIGURATION TABLES

NAME

Unit SizeYes

Voltage110NoNoNoNoYesNoNoYesNoNoNo

://www.51wendang.com/doc/437ec10ed908de0667a81455ITS

NAMEun_cp_aun_cp_bun_cp_cunit_typunitsizefreq_60Hvoltagevarfan_avarfan_bvarfan_csoftstarwye_deltrecl_optfreecoolheat_selcond_valhgbp_selmchx_selboil_selemm_nrcphighdisp

STATUS

USED FOR DISABLE COMPRESSORS (see notes)CP_UNABLCompressor A DisableNo/Yes(See Notes)Compressor B DisableNo/Yes

C Disable*No/Yes

Type3 (Water Cooled)(See Notes)4 (Heat Machine)

Capacity0 to 1800Power Frequence 60HZ SelYes/NoPower Supply Voltage200 to 660NB Fans on Varifan Cir A0 to 6NB Fans on Varifan Cir B0 to 6NB Fans on Varifan Cir C0 to 6Soft Starter Select*Yes/NoWye Delta Start SelectYes/NoAir Cooled Reclaim SelYes/NoFree Cooling Select*Yes/NoCooler Heater Select*Yes/NoCondenser Water Val SelYes/NoHot Gas Bypass SelectYes/NoMCHX Exchanger Select*Yes/NoBoiler Command Select*Yes/NoEnergy Management ModuleYes/NoHigh Tiers Display SelecNo = Use Navigator

://www.51wendang.com/doc/437ec10ed908de0667a81455 as user interface (factory installed)

= Use Touch Pilot  Display as user interface (factory installed)

Password0 to 9999Hydraulic Transducer Kit*Yes/NoCooler Pass Number1 to 3VLT Fan Drive Select*VLT Fan Drive rpm*

Condensing SelectYes/NoMax Condenser LWT=45degCYes/No

Compressor A Config

Trip Amps0 to 600S1 Config Switch (8 to 1)00000000 (8 position dip

configuration)

B ConfigMust Trip Amps0 to 600S1 Config Switch (8 to 1)00000000 (8 position dip

configuration)

C ConfigMust Trip Amps0 to 600S1 Config Switch (8 to 1)00000000 (8 position dip

configuration)

A Total Fans NB2 to 8Circuit B Total Fans NB2 to 8Circuit C Total Fans NB0 to 8EXV A Maximum Steps Numb0/15000EXV B Maximum Steps Numb0/15000EXV C Maximum Steps Numb0/15000Economizer A Steps Numb0/15000Economizer B Steps Numb0/http://www.51wendang.com/doc/437ec10ed908de0667a8145515000Economizer C Steps Numb0/15000*Not supported.

0 = No economizer.NOTES:

.Table used to disable compressors for maintenance purposes. Thecapacity control will consider that these compressors (once set to YES)are failed manually (no alarm will appear).

.Enter unit size. This item allows the controls to determine capacity of eachcompressor and the total number of fans on each circuit based on a com-pressor arrangement array (can be viewed in table FACTORY2). It is notnecessary to enter compressor capacity and number of fans on each cir-cuit. See the 30XW Installation Instructions for more information.

.Number of fans controlled directly by a variable speed fan actuator using0 to 10 vdc signal. This will enable the controls to determine the remainingdiscrete fan staging outputs from the total fans on each circuit.

No200NoNo

to Appendix DRefer to Appendix DRefer to Aphttp://www.51wendang.com/doc/437ec10ed908de0667a81455pendix DRefer to Appendix D00000426042600

2785 0

_passkithydrocpass_nbvlt_selvlt_rpmhighcondmax_clwtcpa_mtaccpa_s1_ccpb_mtaccpb_s1_ccpc_mtaccpc_s1_cnb_fan_anb_fan_bnb_fan_cexva_maxexvb_maxexvc_maxeco_cnfaeco_cnfbeco_cnfc

://www.51wendang.comed for extra functions with the purpose of energy management such asoccupancy override switch, ice storage, setpoint reset, and demand http://www.51wendang.compressor capacity will be automatically determined if unit size enteredin FACTORY table matches the values in the unit compressor configura-tion table.

.Total number of fans includes fans controlled by a variable speed fan. Thisvalue will be automatically populated if unit size entered in FACTORYtable matches the values in the unit compressor configuration table.

APPENDIX C — CCN TABLES (cont)

CONFIGURATION TABLES (cont)

NAMEMAINTENhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ANCE CONFIGServicing Alert

Charge CtrlWater Loop Control

1 Ctl Delay (days)CPump 2 Ctl Delay (days)HPump 1 Ctrl Delay (days)*HPump 2 Ctrl Delay (days)*Water Filter Ctrl (days)Oil Filter A Ctrl (days)Oil Filter B Ctrl (days)Oil Filter C Ctrl (days)

/DisableEnable/DisableEnable/Disable0-10000-10000-10000-10000-10000 to 10000 to 10000 to 1000

NAMEs_alertcharge_cwloop_ccpump1_ccpump2_chpump1_chpump2_cwfilte_coilfia_coilfib_coilfic_c

STATUS

*Not supported.TABLESERVICE1

NAME

Fluid Type

Switch SP*

Freeze Setpoint

Minimum Fluid TempCondenser Fluid TypeEntering Fluid ControlProp PID Gain VarifanInt PID Gain VarifanDeri PID Gain Varifan

Ducted Fan SpeedEXV A Superheat SetpointEXV B Superheat SetpointEXV C Superheat SetpointPihttp://www.51wendang.com/doc/437ec10ed908de0667a81455nch offset circuit APinch offset circuit BPinch offset circuit CEXV MOP Setpoint

Pressure ThresholdCooler Heater Delta SptAuto Start When SM Lost3way Valve Min Position3way Valve Max PositionEconomizer SH Setpoint AEconomizer SH Setpoint BEconomizer SH Setpoint CFast Loading SequenceEWT Probe on Cir A Side

/2

=Water2=Brine0-60

–20.0-34.010.0-34.01/2

=Water2=BrineYes/No–20.0-20.0–5.0-5.0–20.0-20.020-1007.2-447.2-447.2-44–5.4-5.4–5.4-5.4–5.4-5.440-55200-2901-6

/Disable0-5020-1005-155-155-150-4Yes/No

No2.00.20.410014.414.414.45.45.4–3.662275.52

.810.810.80Yes

NAMEflui_typflow_spfreezespmini_lwtcond_typewt_opthd_pghd_ighd_dgfan_maxsh_sp_ash_sp_bsh_sp_cp_ofst_ap_ofst_bp_ofst_cmop_sphp_thheaterspauto_smmin_3wmax_3wesh_sp_aesh_sp_besh_sp_cfastloadewt_cirA

STATUS

&#176;F&#176;F

%^Fhttp://www.51wendang.com/doc/437ec10ed908de0667a81455^F^F^F^F^F&#176;Fpsi^F%%^F^F^F

*Not supported. Must be configured at default.

: This table shall be downloadable at any time. However, modified value shall not be used by tasks until the unit is in OFF state. This shall not apply to the Varifangains that shall be modified at any time and used immediately by the head pressure control tasks even if the unit is in operation.

NAMERANGE

TO BE USED FOR RUN TIMES UPDATE IN CASE OF CONTROL RETROFITUPDHRFAN

Cooling A Pump Hours0Free Cooling B Pump Hours0Circuit A Defrost Number0Circuit B Defrost Number0Circuit A Fan #1 Hours0Circuit A Fan #2 Hours0Circuit A Fan #3 Hours0Circuit A Fan #4 Hours0Circuit A Fan #5 Hours0Circuit A Fan #6 Hours0Circuit A Fan #7 Hours0Circuit A Fan #8 Hours0Circuit A Fan #9 Hours0Circuit A Fan #10 Hours0Circuit B Fan #1 Hours0Circuit B Fan #2 Hours0Circuit B Fan #3 Hours0Circuit B Fan #4 Hours0Circuit B Fhttp://www.51wendang.com/doc/437ec10ed908de0667a81455an #5 Hours0Circuit B Fan #6 Hours0Circuit B Fan #7 Hours0Circuit B Fan #8 Hours0Circuit B Fan #9 Hours0Circuit B Fan #10 Hours0Circuit C Fan #1 Hours0Circuit C Fan #2 Hours0Circuit C Fan #3 Hours0Circuit C Fan #4 Hours0Circuit C Fan #5 Hours0Circuit C Fan #6 Hours0Circuit C Fan #7 Hours0Circuit C Fan #8 Hours0

NAMEWRITE STATUS

_fcp_ahr_fcp_bnb_def_anb_def_bhr_fana1hr_fana2hr_fana3hr_fana4hr_fana5hr_fana6hr_fana7hr_fana8hr_fana9hrfana10hr_fanb1hr_fanb2hr_fanb3hr_fanb4hr_fanb5hr_fanb6hr_fanb7hr_fanb8hr_fanb9hrfanb10hr_fanc1hr_fanc2hr_fanc3hr_fanc4hr_fanc5hr_fanc6hr_fanc7hr_fanc8

: This table shall be used for purposes of transplanting the devices run hours in the event of a module hardware failure or software upgrade via downloading. Itshall http://www.51wendang.com/doc/437ec10ed908de0667a81455be usable only if all items are still null. Afterwards, its access shall be denied.

APPENDIX C — CCN TABLES (cont)

CONFIGURATION TABLES (cont)

NAMERANGE

TO BE USED FOR RUN TIMES UPDATE IN CASE OF CONTROL RETROFITUPDTHOURMachine Operating Hours0

Starts0Compressor A Hours0Compressor A Starts0Compressor B Hours0Compressor B Starts0Compressor C Hours0Compressor C Starts0Water Pump #1 Hours0Water Pump #2 Hours0Condenser Pump #1 Hours0Condenser Pump #2 Hours0

NAMEhr_machst_machhr_cp_ast_cp_ahr_cp_bst_cp_bhr_cp_cst_cp_chr_cpum1hr_cpum2hr_hpum1hr_hpum2

STATUS

: This table shall be used for purposes of transplanting the devices run hours and starts in the event of a module hardware failure or software upgrade via down-loading. It shall be usable only if allhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 items are still null. Afterwards, its access shall be denied.

APPENDIX D — 30XW150-400 CPM DIP SWITCH ADDRESSES

-THE-LINE START — STANDARD CONDENSING

XW  VOLTAGE CPM DIP UNIT SIZE  (3 ph, 60Hz)  SWITCHES

,325

,350

,400

S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2

A

B  4

MTA SETTING SETTING CIRCUIT A  CIRCUIT B

——————http://www.51wendang.com/doc/437ec10ed908de0667a81455———

ON   OFF   ON   OFF   OFF   OFF   ON   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   ON   ON   ON   ON   ON   ON   OFF   ON   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   ON   ON   OFF   OFF   OFF   OFF   ON   ON   ON   OFF   OFF   OFF   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   ON   OFF   ON   OFF   OFF   OFF   ON   ON   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   ON   OFF   OFF   OFF   ON   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   ON   ON   ON   ON   ON   ON   OFF   ON   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   ON   ON   OFF   OFF   OFF   OFF   ON   ON   ON   OFF   OFF   OFF   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   ON   OFF   ON   OFF   OFF   OFF   ON   ON   OFF   ON   OFF   OFF http://www.51wendang.com/doc/437ec10ed908de0667a81455  OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   OFF   OFF   OFF   OFF   ON   OFF   OFF   OFF   OFF   OFF   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   OFF   OFF   OFF   ON   OFF   OFF   OFF   OFF   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   OFF   OFF   OFF   OFF   ON   OFF   OFF   OFF   OFF   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF  ———————— OFF   OFF   ON  ON   OFF   OFF   OFF  ———————— OFF   ON   OFF   OFF   ON   OFF   OFF  ———————— ON   ON   ON   ON  ON  ———————— OFF   ON   OFF   OFF   ON   OFF   OFF  ———————— ON   OFF  ON  ———————— OFF   ON   OFF   OFF   ON   OFF   OFF  ———————— OFF   OFF   ON  OFF   ON  OFF   OFF  ———————— OFF   ON   OFF   OFF   ON   OFF   OFF  ———————— ON   OFF   OFF ON  OFF   ON  http://www.51wendang.com/doc/437ec10ed908de0667a81455 OFF   OFF  ———————— OFF   ON   OFF   OFF   ON   OFF   OFF  ———————— ON   ON  ON   ON  ———————— OFF   ON   OFF   OFF   ON   OFF   OFF  ———————— ON   OFF   OFF  ON   ON OFF   OFF  ———————— OFF   ON   OFF   OFF   ON   OFF   OFF  ———————— OFF  OFF   OFF   OFF  ON   ON   OFF   OFF  ———————— OFF   ON   OFF   OFF   ON   OFF   OFF  ———————— ON   ON   ON  ON  ————————

-THE-LINE START — HIGH CONDENSING/HEAT MACHINE

XW  VOLTAGE CPM DIP

SIZE  (3 ph, 60Hz)  SWITCHES

,325

,350

,400

S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2

A

B  4

MTA SETTING SETTING CIRCUIT A  CIRCUIT B

http://www.51wendang.com/doc/437ec10ed908de0667a814552486

ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   OFF   OFF   OFF   OFF   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   ON   OFF   OFF   ON   ON   ON   ON   ON   ON   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   ON   OFF   OFF   ON   ON   OFF   ON   ON   ON   ON   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   OFF   OFF   OFF   OFF   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   ON   OFF   OFF   ON   ON   ON   ON   ON   ON   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   ON   OFF   OFF   ON   ON   OFF   ON   ON   ON   ON   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF http://www.51wendang.com/doc/437ec10ed908de0667a81455  OFF   ON   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   ON   OFF   OFF   OFF   ON   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   ON   OFF   ON   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   ON   OFF   OFF   ON   ON   ON   ON   ON   OFF   ON   ON   ON   ON   ON  LEGEND

—Compressor Protection ModuleDIP—Dual In-Line PackageMTA—Must Trip Amps

: Sizes 150-200 are Circuit A only.

APPENDIX D — 30XW150-400 CPM DIP SWITCH ADDRESSES (cont)

-DELTA START — STANDARD CONDENSING

A

XW UNIT  VOLTAGE CPM DIP    SIZE  (3 ph, 60Hz)  SWITCHES                    1234 5678

,325

,350

,400

B

MTA

SETTINhttp://www.51wendang.com/doc/437ec10ed908de0667a81455G CIRCUIT A  CIRCUIT B

S2   S1      S2   S1   S2      S1   S2   S1   S2      S1   S2   S1   S2   S1   S2   S1      S2   S1   S2

S2   S1   S2   S1   S2   S1   S2   S1   S2

OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   ON   OFF   ON   ON   ON   ON   ON   ON   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   ON    ON     ON     OFF    ON     ON     ON     ON   ON   ON   ON   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   ON   OFF     ON    OFF     ON         ON     ON   ON   ON   ON   OFF   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   ON   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   ON   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   ON   OFF   OFF   OFF   OFF   ON   ON   http://www.51wendang.com/doc/437ec10ed908de0667a81455OFF   ON   OFF   OFF   OFF   ON    OFF    OFF     ON   OFF     OFF     OFF     OFF     ON   OFF   OFF   ON   OFF   ON   OFF   ON   ON   ON   ON   ON   ON   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   ON   ON   ON   OFF   ON   ON   ON   ON   ON   ON   ON   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   ON   OFF   ON   OFF   ON   ON   ON   ON   ON   ON   OFF   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF    OFF     ON     ON     OFF     OFF     ON     OFF     OFF   OFF   ON   ON   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF

ON   OFF   OFF   OFF   ON   ON   OFF   OFF   OFF   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   ON   OFF   OFF   OFF   OFF   OFF   ON   OFF   OFF   OFF   ON   ON   OFF   OFF   OFF   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   OFF   OFF   OFF

://www.51wendang.com/doc/437ec10ed908de0667a81455ON   OFF   OFF   OFF   OFF   ON   ON   OFF   ON   OFF   OFF   OFF   ON   ON   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   ON   OFF   ON   OFF   ON   ON   ON   ON   ON   OFF   ON   ON   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   OFF   ON   ON   ON   ON   ON   OFF   ON   OFF   ON   ON   OFF   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   ON   ON   ON   ON   ON   ON   ON   ON   OFF   ON   ON   OFF   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   ON   OFF   ON   ON   ON   ON   ON   ON   ON   ON  575460

://www.51wendang.com/doc/437ec10ed908de0667a81455300

S2S1S2S1S2S1S2S1S2S1S2S1S2S1S2S1S2S1S2S1S2S1S2S1S2S1S2S1S2ONONONONONOFFONOFFONOFFONONONONONOFFONOFFONONONONONONONONONOFFONONOFFOFFOFFONOFFONOFFOFFOFFOFFOFFOFFOFFONOFFONOFFOFFOFFONOFFONOFFOFFOFFONOFFONOFFONOFFOFFOFFONOFFOFFOFFONOFFOFFOFFOFFOFFOFFOFFONOFFOFFOFFONOFFOFFOFFOFFOFFONOFFONOFFONONOFFONOFFOFFOFFOFFONOFFONONOFFONONOFFONOFFOFFOFFONONONONONOFFOFFOFFONOFFONOFFOFFOFFOFFONONONONONONOFFONOFFONONONONONONOFFOFFONOFFOFFONOFFONONONONOFFOFFOFFONOFFONOFFONOFFOFFOFFOFFOFFONOFFONOFFOFFOFFONOFFOFFOFFOFFOFFOFFOFFOFFOFFONOFFOFFOFFOFFOFFOFFOFFONOFFOFFOFFOFFOFFOFFOFFOFFOFFOFFOFFOFFOFFOFFOFFONOFFONOFFOFFOFFOFFOFFONOFFONOFFOFFOFFOFFOFFONOFFONOFFONOFFOFFOFFONOFFONOFFONOFFONOFFOFFOFFONOFFON——————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————http://www.51wendang.com/doc/437ec10ed908de0667a81455——————

———————————————

———

Protection ModuleDual In-Line PackageMust Trip Amps

: Sizes 150-200 are Circuit A only.

APPENDIX D — 30XW150-400 CPM DIP SWITCH ADDRESSES (cont)

-DELTA START — HIGH CONDENSING/HEAT MACHINE

XW  VOLTAGE CPM DIP UNIT SIZE  (3 ph, 60Hz)  SWITCHES

,325

,350

,400

S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2   S1   S2

A

B  4

MTASETTINGSETTINGCIRCUIT A  CIRCUIT B

http://www.51wendang.com/doc/437ec10ed908de0667a8145510282354426706810322402486802922

OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   ON   ON   ON   ON   ON   OFF   ON   ON   ON   ON   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   ON   ON   ON   ON   ON   OFF   ON   ON   ON   ON   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   OFF   OFF   OFF   OFF   ON   ON   ON   OFF   OFF   OFF   OFF   OFF   ON   ON   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   ON   ON   ON   OFF   ON   ON   ON   ON   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   OFF   OFF   OFF   ON   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   ON   OFF   OFF   OFF   ON   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   http://www.51wendang.com/doc/437ec10ed908de0667a81455OFF   OFF   OFF   ON   OFF   ON   ON   ON   ON   ON   OFF   ON   ON   ON   ON   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   ON   ON   ON   ON   ON   OFF   ON   ON   ON   ON   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   OFF   OFF   OFF   OFF   ON   ON   ON   OFF   OFF   OFF   OFF   OFF   ON   ON   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   ON   ON   ON   OFF   ON   ON   ON   ON   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   OFF   OFF   OFF   ON   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   ON   OFF   OFF   OFF   ON   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   ON   ON   ON   ON   OFF   ON   ON   ON   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   http://www.51wendang.com/doc/437ec10ed908de0667a81455OFF   ON   ON   ON   ON   ON   OFF   ON   ON   ON   ON   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   ON   ON   ON   ON   ON   ON   ON   ON   ON   ON   ON   ON   ON   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   OFF   OFF   ON   OFF   ON   OFF   OFF   OFF   ON   OFF   ON   OFF   ON   OFF   OFF   OFF   ON   ON   OFF   OFF   OFF   ON   OFF   OFF   ON   OFF   OFF   OFF   ON   OFF   OFF   OFF   OFF   OFF   OFF   ON   OFF   ON   OFF   ON   OFF   OFF   OFF   ON   OFF   ON   OFF   ON

: Sizes 150-200 are Circuit A only.

[此处图片未下载成功]

APPENDIX E — PIPING AND INSTRUMENTATION

XW UNIT ECONOMIZED PIPING

APPENDIX E — PIPING AND INSTRUMENTATION (cont)

XW UNIT NON-ECONOMIZED PIPING

APPENDIX F — GLOBAL TIME SCHEDULE CONFIGURATION FOR i-Vu&#174; DEVICE

CSM CONTROLLERhttp://www.51wendang.com/doc/437ec10ed908de0667a81455

a 30XW chiller so either the i-VuThe following is intended to assist a Carrier technician in&#174;vice, CCN Global Schedule Master, or a CSM controller can 4.0 or 4.2 de-Start and Stop the chiller. The 30XW chiller has unique tablenaming convention for its Time Schedules that are differentthan what is used today in CCN. The five steps outlined in theprocedures below must be followed in order to have the i-Vudevice and CCN products control the chiller.

1 — Chiller Configuration

.Make sure the chiller is shut down and that the Emergen-cy On/Off Switch (SW2) is in the Off Position and theEnable-Off-Remote (SW1) is in the Disable position.2.Next, UPLOAD the chiller to assure the configuration iscurrent.

: This must be done in both NSTV and CVIEW.3.Change the chiller’s Time Schedule Table Name fromOCCyP0xx to OCCPC0xx. See descriptions below.

AND NETWORK TIME SCHEDULEDESCRIPThttp://www.51wendang.com/doc/437ec10ed908de0667a81455IONS

to OCCPC01S.

SCHEDULE TABLE NAME CHANGE

.

.Highlight the chiller, then (at the top menu bar) click onConfigure   Names…

.When the dialog box opens, scroll down to find the fourtime schedules (as seen in Fig. A for Local Schedule orFig. B for Network Time Schedule). Highlight the desiredTime Schedule to edit.

.At the bottom where it says New name, double click onOCC1P01x and rename it with OCCPC01x   click Save  click OK.

.Download the new configuration to the chiller.

.Cycle power to the MBB (main base board) using SW2emergency stop.

.

.Highlight the chiller and click Configure

[此处图片未下载成功]

Table Names.2.When the dialog box opens, scroll down to find the sixOCC tables.

: Only the &quot;S&quot; and &quot;E&quot; Schedules are editable.3.Highlight the Time Schedule OCC1P01x then click Mod-ify…

http://www.51wendang.com/doc/437ec10ed908de0667a81455.In the new dialog box, rename the schedule OCCPC01x(as seen in Fig. C for Local Schedule or Fig. D for Net-work Time Schedule) then click OK to close this dialogbox.

.Click Close to close the Table Names dialog box.6.Download the new configuration to the chiller.

.Cycle power to the MBB (main base board) using SW2emergency stop.

[此处图片未下载成功]

Fig. A — NTSV Table Name (Local Schedule)

[此处图片未下载成功]

Fig. B — NTSV Table Name (Network Schedule)

[此处图片未下载成功]

Fig. C — CVIEW Table Name (Local Schedule)

. D — CVIEW Table Name (Network Schedule)

APPENDIX F — GLOBAL TIME SCHEDULE CONFIGURATION FOR i-Vu&#174; DEVICE

CSM CONTROLLER (cont)

different mode selections for the chiller which are describedbelow. In order to change the mode from the default configura-tion, a scrolling marquee or handheld Navigator  device mustbe used.

://www.51wendang.com/doc/437ec10ed908de0667a81455p://www.51wendang.coming a Navigator device, select Operating Modes

OPER, then enter the password.

.The screen defaults to SWITCH Mode. If using an i-Vudevice or CCN Global Scheduling, use the up arrow toselect Time Sched and then press Enter.or

the up arrow and select CCN to control the chillerusing a CCN Network Command of &quot;CHIL_S_S&quot;.MODE DESCRIPTIONS

.

or by setpoint tables 1 or 2. This mode needs to be se-lected if i-Vu will be writing to either a Local (S) or Network(E) Time Schedule.

: The i-Vu CCN 4.0 device can only write to Networkschedules.

CHIL_S_S for starting and stopping the equipment.

2 —  Chiller  Mode  Selection  —  There are

.Set the Enable-Off-Remote (SW1) switch to the Enableposition. (If Remote is used, external contacts will needto be closed or a jumper needs to be installed on TB-5no. 9, 10http://www.51wendang.com/doc/437ec10ed908de0667a81455.) The chiller will run off either the Switch,Time Schedule, or CCN Mode (see Mode Descriptionsin Step 2).

completes the configuration decisions needed in a30XW unit to enable i-Vu device scheduling to control thechiller start/stop.

5 — i-Vu Device Scheduling Setup

THE i-Vu 4.2 DEVICE (LOCAL ANDGLOBAL SCHEDULING)

.After chiller has been scanned into the database, checkthe Schedule number. To do this, click on the SchedulesTab   CCN Tab. The CCN Schedule Number needs tobe the same number that the user edited in Fig. A or C forlocal or Fig. B or D for global (see Fig. E).

.Next, create a Schedule by highlighting the chiller.3.Click on Schedules   Configure   Add.

.Then select the type of schedule from the drop downmenu.

: Select Normal   Weekly and the scheduleshould look like Fig. F.5.Configure the schedule.

: Refer to the i-Vu Installation andhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 Startup manual formore information on creating a schedule in i-Vu.

THE i-Vu 4.0 DEVICE (GLOBALSCHEDULING)

.After chiller has been scanned into the database, checkthe Schedule number. To do this, expand the Chilleron the left-hand navigation pane   click the on the&quot;Schedule&quot; point   Properties tab

[此处图片未下载成功]

Summary Tab.Enter CCN Global Schedule Number. It needs to bethe same number that the user edited in Fig. B or D (seeFig. G).

.Follow Steps 2 through 5 in the Configuring the i-Vu 4.2device (Local and Global Scheduling) section.

completes configuring a 30XW Chiller, i-Vu device,and CCN Network Time Schedules.

3 — Chiller Cooling Set Point Selec-tion — There are several options for controlling the Leaving

Water temperature. For the purpose of having i-Vu ableto start stop the chiller through the Time Schedule MODE thechiller's &quhttp://www.51wendang.com/doc/437ec10ed908de0667a81455ot;Cooling Set Point Select&quot; decision needs to be con-figured for SETPOINT 1 using a scrolling marquee or Naviga-tor device.

://www.51wendang.coming a Navigator device, select Operating Modes

SP.SE, then enter the password.

.Click the arrow up and select SETPOINT 1 then pushEnter.1.Set the Emergency On/Off Switch (SW2) switch to theOn Position.

4 — Chiller Switch Setup

. E — CCN Tab

APPENDIX F — GLOBAL TIME SCHEDULE CONFIGURATION FOR i-Vu&#174; DEVICE

CSM CONTROLLER (cont)

[此处图片未下载成功]

Fig. F — Schedule Type Example (Weekly)

[此处图片未下载成功]

Fig. G — CCN Global Schedule Number

APPENDIX G — MAINTENANCE SUMMARY AND LOG SHEETS

XW Maintenance Interval Requirements

Oil Level.None.None.

://www.51wendang.com/doc/437ec10ed908de0667a81455mpressorCoolerCondenser

Oil Level.None.None.

Oil Level

refrigerant charge. Check all connec-tions for leaks.None.

Oil Level. Obtain and test an oil sam-ple.

refrigerant charge. Check all connec-tions for leaks. Check approach on unit to determine if tubes need cleaning. Check for temperature drop across filter drier to deter-mine if filter needs replacement.

all coils and clean. Check condenser approach to determine if tubes need to be cleaned.

proper operation of EXV's and TXV's

an Automated Controls test. Run all Compressors and ensure proper operation. Ensure operation of unit flow switch.

all electrical connections and tighten as needed. Measure current to eahttp://www.51wendang.com/doc/437ec10ed908de0667a81455ch compressor and inspect contac-tors.None.

an Automated Controls test. Run all Compressors  and ensure proper operation.

operation of units flow switch.None.

sight glass for moisture and refrigerant level.None.None.

Alarm/Alert History.None.

: Equipment failures caused by lack of adherence to the Main-tenance Interval Requirements are not covered under warranty.

APPENDIX G — MAINTENANCE SUMMARY AND LOG SHEETS

XW Weekly Maintenance Log

___________________________Machine Model No.  ________________DATE

LEVEL

ALARMS

/ FAULTS

: Equipment failures caused by lack of adherence to the Main-tenance Interval Requirements are not covered under warranty.

APPEDIX GN— AMNTENAICEN USMAMR YAN http://www.51wendang.com/doc/437ec10ed908de0667a81455DLG SHEETOS0X3W oMthly nMiatenance LngMonoth Daet Opreatr oNUI STCEITNO ATICO NCehc Okil Levle hCnge aOl Filiter( Scer Cwomrepsors)sSe dn ilOS mpale uO ftr oAnalsis yeaLkTest Ispentc&amp; lCae CnoleroT ubse Isnecpt ooler CHaetr eIspenctR elei VfalvseLeak T estR cerd oWaetr resPure Dsfferentiali(PSI )InpscteWat erPumps Eddy Crrenu Ttset eaLk Tet Inspscet C&amp;lea nonCender Tubes sRcord WaterePr esusreD fferienitl aPS(I) IspnectW aetrP ump asndC ooingl Tower Ispnec tReief VllavseG enrea Cllanengi&amp; igThteing Connecntois Chneck Pessurre ransducTesrCo firm nAccrucya o fThrmestoirs Genealr Tihgtnineg&amp; leaCnignC nnoctionesI spentcAll Cntoatocr sCheck Rfreieganr thaCgr Level Vereiy OpfreaiontO f XV's AEn Record Pdostiino RecordS stym Sueerp Hat UNeI yTs/noeye/sn yoesno/ pp mysen/ amps yes/oonye s/onPSI ye s/o yes/nno pp yms/ne PoS yIe/so nysen/ oeys/onyes n/ yeo/no syesn/ yoe/so nys/eon0 -001?. Fg/ 1//2// 3///4 5/// 6// 7//8 / 9//http://www.51wendang.com/doc/437ec10ed908de0667a81455 1 0// 1/ 1 12///ENTYRY aer th1ne sA Neede dnAnaulylE veyr3 -5 YaesrCoprmesosrColer

E3- 5 eYrsa nAnaull

r46onCrtol Ssatrert Sysemt

aNOTE E:qupmietnfai lrues acues bd yaclkof a hdernceeto he MtanitnencaeI tnrvaleRequirem ens ate rno toveced unrdr weraantr.y

[此处图片未下载成功]

PPNDEX IG—MAI TENANNCESUM AMR AYDN LG SOHEES30TXWSea onsl aShtdouw LngoMonh Datt eperaOot rNITUSE TICNO ooler CCTIONAI osltaeand D arni atWrebxoR emov Watereox bCveo rfor mnO end UEesC mporseed Asr itoCl eanTu es Isolbat eadnDrain aWtreoxbR meoevW atrbex Coveorfr m oOenEn d se CoUpmrsese Air tdo Cean Tules Do NotbD icosne

Cnotrlo Poerw 1///2// 3//  4/ 5///6 //7// 8/ //9 01// 11// 1 2//ETNRYCnodnesreCo nrotls

:N Eqipmeuntf iluarse acusd ebyla c kfo aheredce not teh Maitnennaec Inertvl aReqiuremnet arse otnco verd uedenrwa rarnt.y14

http://www.51wendang.com/doc/437ec10ed908de0667a81455I

[此处图片未下载成功]

INDEX

-20 mA temperature reset      36Actual start-up      46Alarms and alerts      68Alarm control      42

priority      42Routing control      42System name      42Board addresses      17

or glycol operation      28Broadcast acknowledger      20, 41Broadcast configuration      40Capacity control overrides      42

Comfort Network&#174; (CCN)      18Interface      18

controlled demand limit      40Tables      121-135

water flow switch      69

water fluid type selection      27Circuit/compressor staging and loading      29Loading      29Staging      29

failure retry time      42Compressor      Assembly      65Oil system      65Protection      10,71Compressor protection module (CPM)      10Configuration      18-46

module communication      17Controls      9-18

://www.51wendang.com/doc/437ec10ed908de0667a81455entions used in this manual      3Cooler      68

control      28

set point selection      25

DIP switch addresses      136-138Daylight saving time configuration      42Demand limit      39

powered capacity based      39Externally powered current based      40Switch controlled      39Diagnostic alarm codes and possible causes      72Display module usage      3Dual chiller control      30

parallel applications      30For series applications      30Pump control for parallel chiller applications      30Pump control for series chiller applications      30

chiller sequence of operation      56Dual pump and manual control      29Economizer assembly      63

expansion valve (EXV)      63EXV board      13EXV control      63

EXV control      63

procedure      64Emergency on/off switch (SW2)      16Enable-off-remotehttp://www.51wendang.com/doc/437ec10ed908de0667a81455 contact switch (SW1)      16

Management Module (EMM)      16Entering fluid control option      25Flow rate requirements      47Freeze protection      42Fresh water      28

(Controls)      9

time schedule configuration      141-143Green LED      17

pressure control      45

exchangers, inspecting/cleaning      66Heating set point selection      27

2010 Carrier Corporation

reserves the right to discontinue, or change at any time, specifications or designs without notice and without incurring obligations.

No. 04-53300062-01Printed in U.S.A.Form 30XW-2TPg 1487-10Replaces: 30XW-1T

storage operation      40

testing      70

equipment network      17Loss of fluid flow protection      68Low condenser fluid temperature Head pressure control      45Option      45

fluid temperature http://www.51wendang.com/doc/437ec10ed908de0667a81455     68Machine control methods      20Machine on/off control      20Machine start delay      29

Base Board (MBB)      9Maintenance      71

summary and log sheets      144-147Minimum fluid loop volume      47Minimum load control      30MLV/condenser board      15Navigator  display module      7Machine control      23

display tables      108-120No pump control      28Operating limitations      46Operating modes      56Operation      56-63

and instrumentation      139, 140Pressure relief valves      71Pre-start-up      46Pump operation      56Ramp loading      35Re-alarm time      42

maintenance schedule      71Red LED      17

charge      70Refrigerant circuit      70Relief devices      71

alarm and alert relays      18Retubing      69

water reset      35Safety considerations      2Safety devices      70Sensorshttp://www.51wendang.com/doc/437ec10ed908de0667a81455      58

of operation      56Service      63-71Service test      86

point occupancy      25Single pump control      29Space temperature reset      35Start-up      46-56

-up checklist for

XW liquid chillers      CL-1 to CL-7Suction service valve      68System check      46Temperature reset      35Thermistors      58

cooler head bolts      69Touch Pilot display      3,17Display tables      89-107Machine control      20

configuration tables      18Transducers      59

71-88Tube plugging      68Voltage      47

treatment      69Yellow LED      17

START-UP CHECKLIST FOR 30XW LIQUID CHILLERS

.PROJECT INFORMATION

Name________________________________________________________________________________________Address____________________________________________________________________________________http://www.51wendang.com/doc/437ec10ed908de0667a81455______City ________________________________State________________________ Zip  ___________________________Installing Contractor________________________________________________________________________________Sales Office_______________________________________________________________________________________Start-up Performed By______________________________________________________________________________

Information

TYPE

RATE

.D.

_______________________________________Serial ______________________________________

A

_______________________________________Compressor B

_______________________________________Evaporator

_______________________________________Condenser

_______________________________________

://www.51wendang.com/doc/437ec10ed908de0667a81455l ______________________________________Serial ______________________________________Serial ______________________________________Serial ______________________________________

.PRELIMINARY EQUIPMENT CHECK (This section to be completed by installing contractor)

.Is there any physical damage? Yes No      Will this prevent start-up? Yes No      Description

___________________________________________________________________________________________  ___________________________________________________________________________________________2.Unit is installed level as per the installation instructions. Yes No3.Power supply agrees with the unit nameplate. Yes No4.Correct control voltage ________vac. Yes No5.Electrical power wiring is installed properly. Yes No6.Unit is properly grounded. Yes No7.Electrical circuit protection has been sized and installed properly. Yes No8.All terminals are tight. Yes No9.All plug assemhttp://www.51wendang.com/doc/437ec10ed908de0667a81455blies are tight. Yes No10.All cables, thermistors and transducers have been inspected for cross wires. Yes No11.All thermistors are fully inserted into wells. Yes No12.Relief valve vent piping per local codes. Yes No13.Mechanical room temperature maintained above 50 F (10 C). Yes No

Water System Check

chilled water valves are open.

piping is connected properly.

air has been purged from the system.

water pump is operating with the correct rotation.Chilled water pump starter interlocked with chiller.Chilled water flow switch operational.

piping to evaporator includes a 20 mesh strainer within 10 ft.Water loop volume greater than 3 gal/ton for air conditioning  or 6 gal/ton for process cooling and low ambient operation.

.Proper loop freeze protection provided to ____  F ( C) for brine applications.Antifreeze type__________________  Concentration _____%.1http://www.51wendang.com/doc/437ec10ed908de0667a814550.Outdoor piping wrapped with electric heater tape.1.2.3.4.5.6.7.8.

YesYesYesYesYesYesYesYesYesYesYes

NoNoNoNoNoNoNoNoNoNoNo

reserves the right to discontinue, or change at any time, specifications or designs without notice and without incurring obligations.

No. 04-53300062-01Printed in U.S.A.Form 30XW-2TCL-17-10Replaces: 30XW-1T

Condenser Water System Check

.All condenser water valves are open.2.All piping is connected properly.

.All air has been purged from the system.

.Condenser water pump is operating with the correct rotation.5.Condenser water pump starter interlocked with chiller.6.Condenser water flow switch operational.

.Inlet piping to condenser includes a 20 mesh strainer within 10 ft.8.Outdoor piping wrapped with electric heater tape.9.

(Required for entering condenser water below 65 F (18.3 C).)

://www.51wendang.com/doc/437ec10ed908de0667a81455 system equipped with head pressure control?

. UNIT START-UP

.All liquid line service valves are open.2.All discharge service valves are open.3.All suction service valves are open.

.Economizer service valves open (if equipped).5.Oil service valves open.

.Leak check unit. Locate, repair and report any refrigerant leaks.7.Voltage at terminal block is within unit nameplate range.

voltage imbalance:    A-B______ A-C______B-C______Average voltage = __________ (A-B   A-C   B-C)/3Maximum deviation from average voltage = _______

imbalance = ______% (max. deviation / average voltage) X 100Is voltage imbalance less than 2%.

(DO NOT start chiller if voltage imbalance is greater than 2%. Contact local utility for assistance.)8.Verify evaporator flow ratePressure entering evaporator _____ psigPressure leaving evaporator _____ psigEvaporator pressure drop _____ psigpsig x 2.31 ft/phttp://www.51wendang.com/doc/437ec10ed908de0667a81455si = _____ ft of waterkpa x 0.334 m/psi = _____ mm of water

flow rate _____ gpm (l/s) (See Evaporator Pressure Drop Curve)9.Verify condenser flow ratePressure entering condenser _____ psigPressure leaving condenser _____ psigCondenser pressure drop _____ psigpsig x 2.31 ft/psi = _____ ft of waterkpa x 0.334 m/psi = _____ mm of water

flow rate _____ gpm (l/s) (See Condenser Pressure Drop Curve)

and Operate Machine

://www.51wendang.complete component test utilizing Quick Test Mode

.Check refrigerant and oil charge. Record charge information.3.Record compressor motor current.4.Record operating data.

.Provide operating instructions to owner’s personnel.

ACircuit B

Charge

charge required

_____________________Oil Charge

charge required

__________

___________

://www.51wendang.com/doc/437ec10ed908de0667a81455-2

Yes No Yes No Yes No Yes No Yes No Yes No Yes No Yes

No

Yes No

Yes No Yes No Yes No Yes No Yes No Yes No Yes

No

Yes No

- - - - - - - - - - - - - - - - - - - -- - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - -E

- N-I L-  - D- E- T- - -OT -D  - -G -N - O- L- A-  -T - U- C- - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - E- N-I -L  - -D -E -T - - OT- D-  - G- N- -O L- -A  - T- U- -C - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - -

Record Software Versions

PILOT  DESRIPTION

Part Number

ITEM

SUB-MODE

StatusVERS

EXPANSION

-SR-  __ __ __ __ __ __

(Press ENTER &amp; ESCAPE simultaneously to obtain software versions)

Configurationhttp://www.51wendang.com/doc/437ec10ed908de0667a81455 Information

PILOTNAVIGATOR NAVIGATOR RANGEDESCRIPTIONITEMSUBMODE

Display on STDUMETRConfigurationDISPUS-METRLanguage SelectionLANGConfigurationDISPxUnit TypeTYPEConfigurationUNITxUnit Capacity ModelTONSConfigurationUNITXXXPower Supply VoltageVOLTConfigurationUNIT200-690Power Frequency 60HZ Sel60HZConfigurationUNITNO-YESWye Delta Start SelectY.DConfigurationUNITNO-YESMust Trip Amps (Circuit A)MTA.AConfigurationUNITXXXMust Trip Amps (Read Circuit A)R.MT.AConfigurationUNITXXXMust Trip Amps (Circuit B)MTA.BConfigurationUNITXXXMust Trip Amps (Read Circuit B)R.MT.BConfigurationUNITXXXS1 Config Switch (Circuit A)C.SW.AConfigurationUNITXXXS1 Config Switch R.CSAConfigurationUNITXXX(Read Circuit A)

Config Switch (Circuit B)C.SW.BConfigurationUNITXXXS1 Config Switch R.CSBConfigurationUNITXXX(Read Circuit B)

Management ModuleEMMConfigurationUNITNO-YESPassword EnablePAS.EConfigurationUNITENBL/DShttp://www.51wendang.com/doc/437ec10ed908de0667a81455BLFactory PasswordPASSConfigurationUNITXXXCondenser Water Val SelCON.VConfigurationUNITNO-YESHot Gas Bypass SelectHGBPConfigurationUNITNO-YESHigh Tier Display SelecHI.TIConfigurationUNITNO-YESCooler Pass NumberPA.NBConfigurationUNITXHigh Condensing SelectH.CONConfigurationUNITNO-YESCooler Fluid TypeFLUDConfigurationSERVWATER-BRINECondenser Fluid TypeCFLUConfigurationSERVWATER-BRINEEXV MOP SetpointMOPConfigurationSERVXX.XHigh Pressure ThresholdHP.THConfigurationSERVXXX.XEXV A Superheat SetpointSHP.AConfigurationSERVXX.XEXV B Superheat SetpointSHP.BConfigurationSERVXX.XEntering Fluid ControlEWTOConfigurationSERVNO-YESAuto Start When SM LostAU.SMConfigurationSERVNO-YESBrine Minimum Fluid TempLLWTConfigurationSERVXXBrine Freeze SetpointLOSPConfigurationSERVXX.XFast Load SelectF.LOAConfigurationSERVXEWT Probe on Cir A SideEWT.SConfigurationSERVNO-YESMax Condenser LWT 45DCMAXLConfigurationSERVNO-YES

://www.51wendang.com/doc/437ec10ed908de0667a81455par-Cooled

, 230, 380, 460, and 575YESNO

NONONO2NOWATERWATER6229014.414.4NONO38340YESNO

Record Configuration Information

PILOT  DESCRIPTION

Rate

Loading SequenceStaged Loading SequenceRamp Loading SelectUnit Off to On DelayIce Mode Enable

Pumps SequenceCooler Pumps SequencePump Auto Rotation DelayPump Sticking ProtectionNAVIGATOR

.SDELYICE.MHPUMPUMPROT.PPM.PSNAVIGATOR  SUBMODE

OPTNConfiguration OPTNConfiguration OPTNConfigurationOPTNConfiguration OPTNConfigurationOPTNConfiguration OPTNConfigurationOPTNConfiguration OPTNConfigurationOPTNConfiguration OPTNRANGEXXXXXXXXX

-DSBL

-DSBL

-YESDEFAULT103/9600EQUALAUTOMATIC

DSBL0/NO PUMP0/NO PUMP

NOENTRY

- - - http://www.51wendang.com/doc/437ec10ed908de0667a81455- - - - - - - - - - - - - - - - - - - - - - - - - -- - - - - - - - - - - - - - - - - - - -Stop Pump During StandbyP.SBYConfigurationOPTNNO-YESNOFlow Checked if C Pump OnP.LOCConfiguration OPTNNO-YESNOStart Hour (Night Control)LS.STConfigurationOPTNXX.XX00.00End Hour (Night Control)

.NDConfiguration OPTNXX.XX00.00Capacity Limit (Night Control)LS.LTConfigurationOPTNXXX100Reverse Alarms RelayRV.ALConfiguration OPTNNO-YESNOCurrent Limit SelectCUR.SConfigurationOPTNNO-YESNOCurrent Limit at 100%CUR.FConfiguration OPTNXXXX2000Cooling Reset Select

Demand Limit Type SelectDMDCConfiguration RSETX0mA for 100% Demand LimitDMMXConfigurationRSETXX.X0.0mA for 0% Demand LimitDMZEConfiguration RSETXX.X0.0Master/Slave SelectMSSLConfigurationRSETX0Slave AddressSLVAConfiguration RSETXXX2Lead/Lag Select

/Lag Balance DeltaLLBDConfiguration RSETXXX168Lag Start TimerLLDYConfiguratiohttp://www.51wendang.com/doc/437ec10ed908de0667a81455nRSETXX10Start if Error Higher

.ERConfiguration RSETXX.X4Lag Minimum Running TimeLAG.MConfigurationRSETXXX0Lag Unit Pump ControlLAGPConfiguration RSETX0Lead Pulldown TimeLPULConfigurationRSETXX0Chiller in Series

RSET

-YES

DETOTD GNOLA TUCENIL DETOTD GNOLA TUC - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - -

Record Configuration Information

PILOT DESCRIPTION

Setpoint 1Cooling Setpoint 2Cooling Ice Setpoint

No Reset Value (Cooling)Current Full Reset Value (Cooling)Delta T No Reset Value (Cooling)Delta T Full Reset Value (Cooling)OAT No Reset Value (Cooling)OAhttp://www.51wendang.com/doc/437ec10ed908de0667a81455T Full Reset Value (Cooling)Space T No Reset ValueSpace T Full Reset ValueCooling Reset Deg. ValueCooling Ramp LoadingHeating Setpoint 1Heating Setpoint 2

No Reset Value (Heating)Current Full Reset Value (Heating)Delta T No Reset Value (Heating)Delta T Full Reset Value (Heating)OAT No Reset Value (Heating)OAT Full Reset Value (Heating)Heating Reset Deg. ValueHeating Changeover SetpointHeat Ramp LoadingSwitch Limit Setpoint 1Switch Limit Setpoint 2Switch Limit Setpoint 3Water Val Condensing StpNone (I/O Button)Setpoint SelectHeal/Cool Select

.1CSP.2CSP.3CRV1CRV2CRT1CRT2CRO1CRO2CRS1CRS2DGRCCRMPHSP.1HSP.2HRV1HRV2HRT1HRT2HRO1HRO2DGRHHAUTHRMPDLS1DLS2DLS3W.SCTOPERSP.SEHC.SE

SUBMODE

PointCOOLSet Point COOLSet PointCOOLSet Point COOLSet Point COOLSet Point COOLSet PointCOOLSet Point COOLSet Point COOLSet Point COOLSet Point COOLSet Point COOLSet PointCOOLSet Point HEAhttp://www.51wendang.com/doc/437ec10ed908de0667a81455TSet Point HEATSet Point HEATSet Point HEATSet Point HEATSet PointHEATSet Point HEATSet Point HEATSet Point HEATSet Point HEATSet Point HEATSet PointMISCSet Point MISCSet Point MISCSet Point MISC

Modes SLCTOperating Modes SLCTOperating Modes SLCT

.XXXX.XXXX.XXXX.XXXX.XXXX.XXXX.XXXX.XXXX.XXXX.XXXX.XXX.XX.XXXX.XXXX.XXXX.XXXX.XXXX.XXXX.XXXX.XXXX.XXX.XXX.XX.XXXXXXXXXXXXX.XXXX

.0&#176; F44.0&#176; F44.0&#176; F000014.0&#176; F14.0&#176; F14.0&#176; F14.0&#176; F01.0100.0&#176; F100.0&#176; F

.0&#176; F14.0&#176; F064.0&#176; F1.010010010095.0&#176; F——COOLING

Component Test — Complete the following tests to make sure all peripheral components areoperational before the compressors are started.

PILOT  DESCRIPTIONService Test EnableCompressor A OutputSlide Valve Capacity ACompressor B OutputSlide Valve Capacity BQuick Test EnableCircuihttp://www.51wendang.com/doc/437ec10ed908de0667a81455t A EXV PositionCircuit B EXV Position

A Economizer EXV PositionCir B Economizer EXV PositionCircuit A Fan StagesNAVIGATOR ITEM

.REQCP.ASLI.ACP.BSLI.BQ.REQEXV.AEXV.BECO.AECO.BFANANAVIGATOR  SUBMODE

Test TESTService Test TESTService Test TESTService TestTESTService Test TESTService TestQUICService Test QUICService TestQUICService Test QUICService TestQUICService Test QUICRANGEOFF-ONOFF-ON0-2OFF-ON0-2OFF-ONXXXXXXXXXXXX0-8CHECK WHEN COMPLETE

- - - - - - - - - - - - - - - - - - - - - - - - - - - - -- - - - - - - - - - - - - - - - - - - -Circuit B Fan StagesFANBService TestQUIC0-8Cir A Varifan PositionSPD.AService Test QUIC0-100Cir B Varifan PositionSPD.BService TestQUIC0-100Circuit A Oil HeaterHT.AService Test QUICOFF-ONCircuit A Slide Valve 1SL1.AService TestQUICOFF-ONCircuit A Slide Valve 2SL2.AService Test QUICOFF-ONCircuit A Hot Gas BypassHGP.AService TestQUICOFF-ONCircuit A Oil Solenoid

://www.51wendang.com/doc/437ec10ed908de0667a81455arOLS.AService Test QUICOFF-ONCircuit A DGT Cool SolenoidDGT.AService TestQUICOFF-ONCircuit B Oil HeaterHT.BService Test QUICOFF-ONCircuit B Slide Valve 1SL1.BService TestQUICOFF-ONCircuit B Slide Valve 2SL2.BService Test QUICOFF-ONCircuit B Hot Gas BypassHGP.BService TestQUICOFF-ONCircuit B Oil Solenoid

.BService Test QUICOFF-ONCircuit B DGT Cool SolenoidDGT.BService TestQUICOFF-ONWater Exchanger Pump 1PMP.1Service Test QUICOFF-ONWater Exchanger Pump 2PMP.2Service TestQUICOFF-ONCooler Heater OutputCL.HTService Test QUICOFF-ONCir A Heater Ball ValveBVL.AService TestQUICOPEN-CLSECir B Heater Ball ValveBVL.BService Test QUICOPEN-CLSEChiller Ready StatusQ.RDYService TestQUICOFF-ONChiller Running OutputQ.RUNService Test QUICOFF-ONCustomer Shutdown OutSHUTService TestQUICOFF-ONChiller Capacity in 0-10VCATOService Test QUICnn.nAlarm Relay OutputALRMService TestQUICOFF-ONAlert Relay Output

Test QUIC

://www.51wendang.com/doc/437ec10ed908de0667a81455parOFF-ON

DETOTD GNOLA TUCENIL DETOTD GNOLA TUC - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - -

Operating Data:

the following information from the Run Status, Temperatures and Outputs Modes when machine is in a stable operating condition.TEMPERATURES

ENTERING FLUIDCOOLER LEAVING FLUID

ENTERING FLUIDCONDENSER LEAVING FLUIDCONTROL POINTCAPACITY

/LAG LEAVING FLUID

_______________LWT  _______________EWT  _______________LWT  _______________CTPT _______________CAP   _______________

_______________    (Dual Chiller Control Only)

ACIRCUIT B      SCT.A __________SCT.B ______http://www.51wendang.com/doc/437ec10ed908de0667a81455____SST.A __________SST.B  __________DGT.A __________DGT.B  __________SGT.A __________SGT.B  __________SUP.A __________SUP.B  __________ECT.A __________ECT.B  __________ESH.A __________ESH.B  __________CTP.A __________CTP.B  __________EXV.A__________EXV.B  __________ECO.A__________ECO.B  __________

: EXV A and B positions are found in the output http://www.51wendang.comPRESSOR MOTOR CURRENT

L2

A1____________COMPRESSOR B1____________

____________

:

__________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________http://www.51wendang.com/doc/437ec10ed908de0667a81455___________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________http://www.51wendang.com/doc/437ec10ed908de0667a81455___________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________SIGNATURES:Start-up

_____________________________________Customer

__________________________________

________________________________________________

________________________________________________

- - - - - - - - - - - - - - - - - - - - - - - - - - - - -- - - - - - - - - - - - - - - - - - - -Copyright 2010 Carrier Corporation

reserveshttp://www.51wendang.com/doc/437ec10ed908de0667a81455 the right to discontinue, or change at any time, specifications or designs without notice and without incurring obligations.

No. 04-53300062-01Printed in U.S.A.Form 30XW-2TCL-8          7-10A      7-10Replaces: 30XW-1T

DETOTD GNOLA TUCENIL DETOTD GNOLA TUC - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - -

文档下载网是专业的免费文档搜索与下载网站，提供行业资料，考试资料，教学课件，学术论文，技术资料，研究报告，工作范文，资格考试，word文档，专业文献，应用文书，行业论文等文档搜索与文档下载，是您文档写作和查找参考资料的必备网站。

文档下载 https://www.51wendang.com/

亿万文档资料，等你来发现