# CONTENTS

1	Scope	11

1.1	Scope of full standard	11

1.2	Scope of this part of IEC 61968	11

2	Normative , informative, mandatory, and optional material	12

2.1	Normative references	12

2.2	Informative material	12

2.3	Normative material	12

2.3.1	Mandatory vs. Optional	13

3	Terms, definitions and abbreviations	14

3.1	Terms and definitions	14

3.1.1	General	14

3.2	Abbreviations	14

4	Reference and Information Models	16

4.1	General approach to metering systems	16

4.2	Reference Model	17

4.2.1	General	17

4.2.2	Metering System (MS) - Data Collection	20

4.2.3	Metering System (MS) - Control and Reconfiguration	21

4.2.4	Load Control	21

4.2.5	Load Management System (LMS)	21

4.2.6	Outage Management System (OMS)	22

4.2.7	Meter Asset Management (MAM) System	22

4.2.8	Meter Data Management (MDM) System	22

4.2.9	Customer Information System (CIS)	22

4.2.10	Network Operations (NO)	22

4.2.11	Meter Maintenance (MM)	23

4.2.12	Planning	23

4.2.13	Work Management (WM)	23

4.2.14	Point of Sale (POS)	23

4.2.15	Meter	23

4.2.16	Load control devices	23

4.3	Interface Reference Model	24

4.4	Meter reading and control functions and components	24

4.5	Static Information Model	26

4.5.1	General	26

4.5.2	Classes for meter reading and control	26

4.5.3	Classes related to meter reading and control	31

5	Meter reading and control message types	32

5.1	General	32

5.2	End device event messages	32

5.2.1	General	32

5.2.2	Applications	32

5.2.3	Message format	38

5.3	Synchronization between systems	39

5.3.1	General	39

5.3.2	Applications	40

5.3.3	Message format	44

5.4	Meter reading messages	46

5.4.1	General	46

5.4.2	Applications	46

5.4.3	Message format	54

5.5	End device control messages	55

5.5.1	General	55

5.5.2	Applications	55

5.5.3	Message format	63

5.6	Meter service requests	64

5.6.1	General	64

5.6.2	Applications	64

5.6.3	Message format	68

5.7	Metering system events	69

5.7.1	General	69

5.7.2	Applications	70

5.7.3	Message formats	71

5.8	Customer switching	74

5.8.1	General	74

5.8.2	Message format	74

5.9	Payment metering service messages	75

5.9.1	General	75

5.9.2	MS information configuration	75

5.9.3	MS financial information	95

Annex A (Informative)  Description of message type verbs	100

Annex B (Informative)  Recommended message structure	103

Annex C (Informative)  Recommended procedure for the generation of a ReadingType	109

C.1	General	109

C.2	Understanding the important attributes of a data element name	109

C.2.1	General	109

C.2.2	Attribute #1, Time Attribute Enumerations	109

C.2.3	Attribute #2, Data Qualifier	110

C.2.4	Attribute #3, Accumulation behaviour	111

C.2.5	Attribute #4, Direction of flow	112

C.2.6	Attribute #5, Unit of Measure Category	113

C.2.7	Attribute #6, Measurement Category Enumerations	116

C.2.8	Attribute #7, Phase	117

C.2.9	Attribute #8, Metric Multiplier	118

C.2.10	Attribute #9, Displayable Unit of Measure (UOM)	119

C.3	Using data element attributes to define the ReadingType	121

C.3.1	General	121

Annex D (Informative)  Recommended Quality Code enumerations	124

D.1	General	124

D.2	Identification of the system offering commentary on the data	124

D.3	Quality Code Categorization	124

D.4	Quality Code Index	125

D.5	Categorized Quality Codes With Originator Identifier	126

Annex E (Informative)  Recommended EndDeviceEvent Category Enumerations	128

E.1	General	128

E.2	EndDeviceEvent Domains	128

E.3	EndDeviceEvent Domain Parts	128

E.4	EndDeviceEvent types	129

E.5	EndDeviceEvent Index	130

E.6	Numbered Values	136

E.7	Example EndDeviceEvent Codes	136

E.8	Example EndDeviceEvent Request codes	150

Annex F (Informative)  Recommended EndDeviceControl Code Enumerations	151

F.1	General	151

F.2	Example EndDeviceControl Codes	151

Annex G (Informative)  Recommended procedure for maintaining relationships between objects	153

G.1	General	153

G.2	Object Identifiers	153

G.3	CIM based message exchanges	154

G.3.1	Initialization	154

G.3.2	Installation	154

G.3.3	Updates	154

G.4	Example	155

Annex H (Normative)  XML Schemas for Message Payloads	156

H.1	General	156

H.2	CustomerMeterDataSet	156

H.3	MeterAssetReading	163

H.4	EndDeviceControls	165

H.5	EndDeviceEvents	167

H.6	MeterReadings	168

H.7	MeterReadSchedule	173

H.8	MeterServiceRequest	175

H.9	MeterSystemEvent	182

H.10	EndDeviceAssets	184

H.11	EndDeviceFirmware	194

H.12	SupplierConfig	195

H.13	CustomerConfig	199

H.14	ServiceCategoryConfig	203

H.15	PricingStructureConfig	204

H.16	CustomerAccountConfig	213

H.17	CustomerAgreementConfig	214

H.18	AuxilaryAgreementConfig	217

H.19	MeterAssetConfig	223

H.20	ServiceDeliveryPointConfig	226

H.21	ServiceLocationConfig	229

H.22	SDPLocationConfig	234

H.23	ReceiptRecord	239

H.24	TransactionRecord	243

Annex I (Informative)  Mappings to ebIX	251

I.1	General	251

Annex J (Informative)  Request Parameters	258

J.1	General	258

J.2	GetMeterReadings	258

J.3	GetEndDeviceAssets	259

J.4	GetCustomerMeterDataSet	260

Figure 1 – Example of an end device with functions	18

Figure 2 – Part 9 reference model	19

Figure 3 -- Part 9 Reference Model with Customer Information and Billing System	20

Figure 4 -- Outage Detection, request / reply message exchange, Example 1	33

Figure 5 -- Outage Detection, request / reply message exchange, Example 2	34

Figure 6 -- Outage Detection, publish/subscribe exchange, Example 1	35

Figure 7 -- Outage Detection, publish/subscribe exchange, Example 2	35

Figure 8 – Meter Health Event exchange, Example 1	36

Figure 9 -- Meter Health Event exchange, Example 2	36

Figure 10 -- Power quality event exchange, Example 1	37

Figure 11--Power quality event exchange, Example 2	38

Figure 12--End device event message format	39

Figure 13--Example of meter asset management subscriptions	40

Figure 14 – Example of meter asset management publications	41

Figure 15 – Example of WM to MAM exchange – test results	41

Figure 16– Example of WM to MAM exchange – asset status update	42

Figure 17 – Example of reciprocal subscriptions (with MDM present)	43

Figure 18 – Example of synchronization exchanges	44

Figure 19 – End device asset message format	45

Figure 20 – Customer meter data set message format	45

Figure 21 – Example use of meter read schedule to create subscription	47

Figure 22 – Meter read schedule message format	48

Figure 23 – Meter readings message format	49

Figure 24 – Example manual meter reading exchange	51

Figure 25 – Example On-Request meter read exchange	52

Figure 26 – HistoricalMeterData exchange	53

Figure 27– Example billing inquiry message exchange	54

Figure 28 – Meter asset reading message format	55

Figure 29 – Example load control message exchange	56

Figure 30 – Example message exchange for LC unit installation	57

Figure 31 – Example message exchange for change of customer program (meter reconfigured)	58

Figure 32-- Example message exchange for meter reconfiguration due to change of customer program where there is no MDM	59

Figure 33 – Example message exchange for change of customer program with meter changed out	60

Figure 34 – Example message exchange for meter connect / disconnect	61

Figure 35-- Example message exchange for remote connect/disconnect operation directly between a CIS and MS	62

Figure 36 – Example message exchange for real-time price signal	63

Figure 37 – End device controls message format	64

Figure 38 – Example meter installation and removal message exchange	65

Figure 39 – Example end device event message exchange due to meter changeout	66

Figure 40 – Example message exchange due to CIS alarms	67

Figure 41 – Example message exchange when meter is changed out for recalibration	68

Figure 42 – Meter service requests message format	69

Figure 43 – Example MeterSystemHealth message exchange	70

Figure 44 – Example firmware upgrade message exchange	71

Figure 45 – Example meter system event message format	72

Figure 46 – End device firmware message format	73

Figure 47 – Example customer switching message exchange	74

Figure 48 -- Message exchange for transferring supplier information	76

Figure 49 -- Supplier configuration message format	76

Figure 50 – Message exchange for transferring customer information	77

Figure 51 -- Customer configuration message	78

Figure 52 – Message exchange for transferring customer agreement information	79

Figure 53 -- Customer agreement configuration message	79

Figure 54 – Message exchange for transferring customer account information	80

Figure 55 – Customer account configuration message	81

Figure 56 – Message exchange for transferring auxiliary agreement information	82

Figure 57 -- Auxiliary agreement configuration message format	83

Figure 58 – Message exchange for transferring pricing structures	84

Figure 59 – PricingStructureConfig message format	85

Figure 60 – Message exchange for transferring service category information	86

Figure 61 – ServiceCategoryConfig message format	86

Figure 62 – Message exchange for transferring service delivery point information	87

Figure 63 – ServiceDeliveryPointConfig message format	88

Figure 64 – Message exchange for transferring meter information	89

Figure 65 – Meter asset configuration message	90

Figure 66 -- Message exchange for transferring service delivery point location information	91

Figure 67 – SDPLocationConfig message format	92

Figure 68 – Message exchange for transferring service location information	93

Figure 69 – ServiceLocationConfig message format	94

Figure 70 -- Message exchange for transferring receipt information	95

Figure 71 – ReceiptRecord message format	96

Figure 72 – Message exchange for transferring transaction information	97

Figure 73 – TransactionRecord message format	98

Figure B.1 – Recommended Message message-format	103

Figure B.2 – Recommended.Header message format	104

Figure B.3 – Recommended.RequestType message format	104

Figure B.4 – Recommended.ReplyType message format	105

Figure G.1 – Typical CIM Naming Object	153

Figure I.1 - ebIX XML Schema	252

Figure I.1 - ebIX XML Schema (continued)	253

Figure I.2 - ebIX Metered Data as UML Class Diagram Table I.3 - Meter Reading: Mapping ebIX Metered Data to IEC MeterReadings	254

Table I.3 - Meter Reading: Mapping ebIX Metered Data to IEC MeterReadings	255

Figure J.1 - Message Request Structure	258

Figure J.2 - GetMeterReadings	259

Figure J.3 - GetEndDeviceAssets	260

Figure J.4 - 	GetCustomerMeterDataSet	261

Table 1 – Business Functions and Abstract Components	25

Table 2 – Classes for meter reading and control	26

Table 3 – Classes related to meter reading and control	31

Table A.1 – Commonly used Verbs	100

Table B.1 – ReplyCode Categories	105

Table B.2 – Refresh Rate Enumerations	105

Table C.1 – Time Attribute Enumerations	109

Table C.2 -- Data Qualifier Enumerations	110

Table C.3 – Accumulation Behaviour Enumerations	111

Table C.4 – Direction Of Flow Enumerations	112

Table C.5 – Unit of Measure Enumerations	113

Table C.6 – Measurement Categories	116

Table C.7 – MeasurementCategory Enumerations	116

Table C.8 – Phase Enumerations	117

Table C.9 – Metric Multiplier Enumerations	118

Table C.10 – Unit of Measure Enumerations	119

Table C.11 – Example ReadingTypes	122

Table D.1 – Example System IdentifiersValue	124

Table D.2 – Example Quality Code Categories	125

Table D.3 – Example Categorized Codes	125

Table D.4 – Example Quality Codes	127

Table E.1 – Example EndDeviceEvent Domain Codes	128

Table E.2 – Example EndDeviceEvent Domain Part Codes	128

Table E.3 – Example EndDeviceEvent Type Codes	129

Table E.4 – Example EndDeviceEvent Indexes	130

Table E.5 – Example EndDeviceEvent Codes	136

Table E.6 – Example EndDeviceEvent Codes	150

Table F.1 – Comparison of example Demand Reset Codes	151

Table F.2 – Example EndDevice Control Codes	151

Table G.1 – Example meter relationships	155

# INTERNATIONAL ELECTROTECHNICAL COMMISSION

System Interfaces For Distribution Management –

# Part 9: Interface Standard for Meter Reading and Control

# FOREWORD

1)	The IEC (International Electrotechnical Commission) is a worldwide organization for standardization comprising all national electrotechnical committees (IEC National Committees). The object of the IEC is to promote international co-operation on all questions concerning standardization in the electrical and electronic fields. To this end and in addition to other activities, the IEC publishes International Standards. Their preparation is entrusted to technical committees; any IEC National Committee interested in the subject dealt with may participate in this preparatory work. International, governmental and non-governmental organizations liaising with the IEC also participate in this preparation. The IEC collaborates closely with the International Organization for Standardization (ISO) in accordance with conditions determined by agreement between the two organizations.

2)	The formal decisions or agreements of the IEC on technical matters express, as nearly as possible, an international consensus of opinion on the relevant subjects since each technical committee has representation from all interested National Committees.

3)	The documents produced have the form of recommendations for international use and are published in the form of standards, technical reports or guides and they are accepted by the National Committees in that sense.

4)	In order to promote international unification, IEC National Committees undertake to apply IEC International Standards transparently to the maximum extent possible in their national and regional standards. Any divergence between the IEC Standard and the corresponding national or regional standard shall be clearly indicated in the latter.

5)	The IEC provides no marking procedure to indicate its approval and cannot be rendered responsible for any equipment declared to be in conformity with one of its standards.

- Attention is drawn to the possibility that some of the elements of this International Standard may be the subject of patent rights. The IEC shall not be held responsible for identifying any or all such patent rights.

International Standard IEC 61968 has been prepared by Working Group 14, of IEC technical committee 57: Power System Control and Associated Communications.

The text of this standard is based on the following documents:

| FDIS | Report on voting |
| --- | --- |
| 57/----- | 57/------ |

Full information on the voting for the approval of this standard can be found in the report on voting indicated in the above table.

# INTRODUCTION

The purpose of this document is to define a standard for the integration of Metering Systems (MS), which would include traditional (one or two-way) Automated Meter Reading (AMR) Systems, with other systems and business functions within the scope of IEC 61968. The scope of this standard is the exchange of information between a Metering System and other systems within the utility enterprise. The specific details of communication protocols those systems employ are outside the scope of this standard. Instead, this standard will recognize and model the general capabilities that can be potentially provided by advanced and/or legacy meter infrastructures, including two-way communication capabilities such as load control, dynamic pricing, outage detection, distributed energy resource (DER) control signals and on-request read. In this way, this standard will not be impacted by the specification, development and/or deployment of next generation meter infrastructures, either through the use of standards or proprietary means.

The IEC 61968 series of standards is intended to facilitate inter-application integration as opposed to intra-application integration.  Intra-application integration is aimed at programs in the same application system, usually communicating with each other using middleware that is embedded in their underlying runtime environment, and tends to be optimised for close, real-time, synchronous connections and interactive request/reply or conversation communication models. IEC 61968, by contrast, is intended to support the inter-application integration of a utility enterprise that needs to connect disparate applications that are already built or new (legacy or purchased applications), each supported by dissimilar runtime environments. Therefore, these interface standards are relevant to loosely coupled applications with more heterogeneity in languages, operating systems, protocols and management tools. This series of standards is intended to support applications that need to exchange data every few seconds, minutes, or hours rather than waiting for a nightly batch run. This series of standards, which are intended to be implemented with middleware services that exchange messages among applications, will complement, not replace utility data warehouses, database gateways, and operational stores.

As used in IEC 61968, a Distribution Management System (DMS) consists of various distributed application components for the utility to manage electrical distribution networks.  These capabilities include monitoring and control of equipment for power delivery, management processes to ensure system reliability, voltage management, demand-side management, outage management, work management, automated mapping and facilities management.  Standard interfaces are defined for each class of applications identified in the Interface Reference Model (IRM), which is described in Part 1: Interface Architecture and General Requirements

This part of IEC 61968 contains the clauses listed in the table below.

# Document overview for IEC 61968 – 9

| Clause | Title | Purpose |
| --- | --- | --- |
|  | Scope | The scope and purpose of the document are described. |
|  | Normative References | Documents that contain provisions which, through reference in this text, constitute provisions of this International Standard. |
|  | Reference and Information Models | Description of general approach to metering system, reference model, use cases, interface reference model, meter reading and control functions and components, message type terms and static information model. |
|  | Meter Reading and Control Message Types | Message types related to the exchange of information for documents related to meter reading and control. |
| Annex A | Message Type Verbs | Description of the Verbs that are used for the message types |
| Annex B | CIM Extensions | CIM extensions to support the recommended message structure for meter reading and control |
| Annex C | Recommended procedure for the generation of a ReadingTypeId | Recommended technique for constructing, and offers sample enumerations for the ReadingTypeId textual name and mRID. |
| Annex D | Recommended QualityCode enumerations | Recommends technique for constructing, and offers sample enumerations for reading quality codes |
| Annex E | Recommended EndDeviceEvent Code enumerations | Recommends EndDeviceEvent alarm codes |
| Annex F | Recommended EndDeviceControl code enumerations | Describes recommended technique for leveraging EndDeviceEvent codes to create EndDeviceControl codes. |
| Annex G | Recommended Procedure for Maintaining Relationships Between Objects | To describe the use of the master resource identifier (mRID). |
| Annex H | XML Schemas for message payloads | To provide xsd information for use by developers to create part 9 messages. |
| Annex I | ebIX Mappings | To provide mappings between 61968-9 Meterreadings and ebIX. |
| Annex J | Request Parameters | Describes the qualification of GET requests using Request parameters. |

# System Interfaces For Distribution Management –

# Part 9: Interface Standard for Meter Reading and Control

# Scope

## Scope of full standard

The IEC 61968 standard, taken as a whole, defines interfaces for the major elements of an interface architecture for Distribution Management Systems (DMS). Part 1: Interface Architecture and General Requirements, identifies and establishes requirements for standard interfaces based on an Interface Reference Model (IRM). Parts 3-10 of this standard define interfaces relevant to each of the major business functions described by the Interface Reference Model.

As used in IEC 61968, a DMS consists of various distributed application components for the utility to manage electrical distribution networks. These capabilities include monitoring and control of equipment for power delivery, management processes to ensure system reliability, voltage management, demand-side management, outage management, work management, automated mapping, meter reading, meter control and facilities management. This set of standards is limited to the definition of interfaces and is implementation independent.  It provides for interoperability among different computer systems, platforms, and programming languages.  Methods and technologies used to implement functionality conforming to these interfaces are considered outside of the scope of these standards; only the interface itself is specified in these standards.

## Scope of this part of IEC 61968

This document is Part 9 of the IEC 61968 standard and specifies the information content of a set of message types that can be used to support many of the business functions related to Meter Reading and Control. Typical uses of the message types include meter reading, meter control, meter events, customer data synchronization and customer switching. Although intended primarily for electrical distribution networks, IEC 61968-9 can be used for other metering applications, including non-electrical metered quantities necessary to support gas and water networks.

The purpose of this document is to define a standard for the integration of Metering Systems (MS), which includes traditional manual systems, and (one or two-way) Automated Meter Reading (AMR) Systems, with other systems and business functions within the scope of IEC 61968. The scope of this standard is the exchange of information between a Metering System and other systems within the utility enterprise. The specific details of communication protocols those systems employ are outside the scope of this standard. Instead, this standard will recognize and model the general capabilities that can be potentially provided by advanced and/or legacy meter infrastructures, including two-way communication capabilities such as load control, dynamic pricing, outage detection, distributed energy resource (DER) control signals and on-request read. In this way, this standard will not be impacted by the specification, development and/or deployment of next generation meter infrastructures either through the use of standards or proprietary means.

The capabilities and information provided by a meter reading system are important for a variety of purposes, including (but not limited to) interval data, time-based demand data, time-based energy data (usage and production), outage management, service interruption, service restoration, quality of service monitoring, distribution network analysis, distribution planning, demand reduction, customer billing and work management. This standard also extends the CIM (Common Information Model) to support the exchange of meter data.

# Normative , informative, mandatory, and optional material

## Normative references

The following normative documents contain provisions, which through reference in this text, constitute provisions of this International Standard. For dated references, only the editions cited apply. For undated references, the latest edition of the referenced document (including any amendments) applies. Members of IEC and ISO maintain registers of currently valid International Standards.

IEC 60050-300, International Electrotechnical Vocabulary (IEV) - Electrical and electronic measurements and measuring instruments - Part 311: General terms relating to measurements  - Part 312: General terms relating to electrical measurements - Part 313: Types of electrical measuring instruments - Part 314: Specific terms according to the type of instrument 

IEC 61970-301 Ed 2 Energy Management System Application Program Interfaces – Part 301 Common Information Model Core. November 2003.

IEC 61968-1 System Interfaces for Distribution Management – Interface Architecture and General Requirements

IEC 61968-2 System Interfaces for Distribution Management – Glossary

IEC 62051-1:2004, Electricity metering – Data exchange for meter reading, tariff and load control - Glossary of terms – Part 1: Terms related to data exchange with metering equipment using DLMS/COSEM.

ISO 8601, 3rd Edition, 2004-12-01, Data Elements and Interchange Formats – Information Interchange – Representation of Dates and Times

## Informative material

All UML-based sequence diagrams contained herein are to be considered as informative examples of how a message exchange could occur.

Note: One of the strengths of the CIM is its flexibility. As technology advances, and new needs develop, new messages can be created. These new messages might involve additional systems (not pictured.) These new messages may leverage different options than the ones depicted in the example.

All UML-based communication diagrams and message flow diagrams contained herein are to be considered informative.

All UML-based class diagrams contained herein are to be considered informative. The reader is referred to part 1 to locate the document that contains the normative definitions of the classes used in the CIM.

## Normative material

Message format diagrams contained in the body of this document are to be considered normative, with the normative XML Schemas being supplied in Annex H.

Use cases and sequence diagrams presented in this document are for informative purposes only, and represent usage examples for the normative message definitions.

### Mandatory vs. Optional

The messages described within this standard were derived from use cases which satisfy an underlying business need for a specific information exchange. Each use case provides a given context for the use of the CIM. Message format diagrams describe the elements which are passed. The elements depicted in dashed-line boxes are to be considered optional in a given context. The elements depicted in solid boxes are to be considered mandatory in a given context. If a diagram should depict an entire class as mandatory or optional, the reader should interpret this to mean that the use of the class is either mandatory or optional, but not that every element within the class is now mandatory or optional. The reader must refer to the normative definition of the class to determine this.

# Terms, definitions and abbreviations

## Terms and definitions

### General

For the purposes of this standard, the terms and definitions given in IEC 60050-300, IEC 61968-2, IEC 62051, IEC 62055-31 and the following terms apply.

Where there is a difference between the definitions in this standard and those contained in other referenced IEC standards, then those defined in part 2 shall take precedence over the others listed, and those defined in part 9 shall take precedence over those defined in part 2.

customer program

A classification scheme for the sale of energy to consumers according to a particular tariff. The program may specify the purpose, conditions on the time of use, the service voltage(s), the volumes consumed, and/or other terms as a condition of the sale.

Note: Utilities may promote particular programs to their industrial, commercial, agricultural, and residential customers in an effort to encourage a particular behaviour, or to make them aware of their options

end device

Equipment located at the end of the communication system, usually on the customer premises, which may perform functions such as metrology, connect/disconnect, load control, demand response, or other functions, and may have power relay and/or communications capability. This is represented within the CIM using the EndDeviceAsset class.

load control device

Type of End Device which can receive signals causing it to shed load for the purposes of maintaining network reliability and/or commercial agreements.

meter

Type of End Device which performs metrology and supports the tariffing of the distribution and/or transmission network. This is represented using the CIM MeterAsset class, which is a subclass of EndDeviceAsset.

Note: A meter could be defined as a 61850 device with logical nodes.

meter changeout

The process of replacing an existing meter with a new meter.

Note: The installer will customarily follow a work order which specifies a given location, and usually requires that he or she capture readings from the old and new meters, and record the time and day in which the work was performed.

payment meter

Electricity meter with additional functionality that can be operated and controlled to allow the flow of energy according to agreed payment modes.

prepayment mode

payment mode in which automatic interruption occurs when available credit is exhausted.

## Abbreviations

| AM | Asset Management |
| --- | --- |
| AMR | Automated Meter Reading |
| AMI | Advanced Metering Infrastructure |
| CIM | Common Information Model |
| CIS COSEM DLMS UA | Customer Information System Companion Specification for Energy Metering Device Language Message Specification User Association |
| DMS | Distribution Management System |
| IDR IEC | Interval Data Recorder International Electrotechnical Commission |
| LC | Load Control |
| LMS | Load Management System |
| MAM | Meter Asset Management |
| MDM | Meter Data Management |
| MM | Meter Maintenance |
| MR MS | Meter Reading Metering System |
| NO | Network Operations |
| OMS | Outage Management System |
| POS | Point Of Sale |
| RF | Radio Frequency |
| VEE | Validating, Editing, and Estimating |
| WM | Work Management |

# Reference and Information Models

## General approach to metering systems

The spinning disk in an electromechanical meter generally serves as a pulse initiator to the meter recorder module. In a similar fashion, solid-state meters may also employ a metrology unit that generates pulses which represent a fraction of a kWh, and if more sophisticated, the solid-state meter may have a meter recorder which is able to accumulate many different kinds of information and store it for presentation to the meter communications module using a message and table-driven protocol such as ANSI C12.19 or IEC 62056.

The most common metered data element is kWh, but many electricity meters can also capture kW, kVAr, kVArh, and other similar billing quantities. Some meters can also capture pure engineering quantities such as voltage, current, power factor, etc.

Some AMR systems attempt to add value to low-end meters by adding functionality that the meter may lack. For low-end meters (e.g., energy only) it is common for an AMR meter module to add the capability to perform demand metering, Interval Data Recording (IDR), maintain an energisation count, or even provide estimates of certain engineering quantities such as voltage.

Commercial and Industrial meters often employ current transformers and voltage transformers to meter the actual service. Primary voltages and currents are scaled down using potential transformers (PTs) and current transformers (CTs) so that the meter does not have to be constructed to withstand the high voltages and currents actually delivered to the load. Secondary voltage or current values are those that are often measured directly by the meter. Secondary values are small percentage of the primary values that may actually delivered to or connected to the load. If secondary voltages and currents are measured by the meter, these can be converted back to primary values using the PT and CT ratios, which are just the ratio of primary to secondary values.

The metering system will convey meter data and other value-added data through the metering system network to the destination. Depending on the system, the journey may involve multiple steps through public or private networks, licensed or unlicensed RF spectrums, standardized or proprietary systems, in a one-way or two-way fashion.

Some general operations or services can be defined for a metering system. These general operations will translate to specific actions in the context of a given metering solution.

General operations can be scheduled or called on-demand. Each operation returns an answer with a status. A message encapsulates a General operation.

Examples of Meter General Operations (reading) are:

Reading Phone Calls

Reading Load Curve

Reading Encryption Keys

Reading Equipment Configuration

Reading Contract Parameters

Reading Functional Maintenance Data

Reading Technical Maintenance Data

Metrological Reading

Reading Status Parameters

Reading Quality

Reading Date-time

Meter Reading

Reading Historical Data

Reading programming Data

Examples of Meter General Operations (writing) are:

Writing Client Parameters

Writing Season Parameters

Writing Date-Time Changing Seasons

Writing Encryption Keys

Writing First Time In-service

Writing Calling Parameters

Writing Public Holiday Schedule

Writing Self-read Parameters

Writing Status parameters

Writing Programming parameters (pricing)

Writing Defect Parameters

Writing Minimal Defect Threshold Period

Writing Nominal Voltage Level

Readers of Part 9 interested in standards concerning Meter Reading should refer to IEC 62056, DLMS UA (Device Language Message Specification User Association) and the COSEM model: COmpanion Specification for Energy Metering. COSEM specifies 3 steps:

The meter model and data identification.

The mapping of the model into protocol data units.

The transportation of the bits.

## Reference Model

### General

The following diagrams serve as Reference Models and provide examples of the logical components and data flows related to this International Standard. Section 4.5.2 provides references to terms that are defined by the CIM.

The “meter” is treated as an “end device”. The end device may contain a metrology capability, it may contain a communications capability, it may be a Load Control unit, and it may contain a mixture of many different types of functionality. Figure 1 attempts to describe the concept of essentially a shopping-list of functionality which may be available in the (logical or physical) end device.

# Figure 1 – Example of an end device with functions

The end device itself, while presenting a myriad of functionality, is not the subject of this standard. There are many interactions which ultimately affect the end device but occur as a result of a communication between systems at a much higher level in the control architecture. The interaction between systems is within the scope of this standard, and Figure 2 attempts to describe the exact systems involved, and provide an overview to the stakeholder landscape.

From the perspective of this standard, an end device:

- has a unique identity

- is managed as a physical asset

- may issue events

- may receive control requests

- may collect and report measured values

- may participate in utility business processes

The following diagrams of Figures 2 and 3 describe the flows between the components in the Reference Model. Two diagrams are used in order to reduce the complexity that would be experienced by a single diagram. The numbers in brackets provide linkages to the flow definitions.

# Figure 2 – Part 9 reference model

# Figure 3 -- Part 9 Reference Model with Customer Information and Billing System

The reference architecture reflects five main logical components (potentially realized as systems or subsystems) related to metering:

- Metering System, potentially including Data Collection and Control and reconfiguration functionality

- Meter Data Management

- Meter Maintenance

- Load Management, potentially including Load Control and Load Analysis functionality

- Meter Asset Management

- Meter Administration functions, which may be a part of Meter Data Management.

The Metering System and Meter Maintenance System components may be bound to a specific Meter and associated communication technology or they may support multiple meters (and more generically end devices) types and associated communication technology. The Meter Data Management System component may support and consolidate meter data from more than one Metering System. The Metering System may also support consolidation of various measurement and data collection implementations, providing a consistent interface to the Meter Data Management System component.

### Metering System (MS) - Data Collection

The tasks of the Data Collection sub-component within the Metering System may include:

Readings and status collection. Readings and status may be obtained through either manual or automated means, on a scheduled or on-request basis

Transmission of meter readings and status to a Meter Data Management system

Transmission of power reliability and quality event data to Outage Management, Network Operations, and Capacity Planning Systems

Transmission of communication network health information to those responsible for maintaining the communications network.

It is important to note that Metering Systems are significantly diverse with respect to technologies used, protocols used, capabilities and frequency of data collection. The details of the internals of meters, communication transports and protocols are outside the scope of this International Standard.

A handheld device used by a human meter reader could be regarded as a metering system. In a typical meter reading by human, a reader inputs meter data into a handheld device in a field. The handheld device is not connected to a communication network in a field. At the end of day work, the handheld device is connected to a communication network at reader’s home (not in an office), and meter data is uploaded to a meter data management system. In this case, this communication network should be part of a metering system. Data collection is described in 61968-1 as “MR-RMR.”

### Metering System (MS) - Control and Reconfiguration

The tasks of the Control and Reconfiguration subcomponent within the Metering System are:

- Primary interface in executing meter control commands

- Communicating payment system information

- Act as a communication gateway for load control devices

- Service Connect / Disconnect

- Configuration of tariff units of measure and calendar

- Configuration of power quality measurement

- Configuration of meter event recording

- Relay of Load Control signals

- Configuration of meter identity and security credentials

- Fraud detection

This subcomponent is identified separately within the Metering System in order to recognize the existence of Metering Systems that do not have the ability to send messages to meters. 61968-1 describes this subcomponent as “MR-MOP-Meter Configuration.”

### Load Control

The Metering System Infrastructure may often be used as a communication gateway to load control units (61968-1 describes this as “MR-LDC”). Load Control units are End Devices with Load Control (LC) capability. These are wired to control individual, target devices.  End Devices with LC functionality can take on different forms. Quite often a dedicated LC unit can be located at (or near) the device to be controlled. Another approach is to use meters that have relays which are configured to serve as LC devices. Still another approach is to interface with a customer Energy Management System (which would be another type of end device).

### Load Management System (LMS)

A Load Management System is used to manage and control load by the utility in order to promote system reliability. A Load Management System may perform load forecasting, contingency analysis, and other simulations prior to issuing a load control command. This function largely falls under the domain of IEC 61968-5 (Operational Planning and optimization).

### Outage Management System (OMS)

An Outage Management System (OMS) is used by distribution operators to detect and track outages, and to assist in the process of verification and/or restoration. An OMS typically combines (or has ties to) functionality such as Network Operations (61968-3) fault management (NO-FLT); Operational Planning and optimisation (61968-5) network operation simulation (NO-SIM); Maintenance and Construction (61968-6) maintenance and inspection (MC-MAI), and work scheduling and dispatching (MC-SCHD).

The Metering System can be an important source of information for identifying the existence and extent of outages, and can be used to verify the restoration of outages. The MS might have the ability to publish outage and restoration data to the OMS as it finds it. This type of information typically joins customer call-ins in the OMS to allow it to better predict the location of the outage. However, due to the time-sensitive nature of outage detection, there is also the potential need for a request/reply interface with the MS, where the OMS can ask for specific equipment on the distribution network to be tested by the MS, and an energisation status returned for analysis. The request/reply interface can be used by the OMS to supply critical data needed to make an outage prediction, or by a dispatcher who would like to verify that power has been restored to all of the metered endpoints downstream of a particular switch prior to sending the lineman to the next location.

### Meter Asset Management (MAM) System

Utilities will employ some form of asset management software in an effort to maintain detailed records regarding their physical assets. Asset Management is treated categorically in 61968-4. However, metering has such special requirements, that it is common for a utility to use specialized Meter Asset Management software. The software inventories the asset – providing a record of its physical attributes as well as its location. For sake of discussion, the part 9 document will talk about a MAM system which is closely coupled to the MS and MDM, though some implementations will successfully generalize the asset management application sufficiently so that it can live within a more generic AM system.

### Meter Data Management (MDM) System

From a historical perspective, it was common for a utility to have more than one Automated Meter Reading System. Alternatively, a utility might outsource meter reading services to one or more third-party service providers who operate an AMR system and/or read the meters manually.  The Meter Data Management (MDM) system is used to provide a common repository, and point of management and access of meter data that is collected from disparate Metering Systems. In addition to data aggregation, quite often the MDM will also make an effort to scrutinize the data collected from the various Metering Systems, and provide a Validating, Editing, and Estimating (VEE) capability. (IEC 61968-1 includes these functions under “MR-RMR-Meter data aggregation,” and “MR-MOP-Meter Data Management.”)

### Customer Information System (CIS)

A CIS will typically encompass functionality related to customer care and billing. This is a subject which is external to the 61968 standard (refer to Customer account management (EXT-ACT)). The billing function is driven by readings, typically Demand or Time-of-Use, obtained from the meter. The CIS is also often involved with processes related to billing inquires, meter disconnect and meter reconnect, rate program changes.

### Network Operations (NO)

Network Operations (61968-3) may occasionally need to issue load control and pricing signals to meters. This can be done for both economic and emergency reasons.

### Meter Maintenance (MM)

Meter Maintenance is responsible for functionality related to the configuration and installation of meters. This type of functionality generally falls under Meter Asset Management, or Asset Management in general. Performing meter maintenance may require exchanges with Work Management.

### Planning

The planning function is described in Operational planning and optimisation (61968-5) network operation simulation (OP-SIM).

### Work Management (WM)

A Work Management system is responsible for work that is performed by field resources. This subject is covered in Maintenance and Construction (61968-6) maintenance and inspection (MC-MAI).

With respect to metering, WM includes the installation, maintenance and replacement of meters. This may also involve the process of special reads.

### Point of Sale (POS)

A Point of Sale (POS) system is used for the management of payment meters, where a customer either purchases a token or makes a payment for service. Point of Sale falls under the scope of IEC 61968-10.

### Meter

The meter records the data used for tariffing public networks, and data used for network balancing mechanisms.

Readings captured by the MS are collected by a system such as the MDM before being presented for billing purposes. Billing entities may correct the data, or, in some regions, the energy supplier may perform Validating, Editing, and Estimating (VEE) according to rules established by the appropriate supervising regulatory agency. In any case, those corrections are made available to the user who requests them.

Where this International Standard refers to a Meter, it should be realized that a “Meter” is an end device that has metrology capability, it may or may not have communications capability, it may or may not have connect/disconnect capability, or a host of other capabilities. Given that a meter will have metrology capability, it will in all likelihood meter kWh, but possibly also demand, reactive energy and demand, Time Of Use quantities, Interval Data, Engineering quantities, and more.

### Load control devices

Load control devices are used to control loads at a ServiceDeliveryPoint. The metering system may often have a communication network which can be used for transmitting load control signals to various CommunicationsAsset(s) in order to control the load presented by the EndDeviceAsset(s). Alternatively, the communication network could be used to communicate demand response (price) signals to the CommunicationsAsset(s) in order to affect the load presented by the EndDeviceAsset(s).

## Interface Reference Model

It is not the intention of this standard to define the applications and systems that vendors should produce. It is expected that a concrete (physical) application will provide the functionality of one or more abstract (logical) components as listed in this standard. These abstract components are grouped by the business functions of the Interface Reference Model.

In this standard, the term abstract component is used to refer to that portion of a software system that supports one or more of the interfaces defined in Parts 3 to 10. It does not necessarily mean that compliant software is delivered neither as separate modules nor as a single system.

Part 1 of this standard describes infrastructure services common to all abstract components while Parts 3-10 define the details of the information exchanged for specific types of abstract component.

IEC 61968 defines that:

- An inter-application infrastructure is compliant if it supplies services defined in Part 1 to support at least two applications with interfaces compliant to sections of Parts 3 to 10.

- An application interface is compliant if it supports the interface standards defined in Parts 3 to 10 for the relevant abstract components defined in the Interface Reference Model.

- An application is only required to support interface standards of the applicable components listed under Abstract Components. An application is not required to support interfaces required by other Abstract Components of the same Business Sub-Function or within the same Business Function. While this standard primarily defines information exchanged among components in different business functions, it will occasionally also define information exchanged among components within a single Business Function when a strong market need for this capability has been realised.

## Meter reading and control functions and components

It should be noted that the message types defined in this document: IEC 61968 Part 9: Interface Standard for Meter reading and Control, may be sent or received by any type of component within a Distribution Management System (DMS) system.

The Table 1 shows these functions and typical abstract components that are expected to be producers of information for these message types. Typical consumers of the information include, but are not restricted to, the other components as listed in IEC 61968 Part 1.

Table 1 – Business Functions and Abstract Components

| Business Functions | Business Sub-Functions | Abstract Components |
| --- | --- | --- |
| Meter Reading and Control (MR) | Metering System (MS) | Data collection |
|  |  | End point controls |
|  |  | End point reconfiguration |
|  |  | Disconnect/reconnect |
|  |  | Demand reset |
|  |  | On request read |
|  |  | Point of sale |
|  |  | Outage detection and restoration verification |
|  |  | Power reliability and quality events |
|  |  | Metering system events |
|  | Meter Maintenance and Asset Management | End point install, configure, remove, repair, disconnect, reconnect |
|  |  | End point asset history |
|  |  | End point reconfiguration |
|  |  | Special read |
|  |  | Meter service request |
|  |  | Tariffs |
|  | Meter Data Management (MDM) | Meter data repository |
|  |  | Usage history |
|  |  | Validation, estimation and editing |
|  |  | Customer billing data |
|  | Load Management (LM) | Load analysis |
|  |  | Load control |
|  |  | Demand response |
|  |  | Performance measurements |
|  |  | Risk management |

## Static Information Model

### General

The information model relevant to meter reading and control consists of classes that provide a template for the attributes for each message.

The classes are defined in detail in IEC61968 Part 11 or in IEC 61970 Part 301 “Energy Management System Application Program Interfaces – Common Information Model Core.”

### Classes for meter reading and control

Table 2 lists classes used within message types. Usually all the attributes of these classes are contained within a message type. The descriptions provided describe usage within this part.

Classes described as type "Asset" are defined in the 61968/Assets package of the CIM.

Classes described as type "Customer" are defined in the 61968/Customers package of the CIM.

Classes described as type "Metering" are defined in the 61968/Metering package of the CIM.

Classes descrbed as type “Prepayment” are described in the 61968/PaymentMetering” package of the CIM.

Classes described as type "Profile" are contextual profiles defined for 61968-9 that describe message definitions defined using CIM objects.

# Table 2 – Classes for meter reading and control

| Noun | Type | Description |
| --- | --- | --- |
| AuxiliaryAccount | Prepayment | Variable and dynamic part of AuxiliaryAgreement, generally representing the current state of the account related to the outstanding balance defined in AuxiliaryAgreement. |
| AuxiliaryAgreement | Prepayment | An ad-hoc auxiliary account agreement associated with a customer agreement, not part of the customer's account, but typically subject to formal agreement between customer and supplier (utility). Typically this is used to collect revenue owing by the customer for other services or arrears accrued with the utility for other services. It is typically linked to a prepaid token purchase transaction, thus forcing the customer to make a payment towards settlement of the auxiliary account balance whenever he needs to purchase a prepaid token for electricity. The present status of AuxiliaryAgreement can be defined in the context of the utility's business rules, for example: enabled, disabled, pending, over recovered, under recovered, written off, etc. |
| AuxiliaryAgreementConfig | Priofile | Message profile for AuxiliaryAgreements. |
| Card | Prepayment | Documentation of the tender when it is a type of card (credit, debit, etc). |
| Cashier | Prepayment | The operator of the point of sale for the duration of CashierShift. Cashier is under the exclusive management control of Vendor. |
| CashierShift | Prepayment | The operating shift for a cashier, during which he may transact against the CashierShift, subject to VendorShift being open. |
| Charge | Prepayment | A charge element associated with other entities such as tariff structures, auxiliary agreements or other charge elements. The total charge amount applicable to this instance of Charge is the sum of fixedPortion plus percentagePortion. |
| Cheque | Prepayment | The actual tender when it is a type of cheque. Cheque reference number (as printed on the cheque) is specified in 'name.' |
| ComFunction | Metering | Communication function of communication equipment or a device such as a meter. |
| ComMediaAsset | Assets | Communication media such as fibre optic cable, power-line, telephone, etc. |
| ConsumptionTariffInterval | Prepayment | One of a sequence of intervals defined in terms of consumption quantity of a service such as electricity, water, gas, etc. It is typically used in association with TariffProfile to define the steps or blocks in a step tariff structure, where startValue simultaneously defines the entry value of this step and the closing value of the previous step. Where consumption is &gt;= startValue it falls within this interval and where consumption is &lt; startValue it falls within the previous interval. |
| Customer | Customers | Organisation receiving services from ServiceSupplier. |
| CustomerAccount | Customers | Assignment of a group of products and services purchased by the Customer through a CustomerAgreement, used as a mechanism for customer billing and payment. It contains common information from the various types of CustomerAgreements to create billings (invoices) for a Customer and receive payment. |
| CustomerAccountConfig | Profile | Message profile for CuustomerAccounts. |
| CustomerAgreement | Customers | Agreement between the Customer and the ServiceSupplier to pay for service at a specific ServiceLocation. It records certain billing information about the type of service provided at the ServiceLocation and is used during charge creation to determine the type of service. |
| CustomerAgreementConfig | Profile | Message profile for CustomerAgreements. |
| CustomerMeterDataSet | Profile | The CustomerMeterDataSet includes one or more CustomerAccounts for one or more ServiceLocations for one or more ServiceDeliveryPoints. TheCustomerMeterDataSet may include one or more EndDeviceGroups. |
| DemandResponseProgram | Metering | Demand response program. |
| DeviceFunction | Metering | Function performed by a device such as a meter, communication equipment, controllers, etc. |
| ElectricmeteringFunction | Metering | Functionality performed by an electric meter. |
| EndDeviceAsset | Metering | The EndDeviceAsset is equipment that performs the role of an end device. It may contain functionality such as metrology, communications, load control, connect/disconnect, or other capabilities. It is known as “the meter”, “a smart meter”, an “advanced meter”, ”air conditioner”, “refrigerator”, “pool pump”, etc. that a CommModule and/or MeterAsset may monitor and/or control. The asset may be owned by a consumer, a service provider, utility or other party. |
| EndDeviceAssets | Profile | Message used to convey descriptions of one or more EndDeviceAssets. |
| EndDeviceControl | Metering | Used to issue commands to EndDeviceAssets such as meters. May be addressed by EndDeviceAsset or by EndDeviceGroup. EndDeviceControls may have control types and parameters. |
| EndDeviceControls | Profile | Message used to convey one or more EndDeviceControls |
| EndDeviceEvent | Metering | Used to report events detected by end devices such as meters. Each EndDeviceEvent has an event type and a timestamp. |
| EndDeviceEvents | Profile | Message used to convey one or more EndDeviceEvents. |
| EndDeviceFirmware | Profile | Profile for EndDeviceAsset firmware configuration messages. |
| EndDeviceGroup | Metering | An EndDeviceGroup is used for grouping end devices for a variety of purposes including, but not limited to, load control and other types of demand response. An EndDeviceGroup may belong to another EndDeviceGroup, and an end device may belong to zero or more EndDeviceGroups. In some cases the group ID is maintained within the end device, but in other cases it can be managed by a metering system. |
| IntervalBlock | Metering | Time sequence of Readings of the same ReadingType. Contained IntervalReadings may need conversion through the application of an offset and a scalar defined in associated Pending. |
| IntervalReading | Metering | Data captured at regular intervals of time. Interval data could be captured as incremental data, absolute data, or relative data. The source for the data is usually a tariff quantity or an engineering quantity. Data is typically captured in time-tagged, uniform, fixed-length intervals of 5, 10, 15, 30, or 60 minutes. Note: Interval Data is sometimes also called "Interval Data Readings" (IDR). |
| MerchantAccount | Prepayment | The operating account controlled by MerchantAgreement, against which Vendor may vend tokens or receipt payments. Transactions via VendorShift debit the account and bank deposits via BankStatement credit the account. |
| MerchantAgreement | Prepayment | A formal controlling contractual agreement between Supplier and Merchant, in terms of which Merchant is authorised to vend tokens and receipt payments on behalf of Supplier. Merchant is accountable to Supplier for revenue collected at PointOfSale. |
| MeterAsset | Metering | The MeterAsset class is used to describe meters. A MeterAsset is a type of EndDevice typically used to measure and potentially monitor a customer load. The EndDeviceAsset class definition should be used as the basis for MeterAsset class. |
| MeterAssetConfig | Profile | Message profile for MeterAssets configuration messages. |
| MeterAssetReading | Profile | Profile for manually obtaining MeterReadings for MeterAssets. |
| MeterReading | Metering | A set of values obtained from the meter. Each MeterReading may have multiple ReadingTypes, and each ReadingType may contain multiple values. |
| MeterReadings | Profile | Profile for conveying MeterReadings. |
| MeterReadSchedule | Profile | A MeterReadSchedule message is used to schedule meter readings. |
| MeterServiceRequests | Profile | A meter service request is a type of work that can be used for a variety of meter service related activities. These activities would include meter installation, meter change out, customer disconnect/reconnect, , etc. |
| MeterServiceWork | Metering | Work involving meters. |
| MeterSystemEvents | Profile | Profile for meter system event messages. |
| Pending | Metering | When present, a scalar conversion that is associatied with IntervalBlock and which needs to be applied to every contained IntervalReading value. This conversion results in a new associated ReadingType, reflecting the true dimensions of interval reading values after the conversion. |
| PointOfSale | Prepayment | Logical point where transactions take place with operational interaction between Cashier and the payment system; in certain cases PointOfSale interacts directly with the end customer, in which case Cashier might not be a real person: for example a self-service kiosk or over the internet. |
| ReadingQuality | Metering | Quality of a specific reading value or interval reading value. Note that more than one Quality may be applicable to a given Reading. Typically not unsed unless problems or unusual conditions occur (i.e., quality for each Reading is assumed to be 'Good' unless stated otherwise in associated ReadingQuality). |
| ReadingType | Metering | Type of data conveyed by a specific Reading. |
| Receipt | Prepayment | Record of total receipted payment from customer. |
| ReceiptRecord | Profile | Profile for receipt messages. |
| ReceiptSummary | Prepayment | Record of detail of receipts pertaining to one shift of operation (one record per 'tenderKind'). |
| Register | Metering | Display for quantity that is metered on an end device such as a meter. |
| SDPLocation | Metering | Location of an individual service delivery point. For residential or most businesses, it is typically the location of a meter on the customer's premises. For transmission, it is the point(s) of interconnection on the transmission provider's transmission system where capacity and/or energy transmitted by the transmission provider is made available to the receiving party. The point(s) of delivery is specified in the Service Agreement. |
| SDPLocationConfig | Profile | Profile for SDPLocation configuration messages. |
| ServiceCategory | Customers | Category of service provided to the customer. |
| ServiceCategoryConfig | Profile | Profile for ServiceCategory configuration messages. |
| ServiceDeliveryPoint | Metering | Logical point on the network where the ownership of the service changes hands. It is one of potentially many service points within a ServiceLocation, delivering service in accordance with a CustomerAgreement. Used at the place where a meter may be installed. |
| ServiceDeliveryPointConfig | Profile | Profile for ServiceDeliveryPoint configuration messages. |
| ServiceLocationConfig | Profile | Profile for ServiceLocation configuration messages. |
| ServiceSupplier | Prepayment | Organisation that provides services to Customers. |
| Shift | Prepayment | Generally referring to a period of operation or work performed. Whether shift is open/closed can be derived from attributes 'activiryInterval.start' and 'activityInterval.end'. The grand total for receipts (i.e., cumulative total of all actual receipted amounts during this shift; bankable + non-bankable; excludes rounding error totals) can be derived from Receipt attributes: =sum(Receipt.receiptAmount) ; includes bankable and non-bankable receipts. |
| SupplierConfig | Profile | Profile for supplier configuration messages. |
| Tariff | Prepayment | Document, approved by the responsible regulatory agency, listing the terms and conditions, including a schedule of prices, under which utility services will be provided. It has a unique number within the state or province. For Rate Schedules it is frequently allocated by the affiliated Public Utilities Commission. |
| TariffConfig | Profile | Profile for Tariff configuration messages. |
| TariffProfile | Prepayment | A schedule of charges; structure associated with Tariff that allows the definition of complex tarif structures such as step and time of use when used in conjunction with TimeTariffInterval and Charge. Inherited 'status.value' is defined in the context of the utility's business rules, for example: active, inactive, etc. |
| Tender | Prepayment | Tender is what is "offered" by the customer towards making a payment and is often more than the required payment (hence the need for 'change'). The payment is thus that part of the Tender that goes towards settlement of a particular transaction. Tender is modelled as an aggregation of Cheque and Card. Both these tender types can exist in a single tender bid thus 'accountHolderName' must exist separately in each of Cheque and Card as each could have a different account holder name. |
| TimeTariffinterval | Prepayment | One of a sequence of time intervals defined in terms of real time. It is typically used in association with TariffProfile to define the intervals in a time of use tariff structure, where startDateTime simultaneously determines the starting point of this interval and the ending point of the previous interval. |
| Transaction | Prepayment | The record of details of payment for service or token sale. |
| TransactionRecord | Profile | Profile for Transactions messages. |
| TransactionSummary | Prepayment | The record of detail of payment transactions pertaining to one shift of operation (one record per 'transactionKind'). |
| Transactor | Prepayment | The entity that ultimately executes the transaction and who is in control of the process; typically this is embodied in secure software running on a server that may employ secure hardware encryption devices for secure transaction processing. |
| Vendor | Prepayment | The entity that owns PointOfSale and contracts with Cashier to receipt payments and vend tokens using the payment system. Vendor has a private contract with and is managed by Merchant who is a type of Organisation. Vendor is accountable to Merchant for revenue collected, who is in turn accountable to Supplier. |
| VendorShift | Prepayment | The operating shift for a vendor during which he may transact against the merchant's account. It aggregates transactions and receipts during the shift and periodically debits a merchant account. The totals in VendorShift should always = sum of totals aggregated in all cashier shifts that were open under the particular vendor shift. |

Note: The class definitions provided here are for convenience purposes only. The normative definitions are provided by the CIM.

### Classes related to meter reading and control

Table 3 lists those classes that are associated with Meter Reading and Control classes but only the name of an instance is given within messages defined in this standard. The detailed attributes of these classes are used in message types defined in other parts of IEC61968.

# Table 3 – Classes related to meter reading and control

| Related Class | Reference | Description |
| --- | --- | --- |
| Circuit | Collection Package | Static collection of conducting equipment originating at a main distribution center and supplying one or more secondary distribution centers, one or more branch-circuit distribution centers, or any combination of these two types of equipment. It is the source to the next normally open point. |
| LoadDataSet | IEC61968 Part 7 | Customer, supply point, or area load data. May include Meter records for customers (where regulations allow). |
| Organisation | IEC61968 Part 4 | This class is used to identify companies or divisions within companies. Organisations might have roles as utilities, contractors, suppliers, manufacturers, etc. |
| PowerSystemResource | IEC61970-301 | An entity that describes the logical view of a component part of the utility business. PowerSystemResources are further classified as EquipmentContainers e.g. Substations, ConductingEquipment, ProtectionEquipment etc. Instances of type PowerSystemResource may be related to instances of type Asset. |
| PowerTransformer | IEC61970-301 | An electrical device consisting of two or more coupled windings, with or without a magnetic core, for introducing mutual coupling between electric circuits. Transformers can be used to control voltage and phase shift (MW flow). |
| ServiceLocation | Core2/Location Package | A Customer ServiceLocation has one or more ServiceDeliveryPoint(s). Meters are related to a ServiceDeliveryPoint. The location may be a point or a polygon depending on the specific circumstances For Distribution, the ServiceLocation is typically the location of the utility customer's premise. Because a customer’s premise may have one or more meters, the ServiceDeliveryPoint is used to define the actual conducting equipment that the EndDeviceAsset attaches to at the utility customer’s ServiceLocation. For Transmission, it is the point(s) of interconnection on the transmission provider's transmission system where capacity and/or energy transmitted by the transmission provider is made available to the receiving party. |

Note: The class definitions provided here are for convenience purposes only. The normative definitions are provided by the CIM.

# Meter reading and control message types

## General

The purpose of this section is to describe the message types related to IEC 61968-9. It is important to note that some of these message types may also be used by other parts of IEC 61968. The general approach to the realization of message structures and XML schemas for IEC 61968 messages is described in 61968-1.

Although they may be represented in sequence diagrams for context and completeness, this document does not describe message formats that are defined by other parts of IEC 61968. The key message payload structures defined by this part of IEC 61968 include the following:

- CustomerMeterDataSet

- MeterAsset

- MeterAssetReading

- EndDeviceControls

- EndDeviceEvents

- MeterReadings

- MeterReadSchedule

- MeterServiceRequest

- MeterSystemEvents

- EndDeviceFirmware

The normative XML schemas for messages defined by this part are provided in Annex H, providing more detailed, annotated descriptions of the message structures. Message structures are also diagrammed within this section. The notation convention shows required elements with a solid outline, and option elements with dashed outlines.

It is also important to note that the use cases and sequence diagrams provided in this section are informative in nature, and are intended to provide examples of usage for the normative messages definitions. There is no intent by this standard to standardize specific business processes.

## End device event messages

### General

End device events are viewed as a potential data stream which is not necessarily synchronized to the collection of meter reading for billing purposes. However, it may still be relevant to the billing process. A meter health alarm might be so severe that all readings from the meter have to be considered invalid. The data consumer (e.g. the MDM System) becomes responsible to subscribe to all of the available relevant data, and merge the findings appropriately.

### Applications

#### Outage Detection

When an outage is not due to a SCADA trip, electric utilities typically depend on the calls from the customers to identify the location of the fault. However, the use of a MS can provide another means to identify the location of trouble. It is often possible for a MS to determine that it has lost contact with a meter, in which case this can be reported for potential use by an outage management system. It is important to note that loss of communications with a meter may not be sufficient to identify the existence of an outage, as it is common for some MS infrastructures to occasionally lose contact with meters for brief periods of time.

Some MS systems may be prone to false alarms as a result of the particular technology used to communicate with the meters. Many vendors are working to improve their technology and the accuracy of the data. The MDM, much like the role it sometimes plays in cleaning up metered data for billing applications, in many instances, can also play a role in cleaning up outage data supplied by the MS before it is relayed to the OMS. Such a decision, to route outage data through the MDM, depends on the capability of the MS to supply accurate data, the ability of the MDM to clean up data without introducing excessive delays, and the ability of the OMS to tolerate false alarms and delays. To support outage analysis and filtering of bad data, the MS may supply audit-trail data and quality of measurement data for the outage event, much like it supplies audit-trail data for billing reads. Figure 4 describes a deployment in which the MDM is employed to broker outage information.

Figure 4 -- Outage Detection, request / reply message exchange, Example 1

Outage Management Systems analyze the circuit in terms of network topology. The EndDeviceEvent.category can indicate an outage event as detected by an end device for consideration in the analysis, as well as other information such as trouble tickets.

The use of an MDM to broker outage data is at the discretion of the utility. In some deployments, the outage detection request from the OMS may be issued directly to the MS as in the example of Figure 5.

Figure 5 -- Outage Detection, request / reply message exchange, Example 2

A reply (synchronous or asynchronous) from the MS will likely be in the form of zero or more EndDeviceEvents. The mRID will identify the end devices (e.g. meters) affected by the outage or restoration. Some data consumers that interact with the MS might only know how to deal with meter ID’s. Depending on the deployment, it may be required to limit the scope of exchanged mRID’s to that of meters ID’s and not to that of power system resources in general. EndDeviceEvent.status can indicate “live” or “dead”. EndDeviceEvent.category can be used to indicate that the status applies to a meter or power transformer. The reason for the event can be described (e.g. EndDeviceEvent.reason = “consecutiveFailCounter”) and quantified (e.g. EndDeviceEvent.severity = ”3”).

While the request/reply exchange is useful whenever the OMS needs supplementary information, some MS are able to self-detect outages. A pub/sub exchange is ideal in these situations. Figure 6 shows such an exchange at a deployment where the MDM serves as an information broker. Figure 7 shows a deployment with information going directly from the MS to the OMS.

Figure 6 -- Outage Detection, publish/subscribe exchange, Example 1

Not shown is the “SUBSCRIBE” that occurs typically only once upon system installation, and publication of events occurs repeatedly for the duration of the subscription.

Figure 7 -- Outage Detection, publish/subscribe exchange, Example 2

Some deployments may wish to limit the number of interfaces supported. The MeterReadings message structure also provides the means to convey EndDeviceEvents.

#### Meter Health Events

Some types of meters can sometimes generate meter health events, which can be used to identify issues with meter hardware, configuration or connection that should be resolved. The alarms include such things as diagnostic alarms, tamper alarms, or other unusual conditions. The severity of the alarm might range from a simple notification to “fatal”. Often times, resolution of meter health events require a site visit, so typically they result in the creation of a MeterServiceRequest. These events are communicated using EndDeviceEvent messages.

Figure 8 – Meter Health Event exchange, Example 1

In some deployments, the MDM will be present to broker meter health data for other stakeholders as described in the scenario of Figure 8. Other installations however might not have an MDM or use it in this way. It is possible for the MS to publish data directly to the stakeholders that are equipped to receive it. Such an exchange is depicted in Figure 9.

Figure 9 -- Meter Health Event exchange, Example 2

#### Power Quality Event

Meters may collect information related to power quality, including but not limited to, momentary outage events, sustained outage events, low or high voltage events, and high distortion events. This information could be used for outage analysis, maintenance scheduling or capacity planning. Power quality events are a subtype of EndDeviceEvent.

Power quality events may be brokered (i.e. publications managed) by an MDM (as described in Figure 10), or sent directly to the various stakeholders (as described in Figure 11).

Figure 10 -- Power quality event exchange, Example 1

Figure 11--Power quality event exchange, Example 2

### Message format

Meter event messages are implemented using EndDeviceEvent structures in order to support a wider variety of event sources than just meters. The EndDeviceEvent.category is an enumeration which indicates the type of event, such as Outage Detection, Meter Health, or Power Quality. The timestamp and mRID of the end device are also required. The message format is described in Figure 12.

Figure 12--End device event message format

As noted by Figure 12, only the mRID, timestamp and category elements are required. The category element will allow different event types (e.g. meter health, outage detection, etc.) to be differentiated. Different event types would allow for an EndDeviceEvent message to convey events related (but not limited) to:

- Sustained outage detection

- Momentary outage detection

- Low voltage threshold detection

- High voltage threshold detection

- Distortion

- Meter health

- Tamper detection

- Revenue event

# The detailed XML schema is provided in Annex H.4.

## Synchronization between systems

### General

In most cases, data may freely flow from the data producer to all of the data consumers (in parallel). In some cases however, systems add value to the data when they handle it. In this case subscriptions must be established to route the data in sequence between systems.

### Applications

#### Meter asset management

Most assets are assigned an ID by their system of record. (Alternatively, they may be assigned an mRID by an ID broker.) The mRID serves as a permanent key. When a data producer publishes information regarding changes to an asset, it can be understood that the mRID has not changed, but other information in the publication has. Information on the use of the SUBSCRIBE, CREATED, UPDATED, and DELETED verbs may be found in Annex A.

Subscriptions are typically established one time initially between systems (see Figure 13), using mechanisms provided by the messaging infrastructure as opposed to application-level messages. Publications flow as long as the subscription is maintained (see example in Figure 14).

Figure 13--Example of meter asset management subscriptions

#### End device acceptance into inventory

When an end device is purchased (a meter, a load control unit, whole-house connect/disconnect, etc.) the news of the purchase might propagate to the other systems.In these case, the event may reported using either the CREATED (where the asset is new) or UPDATED (where the asset has been updated) verb. The EndDeviceAsset message is structured so that it can be used to present a bundle of DeviceFunctionality which describes the capability of the device identified by the Asset name. The EndDeviceAsset message can also be used to describe the relationship between components. For example, it can describe the relationship between a meter communication module, and the meter that hosts it.

Figure 14 – Example of meter asset management publications

This information is conveyed by creating a meter asset (a subclass of EndDeviceAsset) and ActivityRecord for the new hardware. Test results from the meter vendor as well as any acceptance testing form the start of the ActivityRecord for the EndDeviceAsset.

#### End device retested

When a meter has been changed out (see the section on meter installation and removal), it is typically tested in the meter shop and recalibrated. The test results are added to the ActivityRecord. News of the recalibration, and the results can be sent from the WMS to the MAM as described in Figure 15.

Figure 15 – Example of WM to MAM exchange – test results

#### End device removed from service

When an end device has reached the end of its useful life, it will be destroyed and the inventory adjusted to show that it is no longer an asset of the utility. This might happen when a meter (perhaps after failing a test) is deemed un-repairable, or when a load control unit is unresponsive and considered lost.

A utility might also sell a quantity of used meters in an effort to standardize around a particular brand or model. This too will remove the product from active inventory. Adjustments to inventory can be communicated using a method similar to that described in Figure 16.

Figure 16– Example of WM to MAM exchange – asset status update

#### Customer data synchronization

When changes are made to Customers, CustomerAccounts, CustomerAgreements, MeterAssets (EndDeviceAssets), ServiceDeliveryPoints or ServiceLocations these changes will need to be published for consumption by systems such as OMS and MS. Often the Customer Billing system will be the master repository for this information.

Initially a newly installed system may wish to immediately subscribe to changes in the data of interest (as shown by example of Figure 17.) The system however will require the history of the data as well, and may utilize “GET” and “REPLY” verbs to fill particular gaps, as shown by the example of Figure 18. Some MS may obtain customer data prepared for it by the MDM, while other MS may receive customer data directly from the CIS.

Figure 17 – Example of reciprocal subscriptions (with MDM present)

Metering Systems are typically configured to read meters by group or category. Some Metering Systems may define particular groups or categories of meters directly in the MS. Other MS may subscribe to a meter group or category definition from an MDM. Either case of meter group definition may result in the creation of associated Measurements in the MS.

Figure 18 – Example of synchronization exchanges

### Message format

Messages are implemented using EndDeviceAssets and CustomerMeterDataSet messages. The message format for EndDeviceAssets is described in Figure 19 and the message format for CustmerMeterDataSet is described in Figure 20.

Figure 19 – End device asset message format

# The detailed XML schema for an EndDeviceAssets message is described in Annex H.10.

Figure 20 – Customer meter data set message format

# The detailed XML schema for a CustomerMeterDataSet is described in Annex H.2.

## Meter reading messages

### General

Whenever a “measurement” is required from an end device, a MeterReading exchange is quite likely the appropriate tool for the job. The end device may have metrology capability, and if so, is most likely called a “meter.” But there are other potential applications for MeterReading. If a data consumer wishes to measure the position of the switch on a connect/disconnect switch, this can be done as a MeterReading exchange. If a data consumer wishes to measure the “energisation” status of the end device, this can be done with a MeterReading exchange or alternatively, with an EndDeviceEvent exchange as described in section 5.2.

### Applications

#### Periodic meter reads

It is necessary to periodically gather meter readings from a MS for billing through the Customer Billing system. The request for meter reading should specify a meter or group of meters, a type of reading to collect, and a frequency and duration of interest. The scheduled frequency may consist of regular or irregular periods.

The MeterReadSchedule request may be initiated to the MS from any of the following:

The CIS (in an effort to collect billing determinants).

A Planning and Scheduling application (in an effort to acquire engineering data about the distribution network).

An OMS (to establish a stream of status information).

A Meter Data Management System (in an effort to broker data for any or all of the above applications).

The MS itself may also self-initiate a MeterReadSchedule.

An example for one such exchange (this one using an MDM) is shown in Figure 21.

Figure 21 – Example use of meter read schedule to create subscription

Figure 22 shows the structure used for the payload of a MeterReadSchedule request message:

Figure 22 – Meter read schedule message format

Some Metering Systems may have the ability to decouple MeterReading collection from MeterReading reporting. For Metering Systems without this capability, readings are reported immediately upon collection. In the MeterReadSchedule request, MeterReadings may be requested using a variety of parameters, including:

Specific meter, using the EndDeviceAsset mRID

Specific meter, using a serialNumber as known to the Metering System

EndDeviceGroups, where a EndDeviceGroup identifies a groupAddress used within the Metering System

As specified using a TimeSchedule

ReadingTypes can be specified to identify the desired reading types

The detailed MeterReadSchedule XML Schema is provided in Annex H.6. Details related to the qualification of request messages are described in Annex J.

Figure 23 shows the message format used to present meter readings from one or more end devices.

Figure 23 – Meter readings message format

The MeterReadings message structure allows for:

- Readings from one or more meters

- Reading values each have an associated reading type, timestamp and value

- Many quality values can be associated with each reading value.

- Readings can be supplied in the form of interval blocks, where readings of a common reading type are grouped together

- Event histories can be returned with meter readings.

Key to the reporting of a value from a meter is the reading type. The readingType class in the CIM is defined to allow capture of the following information as related to the description of a reading type:

- mRID (to uniquely identify a reading type)

- channel number

- default quality

- default value data type

- dynamic configuration

- default forward chronology

- interval length (in seconds)

- measurement type category

- unit of measure

- register digits

The details of this and other classes specific to metering are described in the Metering package of the CIM. A more thorough discussion of reading types is provided in Annex C.

Readings are not limited to metering devices. Any EndDevice may potentially produce a measurement. The asset producing the reading is identified by the meterAsset class. It is expected that all assets have a unique mRID so that meters can be distinguished from remote connect/disconnect switches, and from other devices.

Interval data has unique timestamp requirements. The extended capabilities of ISO 8601 provide the means to specify both a formal interval length (as an 8601 “period” of time), as well as a fixed reference point.

# The following XML provides an XML example payload of a MeterReadings message.

<?xml version="1.0" encoding="UTF-8"?>

<m:MeterReadings xsi:schemaLocation="http://iec.ch/TC57/2009/MeterReadings# MeterReadings.xsd" xmlns:m="http://iec.ch/TC57/2007/MeterReadings#" xmlns:xsi="http://www.w3.org/2001/XMLSchema-instance">

# <m:MeterReading>

<m:CustomerAgreement>

# <m:mRID>35437383</m:mRID>

</m:CustomerAgreement>

<m:EndDeviceEvents>

<m:mRID>47474</m:mRID>

<m:category>6.6.1.47.1</m:category>

<m:createdDateTime>2009-12-17T09:37:53.0Z</m:createdDateTime>

</m:EndDeviceEvents>

<m:IntervalBlocks>

<m:IntervalReadings>

<m:timeStamp>2009-12-17T09:30:47.0Z</m:timeStamp>

<m:value>25.44</m:value>

</m:IntervalReadings>

<m:IntervalReadings>

<m:timeStamp>2009-12-17T09:45:47.0Z</m:timeStamp>

<m:value>37.57</m:value>

</m:IntervalReadings>

<m:IntervalReadings>

<m:timeStamp>2009-12-17T10:00:47.0Z</m:timeStamp>

<m:value>23.41</m:value>

<m:ReadingType ref="2.6.7.1.0.12.0.0.0.3.72"/>

</m:IntervalBlocks>

<m:MeterAsset>

<m:mRID>6468822</m:mRID>

<m:status>

<m:value>OK</m:value>

</m:status>

</m:MeterAsset>

<m:Readings>

<m:timeStamp>2009-12-17T09:30:47.0Z</m:timeStamp>

<m:value>3.14159E0</m:value>

<m:ReadingType ref="0.0.1.0.2.13.2.0.0.0.111"/>

</m:Readings>

<m:Readings>

<m:timeStamp>2009-12-17T09:30:47.0Z</m:timeStamp>

<m:value>83837733</m:value>

<m:ReadingQualities>

<m:quality>2.5.256</m:quality>

</m:ReadingQualities>

<m:ReadingType ref="0.0.1.20.0.12.0.0.0.3.72"/>

</m:Readings>

<m:ServiceDeliveryPoint>

<m:mRID>847647647</m:mRID>

# </m:ServiceDeliveryPoint>

</m:MeterReading>

<m:ReadingType>

<m:mRID>2.6.7.1.0.12.0.0.0.3.72</m:mRID>

<m:aliasName>15-minute Incremental IntervalData Forward Energy  (kWh)</m:aliasName>

<m:unit>kWh</m:unit>

</m:ReadingType>

<m:ReadingType>

<m:mRID>0.0.1.0.2.13.2.0.0.0.111</m:mRID>

<m:aliasName>BulkQuantity LoadInterrupt n0 (Count)</m:aliasName>

<m:unit>count</m:unit>

</m:ReadingType>

<m:ReadingType>

<m:mRID>0.0.1.20.0.12.0.0.0.3.72</m:mRID>

<m:aliasName>BulkQuantity Total Energy (kWh)</m:aliasName>

<m:unit>kWh</m:unit>

</m:ReadingType>

</m:MeterReadings>

#### Manual meter reading

Meter readings can be obtained manually by a meter reader. Data collected may be maintained by the Meter Data Manager. Meters may collect a number of different measurement types. Some types of meters may measure more than one phase, or may collect values for non-electrical measurements, such as water or gas.

A meter reader may input data shown on the panel of meter into a handheld device, which could be regarded as a Metering System. Data input occurs several hundred times per day. A meter reader may present an account of the read to the customer. Note that this account is not an invoice. Billing would be generated normally by the CIS even in the manual reading case. Figure 24 shows such an exchange.

Figure 24 – Example manual meter reading exchange

At the end of the day of work, all data stored in the handheld device is sent to the MDM via a communication network.  The MDM publishes a message to the CIS informing of the creation of MeterAssetReading.

Schedules for walking a manual meter reading route are decided well in advance of performing the work.

#### On-Request meter read

Meter read requests are issued to a MS in order to obtain meter readings on a per request basis.  The MS will send a request to the desired meters.  These can be used for billing inquiries, outage extent verification, and verification of restoration.

Many utilities have a policy of routing all revenue readings through the MDM so that all data will receive the same level of validation. However, not all MDM systems are able to offer validation services for outage data. For those that do, the utility must weigh the value of MDM validation over the time delay it introduces, as well as the ability of the particular OMS solution to reject incongruent data. For this reason, the example diagram shows revenue readings routed through the MDM, but outage data routed around it.

It is important to note that not all Metering Systems support On-Request readings. For those that do, the implementation can also vary significantly.

On-request reads may be initiated to the MS from any of the following:

The CIS (in an effort to collect billing determinants).

A Planning and Scheduling application (in an effort to acquire engineering data about the distribution network).

An OMS (in order to verify if a customer is affected by an outage or has been restored)

A Meter Data Management System (in an effort to broker data for any or all of the above applications).

The MS itself may also directly initiate a MeterRead.

An example for one such exchange (this one using an MDM) is shown in Figure 25.

Figure 25 – Example On-Request meter read exchange

#### Historical meter data access

A distribution network planner may use historical meter reading values as load information for capacity planning purposes. (See the request/reply example in Figure 26).This would permit usage to be aggregated to determine loads for a transformer or feeder.

Figure 26 – HistoricalMeterData exchange

It is important to note the use of request parameters to qualify requests for meter data, filtering the results to obtain data for specific meters within specific timeframes.

#### Billing inquiry

A customer or an internal source may identify a customer billing issue. A meter read request in combination with historical meter reads may be used to resolve the billing issue. (The top of Figure 27 shows an inquiry being satisfied by data which recently arrived, while later on in the day an inquiry is made which requires a fresh reading from the meter.)

In some cases the desired data may be accessible from the MDM. In other cases, it may be necessary to issue a read request remotely through the MS, or manually through a meter service request.

Figure 27– Example billing inquiry message exchange

### Message format

The message format used to convey a meter asset reading is described in Figure 28.

Figure 28 – Meter asset reading message format

A meter asset reading message may contain many MeterServiceWork items. Each MeterServiceWork item identifies a MeterAsset and Customer. There may be many Readings and EndDeviceEvents obtained from the MeterAsset. The detailed XML schema for a meter asset reading is described in Annex H.3.

## End device control messages

### General

There are many types of end device control messages. These are used to send instructions to one or more end devices.

### Applications

#### Load control

Load control (a.k.a. direct load control) requests can often be made to a MS for the purpose of load curtailment. This request would typically be initiated from network operations. Not all MS will have load control capabilities.

It should also be noted that this is different from a disconnect, where a disconnect results in the complete loss of power to a single customer.

A load control will typically result in the shedding of specifically configured loads (e.g. air conditioning, pumps, etc.)

The Load Control function executes load shed commands which are computed by Load Management software (contained in the Network Operations block). The Load Management software is used to compute an appropriate load-shed amount, and could potentially include many factors including the predicted duration of generation shortfalls, historical usage patterns, real-time usage data, and weather.

Figure 29 – Example load control message exchange

The example in Figure 29 shows how load history may be obtained from the MDM in the form of MeterReadings and used to perform load analysis. It also shows load control commands being issued by the LMS to the load control system. Deployments that don’t support an MDM would interact directly with the MS instead.

Load control commands are implemented as a type of EndDeviceControl, where the command can be addressed by EndDeviceGroup (using a group address), by EndDeviceAsset (using mRID) or by CustomerAgreement. This is described below in Figure 30.

#### Load Control device installation

The installation of Load Control units is usually more labour intensive than installing a meter, but the data exchange requirements are simpler. LC units are different from meters in the sense that they don’t require periodic recalibration. Once an LC unit is installed it will probably remain in place for the life of the unit, even if the customer withdraws from the LC program, or if there is a change in tenancy.

Figure 30 – Example message exchange for LC unit installation

Before travelling to the service location, the installer will know the customer account data, the type of load control unit to be installed, and the ratings of the device to be controlled. The installation data can confirm device ratings, and where appropriate, document the port number of the LC unit wired to the device. The results of the installation can be published to all of stakeholders as depicted in Figure 30.

#### Change of customer program

Particular metering solutions are usually chosen to fulfil specific metering needs as a result of customer program enrolment. In many cases, a flexible metering solution can provide coverage for a range of customer programs. When a customer transitions from enrolment in one program to another, it may simply require a change to the meter (or communication module) configuration. In extreme cases it may require a meter change out. In other cases, it may require no change at all. Changes to a configuration will need to be communicated amongst the stakeholders. An example exchange in which the deployment involves an MDM is described in Figure 31. Another example in which the deployment lacks an MDM is described in Figure 32.

Figure 31 – Example message exchange for change of customer program (meter reconfigured)

Changes to the meter configuration may be expressed as a changes to the configuration of an EndDeviceAsset.

Figure 32-- Example message exchange for meter reconfiguration due to change of customer program where there is no MDM

In other cases, a change to the customer program might not be accommodated with a meter reconfiguration. The program change may require a meter changeout. (Please refer to section 5.6 for more information on meter changeouts.) Meter changeouts entail a different workflow than meter reconfigurations. This will be reflected in the message exchange between systems. An example exchange is depicted in Figure 33.

Figure 33 – Example message exchange for change of customer program with meter changed out

See the section 5.6.2.1 on meter installation and removal for additional details on the MeterServiceRequest message.

#### Meter disconnect and reconnect

For a variety of reasons, such as non-payment, it may be necessary to disconnect or reconnect a customer. When disconnected, recorded usage should be zero and out of power complaints should be ignored. When it is not possible to perform a disconnect or reconnect remotely through an MS, a meter service request will typically be issued to perform the disconnect or reconnect manually. Example message exchanges for remote operation are depicted below in Figure 34and Figure 35.

.

Figure 34 – Example message exchange for meter connect / disconnect

Figure 35-- Example message exchange for remote connect/disconnect operation directly between a CIS and MS

#### Real-Time pricing

Real-time pricing signals and/or schedules can be sent to a meter via the MS. There are several ways this can be accomplished, such as:

Price signal issued in real-time identifying a price for a given time interval

Time of use (TOU) schedules published, which cause changes in the accumulation for each TOU  Tier

Energy price schedules published in advance.

Often the EndDeviceGroup can be used to differentiate meters with different contracts or tariffs.

The example in Figure 36 shows a price signal being sent from Network Operations, to the MS. The MS then acts as a network service provider to communicate the price in real time to meters and other equipment.

Figure 36 – Example message exchange for real-time price signal

Price signals are implemented as a subtype of EndDeviceControl, where the price is a message parameter.

### Message format

Figure 37 describes the structure of an EndDeviceControls message.

Figure 37 – End device controls message format

Within this message payload structure, specific meters may be addressed by CustomerAgreement, EndDeviceAsset (e.g. meter) and/or EndDeviceGroup. Aside from at least one address, the only required element is the typeControl. The typeControl element identifies the type of control to be performed. Examples of the different control types that could be used include, but is not limited to:

- Load control signal

- Price signal or schedule

- Remote disconnect

- Remote reconnect

- Demand reset

- Demand reduction signal

# The XML schema for this structure is defined in Annex H.4.

## Meter service requests

### General

Meter service requests are a subclass of Work, where an EndDeviceAsset is involved.

### Applications

#### Meter installation and removal

It may be necessary to install, remove or configure meters as a consequence of the registration of a new customer, removal of a customer or the switch of a customer from one supplier to another. There may also be the need to change out a meter which involves the removal of the old meter, installation of the new meter and configuration of the new meter as needed by the Metering System.

Prior to meter installation, subscriptions have been established between the MS and the MDM to receive updates to customer data (see the section on Data Synchronization for more details). The workflow for a meter change out is shown in Figure 38. This encompasses both the meter installation and meter removal processes.

Figure 38 – Example meter installation and removal message exchange

# Figure 42 shows the message payload structure used for MeterServiceRequest messages.

The InitialReading and FinalReading are of type MeterReading. MeterReading contains “ServiceDeliveryPoint” which is needed (in addition to ServiceLocation) to help identify the location of the new and old meters.

#### Meter replaced due to end device event

EndDeviceEvents (as described section 5.2) can cause an evaluation to occur which results in a request for a meter change out. Meter events may be published from the MS or MDM. Figure 39 describes an example exchange where the MDM has identified a problem, and brought it to the attention of the WMS which decides to change out the meter.

Figure 39 – Example end device event message exchange due to meter changeout

#### Meter changed-out due to CIS alarms or customer complaints

Data analysis by the CIS or customer billing complaints may cause the Customer Service department to request a site-visit to the customer location and possibly a meter change out. Figure 40 describes an example exchange where the MDM has identified a problem, and brought it to the attention of the WMS which decides to change out the meter.

Figure 40 – Example message exchange due to CIS alarms

#### Meter changed-out for recalibration.

The WMS may track when meter recalibration is due, and change-out the meter. Some utilities may view the actual meter change out as a WMS issue as depicted in Figure 41, while others treat it as a MS issue.

Figure 41 – Example message exchange when meter is changed out for recalibration

Changes are published using an EndDeviceAsset message, where the ActivityRecord structure within the message may be leveraged.

### Message format

The following message payload structure describes MeterServiceRequests. It can be used for zero or more MeterServiceWork objects.

Figure 42 – Meter service requests message format

The message may include more than one MeterServiceWork item. Each item may refer to up to two meters to provide the means to replace a meter. Meter readings can be obtained as a part of the work. In the case of a meter replacement, readings for the old meter can be obtained as well as initial readings for the new meter. Location references can be supplied as a part of the customer data or for the meter asset, as appropriate for the work being done. The detailed, annotated XML schema is defined in Annex H.8.

## Metering system events

### General

There are different levels of need within the system for different kinds of messages.

The Metering System (per se) may develop problems within its infrastructure which require a work order to fix. The data requirements for communicating this event are different than the requirements of EndDeviceEvent as described in section 5.2. With an EndDeviceEvent, a simple error code can be used to report a problem. This mechanism works when the recipient is able to look-up and interpret the meaning of the code. However, when a more detailed description of the problem is required, a more elaborate schema must be used. In some cases, the recipient is a human and requires a human-readable description of the problem, and the particular piece of equipment involved. When identifying the asset, it will probably be necessary to use vendor-specific terminology to describe the hardware.

### Applications

#### Meter system health

Metering System infrastructure issues, such as communication outages, may require EventMessaging to systems such as the LMS, MDM, and OMS; and WorkOrder messaging to Communication Network Operations systems.

Figure 43 – Example MeterSystemHealth message exchange

An example message exchange in which the EndDeviceEvent is communicated to various stakeholders is depicted above in Figure 43.

This type of message would carry updates to the CommEquipmentAsset, which in turn can carry the name and serial number of the affected equipment, the type of CommEquipment, the event code, as well as ActivityRecord status, statusReason, remarks, and a timestamp.

#### Firmware upgrade

For an automated Metering System capable of two-way communication, it may be possible to upgrade the firmware of MS infrastructure in the field, or in some systems the Communication Assets in the End Devices. Changes to the metering system that materially affect its operation must be communicated to all of the relevant stakeholders. An example of such a publication is depicted in Figure 44.

Figure 44 – Example firmware upgrade message exchange

The firmware upgrade may cause the EndDeviceAsset or CommEquipmentAsset to change in a number of ways, including device functional characteristics, firmware version and revision number, or configuration (expressed as a programId).

### Message formats

#### MeterSystemEvent

Figure 45 describes the structure of a meter system event message.

Figure 45 – Example meter system event message format

The MeterSystemEvent schema supports the reporting of activity within any type of end device (including meters), as well as within the MS communication infrastructure. As described above, the MeterSystemEvent can be used to describe an event in the end device itself, or in the MS communication infrastructure. The detailed XML Schema is described in Annex H.9.

#### End device firmware

The structure of an end device firmware message is described by Figure 46.

Figure 46 – End device firmware message format

The EndDeviceFirmware message structure supports the naming of the affected device function, as well as additional parameter details that may be necessary in the report. It should be noted that a DeviceFunction can be used to describe software components as well as firmware or hardware. This structure, together with the ActivityRecord can effectively describe the nature of the event, when the event occurred, and what has happened. The detailed XML Schema is provided in Annex H.11.

## Customer switching

### General

A customer in an open retail market can switch between energy suppliers. This may require reconfiguration and/or reinstallation of the meter. The reconfiguration or meter replacement may be a consequence of a customer changing energy programs at the time of the change of energy supplier. This process would likely involve an on request read as needed for final billing purposes. An example message exchange is provided below in Figure 47.

Figure 47 – Example customer switching message exchange

### Message format

The structure of a MeterServiceRequest was described by Figure 42. The structure of a MeterReading message was described by Figure 23.

## Payment metering service messages

### General

Payment metering services typically involve prepayment meters installed at customers’ premises and token vending systems situated at convenient locations to serve the needs of customers. For the purpose of this standard, vending systems are regarded as being part of the metering system. Such vending systems typically require information about the meter, customer, service location, service delivery point, tariff, customer account, customer agreement and the supplier of the service that receives the revenue collected by the vending systems.

The information required by the vending systems usually originates in the CIS and Billing system and is then transferred to the vending systems by means of the messages provided in Clause 5.9.2.

Transaction and receipt information on the other hand originate in the vending systems when the customer makes a payment on an account or purchases a prepaid token at a point of sale. This information periodically needs to be transferred to the CIS and Billing system for further processing, for which purpose the messages in Clause 5.9.3.are provided.

### MS information configuration

#### General

In order to operate as a payment metering system, MS typically requires to be configured with information about the supplier of the service, the service being provided, the customers of the supplier, customer agreements, customer accounts, debt to be collected against customer agreements, tariffs, service delivery points, service delivery point locations, service locations and meters deployed in the metering system.

This information typically originates in the CIS and billing system, from where it periodically gets transferred to MS for configuration and update. The messages defined in section 5.9.2 make provision for transferring this information from the CIS and billing system.

#### Suppliers

Information about the supplier (retailer or utility for example) of the service may be configured into MS by means of SupplierConfig message payload.

In the case where a specified range (by date or mRID) of the message payload is to be specified in a particular contextual implementation, this may be realised by making use of the optional elements in the message header (see Figure B.2).

An example of a message exchange is given in Figure 48 and the message format is given in Figure 49.

Figure 48 -- Message exchange for transferring supplier information

Figure 49 -- Supplier configuration message format

The detailed specification for each class and attribute can be found in IEC 61968 - 11 and IEC 61970 - 301. The detailed, annotated XML schema is defined in Annex H.12.

#### Customers

Information about customers of the supplier of the service may be configured into MS by means of CustomerConfig message payload.

In the case where a specified range (by date or mRID) of the message payload is to be specified in a particular contextual implementation, this may be realised by making use of the optional elements in the message header (see Figure B.2).

An example of a message exchange is given in Figure 50 and the message format is given in Figure 51.

Figure 50 – Message exchange for transferring customer information

Figure 51 -- Customer configuration message

The detailed specification for each class and attribute can be found in IEC 61968-11 and IEC 61970-301. The detailed, annotated XML schema is defined in Annex H.13.

#### Customer agreements

Information about customer agreements may be configured into MS by means of CustomerAgreementConfig message payload.

In the case where a specified range (by date or mRID) of the message payload is to be specified in a particular contextual implementation, this may be realised by making use of the optional elements in the message header (see Figure B.2).

An example of a message exchange is given in Figure 52 and the message format is given in Figure 53.

Figure 52 – Message exchange for transferring customer agreement information

Figure 53 -- Customer agreement configuration message

The detailed specification for each class and attribute can be found in IEC 61968-11 and IEC 61970-301. The detailed, annotated XML schema is defined in Annex H.17.

#### Customer accounts

Information about customer accounts may be configured into MS by means of CustomerAccountConfig message payload.

In the case where a specified range (by date or mRID) of the message payload is to be specified in a particular contextual implementation, this may be realised by making use of the optional elements in the message header (see Figure B.2).

An example of a message exchange is given in Figure 54 and the message format is given in Figure 55.

Figure 54 – Message exchange for transferring customer account information

Figure 55 – Customer account configuration message

The detailed specification for each class and attribute can be found in IEC 61968-11 and IEC 61970-301. The detailed, annotated XML schema is defined in Annex H.16.

#### Auxiliary agreements

Information about customer debt for collection may be configured into MS by means of AuxilaryAgreementConfig message payload.

In the case where a specified range (by date or mRID) of the message payload is to be specified in a particular contextual implementation, this may be realised by making use of the optional elements in the message header (see Figure B.2).

An example of a message exchange is given in Figure 56 and the message format is given in Figure 57.

Figure 56 – Message exchange for transferring auxiliary agreement information

Figure 57 -- Auxiliary agreement configuration message format

The detailed specification for each class and attribute can be found in IEC 61968-11 and IEC 61970-301. The detailed, annotated XML schema is defined in Annex H.18.

#### Pricing structure and tariffs

Information about pricing structures may be configured into MS by means of PricingStructureConfig message payload.

In the case where a specified range (by date or mRID) of the message payload is to be specified in a particular contextual implementation, this may be realised by making use of the optional elements in the message header (see Figure B.2).

An example of a message exchange is given in Figure 58 and the message format is given in Figure 59.

Figure 58 – Message exchange for transferring pricing structures

Figure 59 – PricingStructureConfig message format

The detailed specification for each class and attribute can be found in IEC 61968-11 and IEC 61970-301. The detailed, annotated XML schema is defined in Annex H.15.

#### Service categories

Information about the categories of service (electricity, water, gas for example) may be configured into MS by means of ServiceCategoryConfig message payload.

In the case where a specified range (by date or mRID) of the message payload is to be specified in a particular contextual implementation, this may be realised by making use of the optional elements in the message header (see Figure B.2).

An example of a message exchange is given in Figure 60 and the message format is given in Figure 61.

Figure 60 – Message exchange for transferring service category information

Figure 61 – ServiceCategoryConfig message format

The detailed specification for each class and attribute can be found in IEC 61968-11 and IEC 61970-301. The detailed, annotated XML schema is defined in Annex H.14.

#### Service delivery points

Information about the service delivery points may be configured into MS by means of ServiceDeliveryPointConfig message payload.

In the case where a specified range (by date or mRID) of the message payload is to be specified in a particular contextual implementation, this may be realised by making use of the optional elements in the message header (see Figure B.2).

An example of a message exchange is given in Figure 62 and the message format is given in Figure 63.

Figure 62 – Message exchange for transferring service delivery point information

Figure 63 – ServiceDeliveryPointConfig message format

The detailed specification for each class and attribute can be found in IEC 61968-11 and IEC 61970-301. The detailed, annotated XML schema is defined in Annex H.20.

#### Meters

Information about the meters in service may be configured into MS by means of MeterAssetConfig message payload.

In the case where a specified range (by date or mRID) of the message payload is to be specified in a particular contextual implementation, this may be realised by making use of the optional elements in the message header (see  Figure B.2).

An example of a message exchange is given in Figure 64 and the message format is given in Figure 65.

Figure 64 – Message exchange for transferring meter information

Figure 65 – Meter asset configuration message

The detailed specification for each class and attribute can be found in IEC 61968-11 and IEC 61970-301. The detailed, annotated XML schema is defined in Annex H.19.

#### Service delivery point locations

Information about the service delivery point locations may be configured into MS by means of SDPLocationConfig message payload.

In the case where a specified range (by date or mRID) of the message payload is to be specified in a particular contextual implementation, this may be realised by making use of the optional elements in the message header (see Figure B.2).

An example of a message exchange is given in Figure 66 and the message format is given in Figure 67.

Figure 66 -- Message exchange for transferring service delivery point location information

Figure 67 – SDPLocationConfig message format

The detailed specification for each class and attribute can be found in IEC 61968-11 and IEC 61970-301. The detailed, annotated XML schema is defined in Annex H.22.

#### Service locations

Information about the service locations may be configured into MS by means of ServiceLocationConfig message payload.

In the case where a specified range (by date or mRID) of the message payload is to be specified in a particular contextual implementation, this may be realised by making use of the optional elements in the message header (see Figure B.2).

An example of a message exchange is given in Figure 68 and the message format is given in Figure 69.

Figure 68 – Message exchange for transferring service location information

Figure 69 – ServiceLocationConfig message format

The detailed specification for each class and attribute can be found in IEC 61968-11 and IEC 61970-301. The detailed, annotated XML schema is defined in Annex H.21.

### MS financial information

#### General

When a customer purchases a prepaid token at a point of sale or makes a payment on a billed account, financial information is originated in MS relating to this transaction. Typically this information is periodically transferred to the CIS and billing system for further processing.

The messages defined in Clause 5.9.3 make provision for transferring this information to the CIS and billing system.

#### Receipts

When MS receives a payment, a receipt is generated and the relevant information about the payment is typically recorded as a receipt record. This information may be accessed by means of ReceiptRecord message payload.

In the case where a specified range (by date or mRID) of the message payload is to be specified in a particular contextual implementation, this may be realised by making use of the optional elements in the message header (see Figure B.2).

An example of a message exchange is given in Figure 70 and the message format is given in Figure 71.

Figure 70 -- Message exchange for transferring receipt information

Figure 71 – ReceiptRecord message format

The detailed specification for each class and attribute can be found in IEC 61968-11 and IEC 61970-301. The detailed, annotated XML schema is defined in Annex H.23.

#### Transactions

Information about the sale of a prepaid token or the receipt of an account payment is typically also recorded by MS in the form a financial transaction record, capturing the relevant details relating to the particular transaction. This information may be accessed by means of TransactionRecord message payload.

In the case where a specified range (by date or mRID) of the message payload is to be specified in a particular contextual implementation, this may be realised by making use of the optional elements in the message header (see Figure B.2).

An example of a message exchange is given in Figure 72 and the message format is given in Figure 73.

Figure 72 – Message exchange for transferring transaction information

Figure 73 – TransactionRecord message format

The detailed specification for each class and attribute can be found in IEC 61968-11 and IEC 61970–301. The detailed, annotated XML schema is defined in Annex H.24.

(Informative)

Description of message type verbs

Table A.1 – Commonly used Verbs

| Proposed Verbs | Meaning | Message Body |
| --- | --- | --- |
| CREATE | The CREATE verb is used to submit a request to the master system to create a new document. The master system may in turn publish the new document using the verb CREATED. The master system may also use the verb REPLY to response to the CREATE request, indicating whether the request has been processed successfully or not. | Header, Payload |
| UPDATE | The UPDATE verb is used to submit a request to the master system to make a change in the document based on the information in the message. The master system may in turn publish the changed document using the verb UPDATED to notify that the document has been changed since last published. The master system will use the verb REPLY to response to the UPDATE request, indicating whether the request has been processed successfully or not. | Header, Payload |
| Change | Synonym for UPDATE | Header, Payload |
| Cancel | The CANCEL verb is used to submit a request to the master system to cancel the document. The master system may in turn publish the cancelled message using the verb CANCELED to notify that the document has been cancelled since last published. The master system will use the verb REPLY to respond to the CANCEL request, indicating whether the request has been processed successfully or not. The CANCEL verb is used when the business content of the document is no longer valid due to error(s). | Header, Request mRID(s) for objects specified using Reqest.ID |
| Close | The CLOSE verb is used to submit a request to the master system to close the document. The master system may in turn publish the closed message using the verb CLOSED to notify that the document has been closed since last published. The master system will use the verb REPLY to response to the CLOSE request, indicating whether the request has been processed successfully or not. The CLOSE verb is used when the business document reaches the end of its life cycle due to successful completion of a business process. | Header, Request mRID(s) for objects specified using Reqest.ID |
| DELETE | The DELETE verb is used to submit a request to the master system to delete the document. The master system may in turn publish the closed message using the verb DELETED to notify that the document has been deleted since last published. The master system may also use the verb REPLY to response to the DELETE request, indicating whether the request has been processed successfully or not. The DELETE verb is used when the business document should no longer be kept in the integrated systems either due to error(s) or due to archiving needs. | Header, Request mRID(s) for objects specified using Reqest.ID |
| Get | The GET verb is used to submit a query request to the master system to get the current data for a given document reference code or a set of documents. The master system will use the verb REPLY to respond to the GET request. | Header, Request Variety of options to qualify request using request elements |
| Created | The CREATED verb is used to publish the creation of a document as a result of either an external request or an internal action within the master system of that document. This is the first time that data for this document reference code has been published as the result of internal or external request; in which case, it would use the same document reference as the CREATE message. This message type is usually subscribed by interested systems and could be used for mass updates. There is no need to reply to this message type. | Header, Payload |
| UPDATED | The UPDATED verb is used to publish events related to the change of a document as a result of either an external request or an internal action within the master system of that document. This could be a generic change in the content of the document or a specific status change such as “approved”, “issued” etc. This message type is usually subscribed by interested systems and could be used for mass updates. There is no need to reply to this message type. | Header, Payload |
| Changed | Treat as a synonym with UPDATED | Header, Payload |
| Closed | The CLOSED verb is used to publish events related to the normal closure of a document as a result of either an external request or an internal action within the master system of that document. This message type is usually subscribed by interested systems and could be used for mass updates. There is no need to reply to this message type. | Header, Payload |
| Canceled | The CANCELED verb is used to publish the cancellation of a document as a result of either an external request or an internal action within the master system of that document. This message type is usually subscribed by interested systems and could be used for mass updates. There is no need to reply to this message type. | Header, Payload |
| DELETED | The DELETED verb is used to publish the deletion of a document as a result of either an external request or an internal action within the master system of that document. This message type is usually subscribed by interested systems and could be used for mass updates. There is no need to reply to this message type. | Header, Payload |
| Show | Synonym to REPLY, may be deprecated. | Header, Reply, Payload |
| Reply | The REPLY verb is used to return the processing result of a request for a CREATE, UPDATE, DELETE, CANCEL or CLOSE. | Header, Reply, Payload (optional) Where a payload would be supplied in a response to a GET request (unless there were errors), it would not be returned for UPDATE, CANCEL, CLOSE or DELETE requests. |
| SUBSCRIBE | The SUBSCRIBE verb is indicate a subscription for a type of information identified by the noun. This is realized within the integration infrastructure (e.g. JMS). | Not implemement as an application-level message |
| UNSUBSCRIBE | The UNSUBSCRIBE verb is used to indicate the termination of a subscription for a type of information identified by the noun. This is realized within the integration infrastructure (e.g. JMS). | Not implemement as an application-level message |

It is important to note that the verbs are listed in the document are for convenience purposes and also to reflect changes that may be reflected in future versions of IEC 61968-1.

(Informative)

Recommended message structure

The purpose of this section is to describe a recommended message structure. The message structure (see Figure B.1) has several packages for:

Header for message control information

Payload for conveying message data

Request for request parameters

Reply for reply codes and errors

The message payloads would be conveyed using the described message structure, where the message header would identify specific nouns and verbs.

# Figure B.1 – Recommended Message message-format

The structure of the header itself is described by Figure B.2:

# Figure B.2 – Recommended.Header message format

The message payload could be strongly typed or loosely coupled using an XML::any. The type of the payload is determined by the noun in the message header. Not all message require payloads, as in the cases of get, close or cancel messages, as examples

The request package of the message would provide arguments for requests. Figure B.3 contains the recommended structure of the request package:

# Figure B.3 – Recommended.RequestType message format

The reply package is used for returning error codes and specific errors. The recommended message format for the reply is depicted in Figure B.4:

# Figure B.4 – Recommended.ReplyType message format

The suggested ReplyCodes can be categorized into families as described in table B.1:

# Table B.1 – ReplyCode Categories

| Category | Error |
| --- | --- |
| 1 | Missing element |
| 2 | Bad value |
| 3 | Too many values |
| 4 | Request timed out |
| 5 | Application Error |

These categories can serve as the first three digits of a numbering scheme to form codes such as those described in table B.2. Should additional error codes be developed over time, they can be inserted as the next value(s) within the appropriate category.

# Table B.2 – Refresh Rate Enumerations

| ReplyCode | Description |
| --- | --- |
| 0.0 | No Errors |
| 1.1 | Noun element(s) not found in CIM Payload |
| 1.2 | Revision element(s) not found in CIM Payload |
| 1.3 | Verb element(s) not found in CIM Payload |
| 2.1 | Invalid DSI Meter Number(s) |
| 2.2 | Invalid Feeder Name |
| 2.3 | Invalid Feeder Number(s) and Substation Name combination. |
| 2.4 | Invalid Meter Number(s). |
| 2.5 | Invalid Noun value |
| 2.6 | Invalid ReadingTypeID |
| 2.7 | Invalid Substation Name |
| 2.8 | Invalid Switch Name(s) and Substation Name combination. |
| 2.9 | Invalid Verb or Revision number |
| 2.10 | Unable to process the request, ReadingTypeID not supported by the system. |
| 2.11 | Payload mismatch |
| 3.1 | Too many meters in request. |
| 3.2 | Too many pending XML requests. |
| 3.3 | Too many ReadingTypeID’s in request |
| 4.1 | Request timed out. |
| 5.1 | Unable to perform your request due to high system activity level. |
| 5.2 | Unable to process the request. Transaction not attempted. |
| 5.3 | Unable to process the request. Transaction attempted and failed. |

The following XML Schema describes the recommended message structures. This structure can be used by a variety of transport mechanisms including web services and JMS.

# <?xml version="1.0" encoding="utf-8"?>

<!-- edited with XMLSpy v2007 sp1 (http://www.altova.com) by Scott Neumann (UISOL) -->

# <!-- Common Message Specification for ESB Integration via IEC 61968 -->

<xs:schema xmlns="http://www.iec.ch/TC57/2008/schema/message" xmlns:xs="http://www.w3.org/2001/XMLSchema" xmlns:wsse="http://www.docs.oasis-open.org/wss/2004/01/oasis-200401-wss-wssecurity-secext-1.0.xsd" xmlns:wsu="http://www.docs.oasis-open.org/wss/2004/01/oasis-200401-wss-wssecurity-utility-1.0.xsd" targetNamespace="http://www.iec.ch/TC57/2008/schema/message" elementFormDefault="qualified" attributeFormDefault="unqualified" version="1.0.0">

<xs:import namespace="http://www.docs.oasis-open.org/wss/2004/01/oasis-200401-wss-wssecurity-secext-1.0.xsd" schemaLocation="WSS200401wssecurity-secext-10.xsd"/>

<xs:import namespace="http://www.docs.oasis-open.org/wss/2004/01/oasis-200401-wss-wssecurity-utility-1.0.xsd" schemaLocation="WSS200401wssecurity-utility-10.xsd"/>

# <xs:complexType name="RequestType">

<xs:sequence>

# <xs:element name="StartTime" type="xs:string" minOccurs="0">

</xs:element>

# <xs:element name="EndTime" type="xs:string" minOccurs="0">

</xs:element>

<xs:element name="Option" type="xs:string" minOccurs="0">

</xs:element>

<xs:element name="ID" type="xs:string" minOccurs="0" maxOccurs="unbounded">

</xs:element>

<xs:any namespace="##other" processContents="lax" minOccurs="0" maxOccurs="unbounded"/>

# </xs:sequence>

</xs:complexType>

<xs:complexType name="ReplyType">

<xs:sequence>

<xs:element name="ReplyCode" type="xs:string">

</xs:element>

<xs:element name="Error" type="xs:string" minOccurs="0" maxOccurs="unbounded">

</xs:element>

<xs:element name="ID" type="xs:string" minOccurs="0" maxOccurs="unbounded">

</xs:element>

<xs:any namespace="##other" processContents="lax" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="PayloadType">

<xs:sequence>

<xs:choice>

<xs:any namespace="##other" processContents="skip" minOccurs="0" maxOccurs="unbounded">

</xs:any>

<xs:element name="Compressed" type="xs:string" minOccurs="0">

</xs:element>

</xs:choice>

<xs:element name="format" type="xs:string" minOccurs="0">

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:complexType name="ReplayDetectionType">

<xs:sequence>

<xs:element name="Nonce" type="wsse:EncodedString"/>

<xs:element name="Created" type="wsu:AttributedDateTime"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="UserType">

<xs:sequence>

<xs:element name="UserID" type="xs:string">

</xs:element>

<xs:element name="Organization" type="xs:string">

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:complexType name="HeaderType">

<xs:sequence>

<xs:element name="Verb" type="xs:string">

</xs:element>

<xs:element name="Noun" type="xs:string">

</xs:element>

<xs:element name="Revision" type="xs:string" minOccurs="0">

</xs:element>

<xs:element name="ReplayDetection" type="ReplayDetectionType" minOccurs="0"/>

<xs:element name="Context" minOccurs="0">

<xs:simpleType>

<xs:restriction base="xs:string">

<xs:enumeration value="PRODUCTION"/>

<xs:enumeration value="TESTING"/>

<xs:enumeration value="DEVELOPMENT"/>

<xs:enumeration value="STUDY"/>

<xs:enumeration value="TRAINING"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="Timestamp" type="xs:dateTime" minOccurs="0">

</xs:element>

<xs:element name="Source" type="xs:string" minOccurs="0">

</xs:element>

<xs:element name="AsyncReplyFlag" type="xs:boolean" minOccurs="0">

</xs:element>

<xs:element name="ReplyAddress" type="xs:string" minOccurs="0">

</xs:element>

<xs:element name="AckRequired" type="xs:boolean" minOccurs="0">

</xs:element>

<xs:element name="User" type="UserType" minOccurs="0">

</xs:element>

<xs:element name="MessageID" type="xs:string" minOccurs="0">

</xs:element>

<xs:element name="CorrelationID" type="xs:string" minOccurs="0">

</xs:element>

<xs:element name="Comment" type="xs:string" minOccurs="0">

</xs:element>

<xs:element name="Property" type="MessageProperty" minOccurs="0" maxOccurs="unbounded">

</xs:element>

<xs:any namespace="##other" processContents="lax" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:element name="Message" type="MessageType">

</xs:element>

<xs:complexType name="MessageProperty">

<xs:sequence>

<xs:element name="Name" type="xs:string"/>

<xs:element name="Value" type="xs:string" minOccurs="0"/>

</xs:sequence>

</xs:complexType>

<xs:element name="RequestMessage" type="RequestMessageType">

</xs:element>

<xs:element name="ResponseMessage" type="ResponseMessageType">

</xs:element>

<xs:element name="FaultMessage" type="FaultMessageType">

</xs:element>

<xs:element name="EventMessage" type="EventMessageType">

</xs:element>

<xs:complexType name="MessageType">

<xs:sequence>

<xs:element name="Header" type="HeaderType"/>

<xs:element name="Request" type="RequestType" minOccurs="0"/>

<xs:element name="Reply" type="ReplyType" minOccurs="0"/>

<xs:element name="Payload" type="PayloadType" minOccurs="0"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="RequestMessageType">

<xs:sequence>

<xs:element name="Header" type="HeaderType"/>

<xs:element name="Request" type="RequestType" minOccurs="0"/>

<xs:element name="Payload" type="PayloadType" minOccurs="0"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="ResponseMessageType">

<xs:sequence>

<xs:element name="Header" type="HeaderType"/>

<xs:element name="Reply" type="ReplyType"/>

<xs:element name="Payload" type="PayloadType" minOccurs="0"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="FaultMessageType">

<xs:sequence>

<xs:element name="Reply" type="ReplyType"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="EventMessageType">

<xs:sequence>

<xs:element name="Header" type="HeaderType"/>

<xs:element name="Request" type="RequestType" minOccurs="0"/>

<xs:element name="Payload" type="PayloadType" minOccurs="0"/>

</xs:sequence>

</xs:complexType>

</xs:schema>

(Informative)

Recommended procedure for the generation of a ReadingType

General

Metering Systems collect readings from meters, manage configurations, operate remote devices, and more as new systems develop and capabilities continue to grow. AMR/AMI vendors often times must interface with a variety of meter vendors, a variety of MDM systems and/or a variety of Customer Information Systems. Different vendors tend to use different terminology. In an effort to rise above the specific vendor names, it is common for a utility or vendor to give names to the data elements that they use. This annex describes a procedure that may be used to create data element names, and suggests that data element names may be used as the ReadingType.name. Then, having identified the attributes of a given data element, this annex also recommends a technique to populate the ReadingType.mRID attributes.

Understanding the important attributes of a data element name

General

Data elements can be described in terms of 11 key attributes.

Attribute #1, Time Attribute Enumerations

Attribute #1 supplies an “adjective” to describe aspects of a “time attribute” with regard to the measurement. Enumerated values include the values described in Table C.1.

The user should note that for reading types which involve a period of time (such as Attribute#3=IntervalData), the specific period of time (e.g. “hourly”) is represented in the timestamp field per ISO 8601. For example, “[P1H]” represents a period of 1 hour, “[P15M]” represents a period of 15 minutes. With the interval period broken out in a separate field, data consumers as well as data producers will need to be mindful to study the timestamp field for period information.

NOTE 1	ISO 8601 supports the ability to use the timestamp to identify the start or end of the interval by careful placement of the timestamp field relative to the period field.

NOTE 2	ISO 8601 also supports the ability to identify the number of recurring periodic intervals with the optional “R” prefix.

Attribute #1 is used to describe time attributes (of the measurement) which cannot be expressed in the extended ISO 8601 timestamp field. It can also be used to identify certain releative relational properties.

# Table C.1 – Time Attribute Enumerations

| Index | Enumeration | Comments |
| --- | --- | --- |
| 0 |  | Not Applicable, or the bulk quantity of a commodity (e.g. the dial reading on an electromechanical watt-hour meter) |
| 1 | RESERVED | Reserved for “10-minute” |
| 2 | RESERVED | Reserved for “15-minute” |
| 3 | RESERVED | Reserved for “1-minute” |
| 4 | RESERVED | Reserved for “24-hour” |
| 5 | RESERVED | Reserved for “30-minute” |
| 6 | RESERVED | Reserved for “5-minute” |
| 7 | RESERVED | Reserved for “60-minute” |
| 8 | Billing-Shifted | Billing period shifted (whatever the billing period is) |
| 9 | Block | A block of data |
| 10 | RESERVED | Reserved for “2-minute” |
| 11 | Daily-Shifted | Daily Self-Read |
| 12 | Instantaneous | Typically measured over tens of milliseconds |
| 13 | Monthly-Shifted | Monthly Self-Read |
| 14 | RESERVED | Reserved for “3-minute” |
| 15 | Present | Within the present monthly cycle |
| 16 | Previous | Within the previous monthly cycle and data set |
| 17 | Previous-Season | Within the previous season and data set |
| 18 | Q1-Shifted | First Quarter |
| 19 | Q2-Shifted | Second Quarter |
| 20 | Q3-Shifted | Third Quarter |
| 21 | Q4-Shifted | Fourth Quarter |
| 22 | Seasonal | e.g. “Summer, Spring, Fall, and Winter” based cycle |
| 23 | Sub-block | A portion of a block of data |
| 24 | Weekly-shifted | Weekly Self Read |
| 25 | Expiration | The time at which an action is scheduled to expire. |
| 26 | Has | “Exists” or “is” |
| 27 | Last | Of all the previous readings, this one is the most recent chronologically. |
| 28 | Next | Of any future (pending) events, this one is next. |
| 29 | Requires | “Must” or “Mandates” |
| 30 | Start | The time at which an action is scheduled to start. |

Attribute #2, Data Qualifier

The data type can be used to describe a salient attribute of the data. Possible enumerations include those described in Table C.2.

# Table C.2 -- Data Qualifier Enumerations

| Index | Enumeration | Comments |
| --- | --- | --- |
| 0 |  | Not Applicable |
| 1 | Absolute |  |
| 2 | Average |  |
| 3 | Compensated |  |
| 4 | Excess |  |
| 5 | HighThreshold |  |
| 6 | Incremental |  |
| 7 | LowThreshold |  |
| 8 | Maximum |  |
| 9 | Minimum |  |
| 10 | Missing |  |
| 11 | Nominal |  |
| 12 | Normal |  |
| 13 | Relative |  |
| 14 | Required |  |
| 15 | RMS | Root Mean Squared |
| 16 | SecondMaximum |  |
| 17 | SecondMinimum |  |
| 18 | SurveyData | Data which should serve as a representative sample of the population |
| 19 | TestData | Not real billing data |
| 20 | Uncompensated |  |
| 21 | Unstable |  |
| 22 | Action |  |

Attribute #3, Accumulation behaviour

The “accumulation behaviour” indicates how the value is represented to accumulate over time. Enumerated values include those described in Table C.3.

One benefit to explicitly declaring the accumulation behaviour as part of the readingType in an exchange between a MS and MDM is to help the MDM ensure that appropriate validation rules are applied to the data supplied by the MS.

# Table C.3 – Accumulation Behaviour Enumerations

| Index | Enumeration | Comments |
| --- | --- | --- |
| 0 |  | Not Applicable, or implied by the unit of measure. |
| 1 | BulkQuantity | A value from a register which represents the bulk quantity of a commodity. This quantity is computed as the integral of the commodity usage rate. This value is used as the basis for the dial reading at the meter, and as a result, may roll over upon reaching a maximum dial value. Note: This enumeration is usually implied by the context. Users may elect to omit phrases implied by their context from a textual description (e.g. the “alias name”), but choose to retain them in the numeric description (e.g. the “name”). |
| 2 | ContinuousCumulative | The sum of the previous billing period values and the present period value. |
| 3 | Cumulative | The sum of the previous billing period values. |
| 4 | DeltaData | The "consumption" or "usage" of a commodity between two distinct points in time. Or alternatively, the quantity consumed over a specific period of time (with "zero" at the start of the measurement). The period over which the begin and endpoints occur may be non-recurring or irregular (such as a billing period which changes size with the number of days in a month). Further context is provided by the TimeAttribute, Flow direction, and the time-stamp(s). (See also "Interval data" for a related concept). |
| 6 | Indicating | As if a needle swung out to a value to indicate the current value. |
| 7 | IntervalData | The "delta" difference between two values at regularly spaced intervals in time. The use of "IntervalData" implies that the datum is part of a consecutive series of data sampled at uniform intervals of time. |
| 8 | RecordedData | A series of data samples accompanied by timestamp(s) |
| 9 | Summation | A form of accumulation which may be selective with respect to time. Note: This enumeration is usually implied by the unit of measure. |
| 10 | TimeDelay | A form of computation which introduces a time delay characteristic to the data value |

It should be noted that the formulas for interval data are specific, and often qualified as “incremental” or “absolute”. (The “Data Qualifier” attribute can be used for this purpose.)

Incremental Interval Data (a “delta” or “interval” difference between two samples captured at regularly spaced intervals in time.)

Relative Interval Data (the difference between a scaled sample and a reference value.)

Absolute Recorded Data (a sample accompanied by a timestamp.)

Attribute #4, Direction of flow

Anything involving current might have a flow direction. Possible enumerations include those described in Table C.4.

# Table C.4 – Direction Of Flow Enumerations

| Index | Enumeration | Comments |
| --- | --- | --- |
| 0 |  | N/A |
| 1 | Forward | "Delivered," or "Import" See 61968-2 |
| 2 | Lagging | Typically used to describe that a power factor or reactive energy component is lagging the reference value. |
| 3 | Leading | Typically used to describe that a power factor or reactive energy component is leading the reference value. |
| 4 | Net | ¦Forward¦ - ¦Reverse¦, See 61968-2 |
| 5 | Q1+Q2 | Reactive positive quadrants |
| 6 | Q1+Q2+Q3+Q4 | Sum of all quadrants |
| 7 | Q1+Q3 |  |
| 8 | Q1+Q4 | Quadrants 1 and 4 |
| 9 | Q1-Q4 | Q1 minus Q4 |
| 10 | Q2+Q3 | Quadrants 2 and 3 |
| 11 | Q2+Q4 |  |
| 12 | Q2-Q3 | Q2 minus Q3 |
| 13 | Q3+Q4 | Reactive negative quadrants |
| 14 | Q3-Q2 | Q3 minus Q2 |
| 15 | Quadrant1 |  |
| 16 | Quadrant2 |  |
| 17 | Quadrant3 |  |
| 18 | Quadrant4 |  |
| 19 | Reverse | "Received," or "Export" See 61968-2 |
| 20 | Total | ¦Forward¦ + ¦Reverse¦, See 61968-2 |

Attribute #5, Unit of Measure Category

The categorization scheme described here breaks the unit of measure into separate classes. One class collects all types of meter readings, another meter system parameters, and yet another class for event related measurements. Categories include those described in Table C.5.

# Table C.5 – Unit of Measure Enumerations

| Attribute 5.1 --Subclass | Attribute 5.2 --Index | Enumeration | Comments |
| --- | --- | --- | --- |
| 0 | 0 |  | Not Applicable |
| 0 | 1 | Air |  |
| 0 | 2 | ApparentPowerFactor |  |
| 0 | 3 | Currency |  |
| 0 | 4 | Current |  |
| 0 | 5 | CurrentAngle |  |
| 0 | 6 | CurrentImbalance |  |
| 0 | 7 | Date |  |
| 0 | 8 | Demand |  |
| 0 | 9 | Distance |  |
| 0 | 10 | DistortionVoltAmperes |  |
| 0 | 11 | Energization |  |
| 0 | 12 | Energy |  |
| 0 | 13 | EnergizationLoadSide |  |
| 0 | 14 | Fan |  |
| 0 | 15 | Frequency |  |
| 0 | 16 | Funds |  |
| 0 | 17 | IEEE1366ASAI |  |
| 0 | 18 | IEEE1366ASIDI |  |
| 0 | 19 | IEEE1366ASIFI |  |
| 0 | 20 | IEEE1366CAIDI |  |
| 0 | 21 | IEEE1366CAIFI |  |
| 0 | 22 | IEEE1366CEMIn |  |
| 0 | 23 | IEEE1366CEMSMIn |  |
| 0 | 24 | IEEE1366CTAIDI |  |
| 0 | 25 | IEEE1366MAIFI |  |
| 0 | 26 | IEEE1366MAIFIe |  |
| 0 | 27 | IEEE1366SAIDI |  |
| 0 | 28 | IEEE1366SAIFI |  |
| 0 | 29 | InsulativeGas |  |
| 0 | 30 | InsulativeOil |  |
| 0 | 31 | LineLosses |  |
| 0 | 32 | Losses |  |
| 0 | 33 | NegativeSequence |  |
| 0 | 34 | PhasorPowerFactor |  |
| 0 | 35 | PhasorReactivePower |  |
| 0 | 36 | PositiveSequence |  |
| 0 | 37 | Power |  |
| 0 | 38 | PowerFactor |  |
| 0 | 39 | Price |  |
| 0 | 40 | QuantityPower |  |
| 0 | 41 | Sag | or Voltage Dip |
| 0 | 42 | Swell |  |
| 0 | 43 | SwitchPosition |  |
| 0 | 44 | TapPosition |  |
| 0 | 45 | TariffRate | DR |
| 0 | 46 | Temperature |  |
| 0 | 47 | TotalHarmonicDistortion |  |
| 0 | 48 | TransformerLosses |  |
| 0 | 49 | UNIPEDEVoltageDip10to15 |  |
| 0 | 50 | UNIPEDEVoltageDip15to30 |  |
| 0 | 51 | UNIPEDEVoltageDip30to60 |  |
| 0 | 52 | UNIPEDEVoltageDip60to90 |  |
| 0 | 53 | UNIPEDEVoltageDip90to100 |  |
| 0 | 54 | Voltage |  |
| 0 | 55 | VoltageAngle |  |
| 0 | 56 | VoltageExcursion |  |
| 0 | 57 | VoltageImbalance |  |
| 0 | 58 | Volume |  |
| 0 | 59 | ZeroFlowDuration |  |
| 0 | 60 | ZeroSequence |  |
| 1 | 0 | ApplicationContext |  |
| 1 | 1 | ApTitle |  |
| 1 | 2 | AssetNumber |  |
| 1 | 3 | Bandwidth |  |
| 1 | 4 | BatteryVoltage |  |
| 1 | 5 | BroadcastAddress |  |
| 1 | 6 | DeviceAddressType1 |  |
| 1 | 7 | DeviceAddressType2 |  |
| 1 | 8 | DeviceAddressType3 |  |
| 1 | 9 | DeviceAddressType4 |  |
| 1 | 10 | DeviceClass |  |
| 1 | 11 | ElectronicSerialNumber |  |
| 1 | 12 | EndDeviceID |  |
| 1 | 13 | GroupAddressType1 |  |
| 1 | 14 | GroupAddressType2 |  |
| 1 | 15 | GroupAddressType3 |  |
| 1 | 16 | GroupAddressType4 |  |
| 1 | 17 | IpAddress |  |
| 1 | 18 | MacAddress |  |
| 1 | 19 | MfgAssignedConfigurationID |  |
| 1 | 20 | MfgAssignedPhysicalSerialNumber |  |
| 1 | 21 | MfgAssignedProductNumber |  |
| 1 | 22 | MfgAssignedUniqueCommunicationAddress |  |
| 1 | 23 | MultiCastAddress |  |
| 1 | 24 | OneWayAddress |  |
| 1 | 25 | SignalStrength |  |
| 1 | 26 | TwoWayAddress |  |
| 2 | 0 | Alarm |  |
| 2 | 1 | BatteryCarryover |  |
| 2 | 2 | DataOverflowAlarm |  |
| 2 | 3 | DemandLimit |  |
| 2 | 4 | DemandReset |  |
| 2 | 5 | Diagnostic |  |
| 2 | 6 | EmergencyLimit |  |
| 2 | 7 | EncoderTamper |  |
| 2 | 8 | IEEE1366MomentaryInterruption |  |
| 2 | 9 | IEEE1366MomentaryInterruptionEvent |  |
| 2 | 10 | IEEE1366SustainedInterruption |  |
| 2 | 11 | InterruptionBehaviour |  |
| 2 | 12 | InversionTamper |  |
| 2 | 13 | LoadInterrupt |  |
| 2 | 14 | LoadShed |  |
| 2 | 15 | Maintenance |  |
| 2 | 16 | PhysicalTamper |  |
| 2 | 17 | PowerLossTamper |  |
| 2 | 18 | PowerOutage |  |
| 2 | 19 | PowerQuality |  |
| 2 | 20 | PowerRestoration |  |
| 2 | 21 | Programmed |  |
| 2 | 22 | Pushbutton |  |
| 2 | 23 | RelayActivation |  |
| 2 | 24 | RelayCycle |  |
| 2 | 25 | RemovalTamper |  |
| 2 | 26 | ReprogrammingTamper |  |
| 2 | 27 | ReverseRotationTamper |  |
| 2 | 30 | SwitchArmed |  |
| 2 | 31 | SwitchDisabled |  |
| 2 | 32 | Tamper |  |
| 2 | 33 | WatchdogTimeout |  |

Attribute #6, Measurement Category Enumerations

The technique proposed here is to categorize cardinal and ordinal number values into families of codes as described in table C.6.

# Table C.6 – Measurement Categories

| Attribute 6.1 -- Category | Error |
| --- | --- |
| 0 | Harmonics |
| 1 | Interharmonics |
| 2 | Ordinal or cardinal numbering |
| 3 | Time of Use (TOU) tier numbering |
| 4 | Currency code (per ISO 4217) |

These categories provide context for the numbering scheme supplied by attribute 6.2. Attribute 6.2 is merely a number. Joined together, they form attribute 6 as described in table C.7.

# Table C.7 – MeasurementCategory Enumerations

| Attribute 6 - Categorized Index | Enumeration | Comments |
| --- | --- | --- |
| 0.0 |  | Not Applicable |
| 0.1 | Harmonic1 | fundamental |
| 0.2 | Harmonic2 | second harmonic |
| 0.3 | Harmonic3 | third harmonic |
| 0.4 | Harmonic4 | fourth harmonic |
| 0.5 | Harmonic5 | fifth harmonic |
| 0.6 | Harmonic6 | sixth harmonic |
| 0.7 | Harmonic7 | etc. (additional harmonics (up to 999) created as necessary in category=0) |
| 1.1 | Interharmonic1 | fundamental |
| 1.2 | Interharmonic2 | second interharmonic |
| 1.3 | Interharmonic3 | third interharmonic |
| 1.4 | Interharmonic4 | fourth interharmonic |
| 1.5 | Interharmonic5 | fifth interharmonic |
| 1.6 | Interharmonic6 | sixth interhamonic |
| 1.7 | Interharmonic7 | etc. (additional interharmonics (up to 999) created as necessary in category=1) |
| 2.0 | n0 | Zeroth unit (for systems that use zero based numbering schemes) |
| 2.1 | n1 | First; or "1" where the measure needs an argument such as CEMI(n=1) |
| 2.2 | n2 | Second; or "2" where the measure needs an argument such as CEMI(n=2) |
| 2.3 | n3 | Third; or "3" where the measure needs an argument such as CEMI(n=3) |
| 2.4 | n4 | Fourth; or "4" where the measure needs an argument such as CEMI(n=4) |
| 2.5 | n5 | Fifth; or "5" where the measure needs an argument |
| 2.6 | n6 | Sixth, or "6" |
| 2.7 | n7 | Seventh, or "7" |
| 2.8 | n8 | Eigth, or "8" |
| 2.9 | n9 | Nineth, or "9" |
| 2.10 | n10 | Tenth, or "10" |
| 2.15 | n15 | "15" |
| 2.30 | n30 | "30" |
| 2.45 | n45 | "45" |
| 2.60 | n60 | "60" |
| 21.55 | n155 | "155" |
| 2.305 | n305 | “305”, etc. (additional numbers up to 999 as necessary in class=2) |
| 3.1 | TouRateA | First Tier |
| 3.2 | TouRateB | Second Tier |
| 3.3 | TouRateC | Third Tier |
| 3.4 | TouRateD | Fourth Tier |
| 3.5 | TouRateE | Fifth Tier |
| 3.6 | TouRateF | Sixth Tier |
| 3.7 | TouRateG | etc. (additional tiers (up to 999) created as necessary in class=3) |
| 4.392 | JPY | Japanese Yen, adapted from ISO 4217 currency codes |
| 4.710 | ZAR | South African Rand |
| 4.752 | SEK | Swedish Krona |
| 4.756 | CHF | Swiss Franc |
| 4.840 | USD | US Dollar |
| 4.978 | EUR | Euro |

Attribute #7, Phase

The proposed phase enumerations are described in Table C.8.

# Table C.8 – Phase Enumerations

| Index | Enumeration | Comments | A1 | B1 | C1 | N1 | A2 | B2 | C2 | N2 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 |  | Not Applicable to any phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 128 | Phase-A | Phase A | 1 |  |  |  |  |  |  |  |
| 136 | Phase-AA | Phase A current relative to Phase A voltage | 1 |  |  |  | 1 |  |  |  |
| 132 | Phase-AB | Phase A to B | 1 |  |  |  |  | 1 |  |  |
| 225 | Phase-ABC-N | ABC to Neutral | 1 | 1 | 1 |  |  |  |  | 1 |
| 193 | Phase-AB-N | AB to Neutral | 1 | 1 |  |  |  |  |  | 1 |
| 129 | Phase-AN | Phase A to Neutral | 1 |  |  |  |  |  |  | 1 |
| 64 | Phase-B | Phase B |  | 1 |  |  |  |  |  |  |
| 72 | Phase-BA | Phase B current relative to Phase A voltage |  | 1 |  |  | 1 |  |  |  |
| 66 | Phase-BC | Phase B to C |  | 1 |  |  |  |  | 1 |  |
| 97 | Phase-BC-N | BC to Neutral |  | 1 | 1 |  |  |  |  | 1 |
| 65 | Phase-BN | Phase B to Neutral |  | 1 |  |  |  |  |  | 1 |
| 32 | Phase-C | Phase C |  |  | 1 |  |  |  |  |  |
| 40 | Phase-CA | Phase C current relative to Phase A voltage |  |  | 1 |  | 1 |  |  |  |
| 40 | Phase-CA | Phase C to A |  |  | 1 |  | 1 |  |  |  |
| 41 | Phase-CA-N | CA to Neutral |  |  | 1 |  | 1 |  |  | 1 |
| 33 | Phase-CN | Phase C to Neutral |  |  | 1 |  |  |  |  | 1 |
| 16 | Phase-N | Neutral |  |  |  | 1 |  |  |  |  |
| 224 | Phases-ABC | Involving all phases | 1 | 1 | 1 |  |  |  |  |  |

Note: The index values were computed by:

When current is measured, it is often simple a single phase conductor indicated such as:

- A

- B

- C

- N

When voltage is measured, it may contain a simple description of the phase conductor, or if measured relative to something else, an indication of the measurement being “line-to-neutral” or “line-to-line” measured. Common voltage measurements include:

A

B

C

AN

BN

CN

AB

BC

CA

ABC

When phase angles are measured, it is usually relative to a fixed reference such as voltage phase A. The word “angle” has already been described in a previous field. This field may therefore contain an angle designation such as:

AcurrentAvolts

BcurrentAvolts

CcurrentAvolts

Where the first phase listed describes the current or voltage phase being measured, and the second phase (the “A”) describes what it is being measured against (voltage phase A.) Since the fact that the measurement is an angle can be determined from the context (provided by the unit of measure), and the point of reference is always the second phase, there is no need to provide additional indications within the phase lettering. This allows the same code (such as “Phase-CA”) to be used as a line-to-line voltage descriptor, a voltage phase-angle descriptor, as well as a current phase-angle descriptor.

Attribute #8, Metric Multiplier

The CIM has developed a technique of separating the metric multiplier from the unit of measure. In an effort to avoid negative numbers as enumeration values, negative exponents are made positive by the creation of a large positive number. The proposed multiplier enumerations are described in Table C.9.

# Table C.9 – Metric Multiplier Enumerations

| Index | Enumeration | Comments |
| --- | --- | --- |
| 0 |  | Not Applicable or "x1" |
| 1 | Da | Deca = x10 = x101 |
| 2 | ‘h’ or ‘%’ | hecto, x100 (or a dimensionless value expressed as a percentage) = x102 |
| 3 | K | kilo, x1,000 = x103 |
| 6 | M | Mega, x1,000,000 = x106 |
| 9 | G | Giga = x1,000,000,000 = x109 |
| 255 | d | Deci = x0.1 = x10-1 |
| 254 | c | Centi = x0.01 = x10-2 |
| 253 | m | milli, x0.001 = x10-3 |
| 250 | μ | micro, x0.000,001 = x10-6 |
| 247 | n | nano, x0.000,000,001 = x10-9 |

Attribute #9, Displayable Unit of Measure (UOM)

The displayable unit of measure is typically indicated on the meter faceplate. Typical units of measure include those described in Table C.10.

# Table C.10 – Unit of Measure Enumerations

| Value | Quantity | Unit name | Symbol |
| --- | --- | --- | --- |
| 0 | N/A | none |  |
| 2 | Length | meter | m |
| 3 | Mass | gram | g |
| 4 | Rotational speed | rotations per second | rev/s |
| 5 | Current | ampere | A |
| 6 | Temperature | Kelvin | K |
| 7 | Amount of substance | mole | mol |
| 8 | Luminous intensity | candela | cd |
| 9 | Plane angle | degrees | deg |
| 10 | Plane angle | radian | rad |
| 11 | Solid angle | steradian | sr |
| 21 | Absorbed dose | Gray (J/kg) | Gy |
| 22 | Radioactivity | Becquerel (l/s) | Bq |
| 23 | Relative temperature | degrees Celsius | °C |
| 24 | Dose equivalent | Sievert (J/kg) | Sv |
| 25 | Electric capacitance | Farad (C/V) | F |
| 26 | Electric charge | Coulomb (AS) | C |
| 27 | Time | second | seconds |
| 28 | Electric inductance | Henry (Wb/A) | H |
| 29 | Electric potential | Volt (W/A) | V |
| 30 | Electric resistance | Ohm (VA) | Ω |
| 31 | Energy joule | (N m) | J |
| 32 | Force newton | (kg m/s²) | N |
| 33 | Frequency hertz | (1/s) | Hz |
| 34 | Illuminance lux | (lm/m²) | lx |
| 35 | Luminous flux | lumen (cd sr) | Lm |
| 36 | Magnetic flux | Weber (V s) | Wb |
| 37 | Magnetic flux density | Tesla (Wb/m2) | T |
| 38 | Real power | Watts (I²R) | W |
| 39 | Pressure | Pascal (N/m²) | Pa |
| 41 | Area | square meter | m² |
| 42 | Volume | cubic meter | m³ |
| 43 | Velocity | meters per second (m/s) | m/s |
| 44 | Acceleration | meters per second squared | m/s² |
| 45 | Volumetric flow rate | cubic meters per second | m³/s |
| 46 | Fuel efficiency | meters / cubic meter | m/m³ |
| 47 | Moment of mass | kilogram meter (kg m) | M |
| 48 | Density | kilogram/cubic meter | kg/m³ |
| 49 | Viscosity | meter squared / second | m²/s |
| 50 | Thermal conductivity | Watt/meter Kelvin | W/m K |
| 51 | Heat capacity | Joule/Kelvin | J/K |
| 52 | Concentration | parts per million | ppm |
| 53 | Electric conductance | Siemens (A/V) | Siemens |
| 54 | Angular velocity | radians per second | rad/s |
| 61 | Apparent power | Volt Ampere | VA |
| 63 | Reactive power | Volt Ampere reactive (VISinθ) | VAr |
| 64 | Phase angle | degrees | θ-Deg |
| 65 | Power factor | dimensionless | Cosθ |
| 66 | Volt seconds | Volt seconds (Ws/A) | Vs |
| 67 | Volts squared | Volt squared (W2/A2) | V² |
| 68 | Amp seconds | amp seconds | As |
| 69 | Amps squared | amp squared | A² |
| 70 | Amps squared time | amp square second | A²t |
| 71 | Apparent energy | Volt Ampere hours | VAh |
| 72 | Real energy | Watt hours | Wh |
| 73 | Reactive energy | Volt Ampere reactive hours | VArh |
| 74 | Magnetic flux | Volts per Hertz | V/Hz |
| 75 | Rate of change of frequency | hertz per second | Hz/s |
| 76 | Number of characters | characters | char |
| 77 | Data rate | characters per second | char/s |
| 78 | Turbine inertia | kg square meter | kgm² |
| 79 | Sound pressure level | decibel | dB |
| 80 | Monetary unit | Money (Note: Generic money unless supplemented with ISO 4217 currency codes via MeasurementCategory Enumerations). | ¤ |
| 100 | Quantity power | Q | Q |
| 101 | Quantity energy | Qh | Qh |
| 102 | resistivity | ρ (rho) | Ωm |
| 103 | A/m | magnetic field strength, Ampere per metre | A/m |
| 104 | volt-squared hour | Volt-squared-hours | V²h |
| 105 | ampere-squared hour | Ampere-squared hour | A²h |
| 106 | Ampere-hours | Ampere-hours | Ah |
| 107 | Wh/m3 | energy per volume | Wh/m³ |
| 108 | Timestamp | time and date per ISO 8601 | timeStamp |
| 109 | Boolean | "1" = "true", "live", "on", "high", "set"; "0" = "false", "dead", "off", "low", "cleared" | status |
| 110 | BooleanArray | An array of boolean values describing an array or gang of switches | statuses |
| 111 | Count | counter value | Count |
| 113 | Signal Strength | receive signal strength indicator | dBm |
| 114 | ApplicationValue | encoded value | Code |
| 115 | Kh-Wh | active energy metering constant | Wh/rev |
| 116 | Kh-VArh | reactive energy metering constant | VArh/rev |
| 117 | Kh-Vah | apparent energy metering constant | VAh/rev |
| 118 | EndDeviceEvent | value to be interpreted as a EndDeviceEventCode | MeCode |

Using data element attributes to define the ReadingType

General

The “ReadingType” may be automatically generated by judiciously populating each of the attributes and presenting them in order side-by-side. It is recommended that attributes be as explicit as possible to identify a data element, but on the other hand, not become so explicit that it overspecifies the data element.

The mRID of the ReadingTypeID is taken as authoritative by the system, and can be generated by presenting the numeric form of each attribute in side-by-side fashion seperated by commas (i.e. CSV style).

<ReadingTypeID mRID> := <attribute 1>.<attribute 2>.<attribute 3>.<attribute 4>.<attribute 5>.<attribute 6>.<attribute 7>.<attribute 8>.<attribute 9>

It should be noted that two of the attributes themselves are compound fields. This result is to have a Name with 11 fields:

- TimeAttribute

- DataQualifier

- AccumlationBehaviour

- FlowDirection

- UomCategorySubclass

- UomCategoryIndex

- MeasurementCategory

- Enumeration

- Phase

- Multiplier

- UnitOfMeasure

This Name can be regionalized as appropriate by using the regional text form for each attribute, and presenting them in order, side-by-side, seperated by spaces. The example described below suggests that the metric multiplier together with the unit of measure attributes be presented within parenthesis without a space seperator. This produces an effective unit of measure for the data element. In order to eliminate excessive spoken words, a practice may be established within a product of exposing a simplified aliasName or description to users. The aliasName can offer a simplified name which omits attributes which are clearly understood from the context.

<Name> := <attribute 1> <attribute 2> <attribute 3> <attribute 4> <attribute 5> <attribute 6> <attribute 7> (<attribute 8><attribute 9>)

While a good interface will eliminate abigutity, and not publish “anonymous” data, a good interface will also not go to the other extreme and overspecify the data it publishes. The concept is similar to the practice of publishing an appropriate number of digits of resolution for a numerical value. One system may know (for example) the phase on which a voltage was measured and supply it as an attribute of the measurement. Another system might not know the phase with good authority and simply publish the voltage measured at a given meter. One system might not The ReadingTypeIDs used by a data publisher should be appropriate for the data supplied. The ReadingTypeIDs used in a response may (therefore) differ slightly than the ReadingTypeIDs used in a request.

Examples of ReadingTypeIDs are found in table C.11. These are merely examples, and by no means an exhaustive list of what can be constructed given the enumeration values listed above.

# Table C.11 – Example ReadingTypes

| Example mRID | Example Name | Example aliasName |
| --- | --- | --- |
| 2.6.7.1.0.12.0.0.0.3.72 | 15-minute Incremental IntervalData Forward Energy (kWh) | 15-minute IntervalData Forward Energy (kWh) |
| 4.6.4.0.2.8.0.0.0.0.111 | 24-hour Incremental DeltaData IEEE1366MomentaryInterruption (Count) | Momentary Interruption (count) |
| 4.6.4.0.2.9.0.0.0.0.111 | 24-hour Incremental DeltaData IEEE1366MomentaryInterruptionEvent (Count) | Momentary Interruption Event (count) |
| 4.6.4.0.2.10.0.0.0.0.111 | 24-hour Incremental DeltaData IEEE1366SustainedInterruption (Count) | Sustained Interruption (count) |
| 4.6.4.0.2.10.0.0.0.0.27 | 24-hour Incremental DeltaData IEEE1366SustainedInterruption (seconds) | Sustained Interruption (seconds) |
| 7.6.7.1.0.12.0.0.0.3.73 | 60-minute Incremental IntervalData Forward Energy (kVArh) | Hourly Interval Data Forward Energy (kVArh) |
| 7.6.7.1.0.12.0.0.0.3.72 | 60-minute Incremental IntervalData Forward Energy (kWh) | Hourly Interval Data Forward Energy (kWh) |
| 7.6.7.4.0.12.0.0.0.3.73 | 60-minute Incremental IntervalData Net Energy (kVArh) | Hourly Interval Data Net Energy (kVArh) |
| 7.6.7.4.0.12.0.0.0.3.72 | 60-minute Incremental IntervalData Net Energy (kWh) | Hourly Interval Data Net Energy (kWh) |
| 7.6.7.19.0.12.0.0.0.3.73 | 60-minute Incremental IntervalData Reverse Energy (kVArh) | Hourly Interval Data Reverse Energy (kVArh) |
| 7.6.7.19.0.12.0.0.0.3.72 | 60-minute Incremental IntervalData Reverse Energy (kWh) | Hourly Interval Data Reverse Energy (kWh) |
| 7.6.7.20.0.12.0.0.0.3.73 | 60-minute Incremental IntervalData Total Energy (kVArh) | Hourly Interval Data Total Energy (kVArh) |
| 7.6.7.20.0.12.0.0.0.3.72 | 60-minute Incremental IntervalData Total Energy (kWh) | Hourly Interval Data Total Energy (kWh) |
| 0.0.1.0.2.4.0.0.0.0.111 | BulkQuantity DemandReset (Count) | DemandReset (Count) |
| 0.0.1.0.0.11.0.0.0.0.111 | BulkQuantity Energization (Count) | Energization (Count) |
| 0.0.1.1.0.12.0.0.0.3.73 | BulkQuantity Forward Energy (kVArh) | Forward Energy (kVArh) |
| 0.0.1.1.0.12.0.0.0.3.72 | BulkQuantity Forward Energy (kWh) | Forward Energy (kWh) |
| 0.0.1.0.2.13.2.0.0.0.111 | BulkQuantity LoadInterrupt n0 (Count) | LoadInterrupt (Count) |
| 0.0.1.0.2.13.2.1.0.0.111 | BulkQuantity LoadInterrupt n1 (Count) |  |
| 0.0.1.4.0.12.0.0.0.3.73 | BulkQuantity Net Energy (kVArh) | Net Energy (kVArh) |
| 0.0.1.4.0.12.0.0.0.3.72 | BulkQuantity Net Energy (kWh) | Net Energy (kWh) |
| 0.0.1.0.2.23.2.0.0.0.111 | BulkQuantity RelayActivation n0 (Count) | RelayActivation (Count) |
| 0.0.1.0.2.24.2.0.0.0.111 | BulkQuantity RelayCycle n0 (Count) |  |
| 0.0.1.0.2.24.2.1.0.0.111 | BulkQuantity RelayCycle n1 (Count) |  |
| 0.0.1.19.0.12.0.0.0.3.73 | BulkQuantity Reverse Energy (kVArh) | Reverse Energy (kVArh) |
| 0.0.1.19.0.12.0.0.0.3.72 | BulkQuantity Reverse Energy (kWh) | Reverse Energy (kWh) |
| 0.0.1.20.0.12.0.0.0.3.73 | BulkQuantity Total Energy (kVArh) | Total Energy (kVArh) |
| 0.0.1.20.0.12.0.0.0.3.72 | BulkQuantity Total Energy (kWh) | Total Energy (kWh) |
| 11.8.6.1.0.8.0.0.0.3.38 | Daily-Shifted Maximum Indicating Forward Demand (kW) | Daily Max Demand (kW) |
| 11.0.9.1.0.12.3.1.0.3.72 | Daily-Shifted Summation Forward Energy TouRateA (kWh) | Daily Forward TOU Rate A (kWh) |
| 0.0.0.0.0.011.0.0.0.0.109 | Energization ( status) | Energization status |
| 0.0.6.0.0.4.0.0.0.0.5 | Indicating Current (A) | Current (A) |
| 0.0.6.0.0.4.0.0.128.0.5 | Indicating Current Phase-A (A) | Current Phase A (Amps) |
| 0.0.6.0.0.4.0.0.64.0.5 | Indicating Current Phase-B (A) | Current Phase B (Amps) |
| 0.0.6.0.0.4.0.0.32.0.5 | Indicating Current Phase-C (A) | Current Phase C (Amps) |
| 0.0.6.0.0.5.0.0.136.0.64 | Indicating CurrentAngle Phase-AAv (θ-Deg) | CurrentAngle Phase-AAv (θ-Deg) |
| 0.0.6.0.0.5.0.0.72.0.64 | Indicating CurrentAngle Phase-BAv (θ-Deg) | CurrentAngle Phase-BAv (θ-Deg) |
| 0.0.6.0.0.5.0.0.41.0.64 | Indicating CurrentAngle Phase-CAv (θ-Deg) | CurrentAngle Phase-CAv (θ-Deg) |
| 0.0.6.0.0.15.0.0.0.0.33 | Indicating Frequency (Hz) | Frequency (Hz) |
| 0.0.6.0.0.38.0.0.0.0.65 | Indicating PowerFactor (Cosθ) | PowerFactor (Cosθ) |
| 0.0.6.0.0.54.0.0.0.0.29 | Indicating Voltage (V) | Voltage (V) |
| 0.0.6.0.0.54.0.0.128.0.29 | Indicating Voltage Phase-A (V) | Voltage Phase A (V) |
| 0.0.6.0.0.54.0.0.64.0.29 | Indicating Voltage Phase-B (V) | Voltage Phase B (V) |
| 0.0.6.0.0.54.0.0.32.0.29 | Indicating Voltage Phase-C (V) | Voltage Phase C (V) |
| 0.0.6.0.0.55.0.0.72.0.64 | Indicating VoltageAngle Phase-BAv (θ-Deg) | VoltageAngle Phase-BAv (θ-Deg) |
| 0.0.6.0.0.55.0.0.41.0.64 | Indicating VoltageAngle Phase-CAv (θ-Deg) | VoltageAngle Phase-CAv (θ-Deg) |
| 12.0.6.1.0.8.0.0.0.3.38 | Instantaneous Indicating Forward Demand (kW) | Instantaneous Demand (kW) |
| 15.0.3.1.0.8.0.0.0.3.38 | Present Cumulative Forward Demand (kW) | Present Cumulative Demand (kW) |
| 15.8.6.1.0.8.0.0.0.3.38 | Present Maximum Indicating Forward Demand (kW) | Max Demand (kW) |
| 16.8.6.1.0.8.0.0.0.3.38 | Previous Maximum Indicating Forward Demand (kW) | Max Demand (kW) |
| 16.16.6.1.0.8.0.0.0.3.38 | Previous SecondMaximum Indicating Forward Demand (kW) | Second Max Demand (kW) |
| 0.0.9.20.0.12.3.1.0.3.73 | Summation Total Energy TouRateA (kVArh) | Total Energy TOU Rate A (kVArh) |
| 0.0.9.20.0.12.3.1.0.3.72 | Summation Total Energy TouRateA (kWh) | Total Energy TOU Rate A (kWh) |
| 0.0.9.20.0.12.3.2.0.3.73 | Summation Total Energy TouRateB (kVArh) | Total Energy TOU Rate B (kVArh) |
| 0.0.9.20.0.12.3.2.0.3.72 | Summation Total Energy TouRateB (kWh) | Total Energy TOU Rate B (kWh) |
| 0.0.9.20.0.12.3.3.0.3.73 | Summation Total Energy TouRateC (kVArh) | Total Energy TOU Rate C (kVArh) |
| 0.0.9.20.0.12.3.3.0.3.72 | Summation Total Energy TouRateC (kWh) | Total Energy TOU Rate C (kWh) |
| 0.0.0.0.0.43.0.0.0.0.118 | SwitchPosition ( MeCode) |  |

(Informative)

Recommended Quality Code enumerations

General

Quality codes may be returned with a Reading.value to indicate that there is something remarkable about the data. This annex describes proposed enumerations for quality codes to be used in this context.

The presence of a quality code is optional. When a value of zero is supplied, it is taken to mean that a system is explicitly declaring that the data is valid. When an end device which produces the data (a meter) declares data to be valid, it is saying that no remarkable events occurred during the collection of the data. Whan a meter data management system says that the data is “valid” it implies that the value has satisfied all of the appropriate validation rules.

The quality code values defined by this section are conveyed within a message using the ReadingQuality.quality element.

Identification of the system offering commentary on the data

Concievably, any piece of equipment which touches the data could introduce error, or offer remarks regarding the veracity of the data. For example, a meter might record interval data, and offer this data to the data collection system, but in doing so also indicate that something remarkable (such as a power outage or clock adjustment) occurred during some of the intervals. A meter data collection system might obtain readings from the field, but perform a sanity check on the values to find that some of them are unreasonable. A meter data management system, armed with a knowledge of the account history and usage patterns might scrutinize the data to find that certain values are suspect or possibly suggest that tampering may have occurred. All of these systems need an opportunity to comment on the data without (necessarily) changing it. When a system does change the data, this too can be noted in the quality codes.

This annex proposes using a three digit code as a prefix to the actual quality code. This is described in Table D.1.

| Table D.1 – Example System IdentifiersValue | Issuer of code |
| --- | --- |
| 0 | Not Applicable, or unidentified |
| 1 | End Device |
| 2 | Metering system (data collection) network |
| 3 | Meter Data Management System |

Quality Code Categorization

Quality codes can be categorized. Table D.2 describes the categories proposed by this annex.

# Table D.2 – Example Quality Code Categories

| Category | Description |
| --- | --- |
| 1 | Diagnostics related |
| 2 | Power quality related issues at the data collection point |
| 3 | Tamper / Revenue Protection related |
| 4 | Data collection related |
| 5 | Failed reasonability testing |
| 6 | Failed validation testing |
| 7 | Edited |
| 8 | Estimated |
| 9 | Oscillatory |
| 10 | Questionable |

Quality Code Index

When these categories are applied to a particular index of codes, it results in examples such as those in Table D.3.

# Table D.3 – Example Categorized Codes

| Categorized code | Enumeration | Comments |
| --- | --- | --- |
| Null | AssumedValid | Missing or empty quality code tags |
| 0.0 | DataValid | The system which declares the data as "valid" is indicated by the origin code. |
| 1.0 | DiagnosticsFlag | Look for related EndDeviceEvent(s) |
| 1.1 | BatteryLow |  |
| 1.3 | SensorFailure |  |
| 1.4 | WatchdogFlag |  |
| 2.0 | PowerQualityFlag | Look for related MeterEvent(s) |
| 2.1 | ExcessiveOutageCount | Power outage threshold count exceeded |
| 2.2 | PqCounter | Power quality threshould count exceeded |
| 2.3 | ServiceDisconnectSwitching | Service Disconnect operation during data collection interval |
| 2.32 | PowerFail | Power fail occurred during or at the start of this interval. ANSI C12.19. If power is out for the entire interval, the data value presented should be zero. |
| 3.0 | RevenueProtection | Tamper / Revenue Protection Suspect flag Look for related EndDeviceEvent(s) |
| 3.1 | CoverOpened |  |
| 3.2 | LogicalDisconnect |  |
| 3.3 | RevenueProtectionSuspect |  |
| 3.4 | ReverseRotation |  |
| 3.5 | StaticDataFlag |  |
| 4.0 | AlarmFlag |  |
| 4.1 | OverflowConditionDetected | Numeric overflow condition detected in the meter |
| 4.2 | PartialInterval | Partial interval recorded in the meter due to clock change, power outage, or some similar event. |
| 4.3 | LongInterval | Long interval recorded in the meter due to a clock change or some similar event. |
| 4.4 | SkippedInterval | Skipped interval by the meter due to a clock change or similar event. |
| 4.5 | TestData |  |
| 4.6 | ConfigurationChanged | Configuration changed during this interval |
| 4.7 | NotRecording | Load profile recording stopped |
| 4.16 | DstInEffect | Daylight saving time in effect during or at start of this interval |
| 4.64 | ClockSetForward | Clock set forward during or at the start of this interval. The interval may be short. |
| 4.128 | ClockSetBackward | Clock set backward during or at the start of this interval. The interval may be long. |
| 4.259 | DstChangeOccurred | Data has been adversely affected by a change in Daylight Saving Time. Timestamps and/or data values may be incorrect. Note: Compared to the ANSI C12.19 approach in which the DST flag is set for the entire Summer, this flag is only set for the affected data when the DST change occurs in the Spring and Fall. |
| 5.256 | DataOutsideExpectedRange | Presented data was identified as "invalid" by the originating system. |
| 5.257 | ErrorCode | Data was identified as "invalid" by the originating system and replaced with a special coded value to indicate an error. |
| 5.258 | Suspect | Data should be scrutinized and considered suspect |
| 5.259 | KnownMissingRead |  |
| 6.0 | Failed generic validation |  |
| 6.1 | Failed validation rule #1 | It is recommended that the validation rule numbers be assigned regional prefixes as necessary. For example, USCAISO1, AUS1, etc. |
| 6.2 | Failed validation rule #2 |  |
| 6.3 | Failed validation rule #3 |  |
| 6.4 | Failed validation rule #4 |  |
| 6.5 | Failed validation rule #5 |  |
| 6.6 | Failed validation rule #6 |  |
| 6.7 | Failed validation rule #7 |  |
| 6.8 | Failed validation rule #8 |  |
| 6.9 | Failed validation rule #9 |  |
| 6.10 | Failed validation rule #10 | Etc. |
| 7.0 | Manually edited | Generic |
| 7.1 | Edited 1 | Edited using approach #1 |
| 7.2 | Edited 2 | Edited using approach #2 |
| 7.3 | Edited 3 | Etc. |
| 8.0 | Generic Estimation |  |
| 8.1 | Estimated 1 | Estimated value using approach #1 |
| 8.2 | Estimated 2 | Estimated value using approach #2 |
| 8.3 | Estimated 3 | Etc. |

Categorized Quality Codes With Originator Identifier

When the concepts described above are combined, it can result in a code that fully describes the originating system, along with the categorized quality code.

# ReadingQuality.quality := <Originating System ID>.<Code Category>.<Code Index>

# Examples of the resulting quality code are described in table D.4

# Table D.4 – Example Quality Codes

| QualityCode | Origin | Code |
| --- | --- | --- |
| Null | N/A | 0 | AssumedValid | Null |
| 1.0.0 | EndDevice | 1 | DataValid | 0.0 |
| 2.0.0 | MsNetwork | 2 | DataValid | 0.0 |
| 3.0.0 | MDM | 3 | DataValid | 0.0 |
| 3.8.0 | MDM | 3 | Generic estimation | 8.0 |
| 3.6.1 | MDM | 3 | Failed validation rule #1 | 6.1 |
| 1.4.5 | EndDevice | 1 | TestData | 4.5 |
| 1.5.257 | EndDevice | 1 | ErrorCode | 5.257 |
| 2.5.256 | MsNetwork | 2 | DataOutsideExpectedRange | 5.256 |
| 1.4.5 | EndDevice | 1 | TestData | 4.5 |
| 2.3.4 | MsNetwork | 2 | ReverseRotation | 3.4 |
| 1.1.4 | EndDevice | 1 | WatchdogFlag | 1.4 |
| 3.3.5 | MDM | 3 | StaticDataFlag | 3.5 |
| 2.3.5 | MsNetwork | 2 | StaticDataFlag | 3.5 |
| 1.5.257 | EndDevice | 1 | ErrorCode | 5.257 |
| 2.4.259 | MsNetwork | 2 | DstChangeOccurred | 4.259 |
| 1.4.16 | EndDevice | 1 | DstInEffect | 4.16 |
| 1.4.1 | EndDevice | 1 | OverflowConditionDetected | 4.1 |
| 1.4.2 | EndDevice | 1 | PartialInterval | 4.2 |
| 1.4.3 | EndDevice | 1 | LongInterval | 4.3 |
| 1.4.4 | EndDevice | 1 | SkippedInterval | 4.4 |
| 3.8.1 | MDM | 3 | Estimated value using approach #1 | 8.1 |
| 3.7.0 | MDM | 3 | Manually edited (generic) | 7.0 |
| 3.7.2 | MDM | 3 | Edited using approach #2 | 7.2 |
| 3.3.3 | MDM | 3 | RevenueProtectionSuspect | 3.3 |

(Informative)

Recommended EndDeviceEvent Category Enumerations

General

Metering Systems collect not only readings from meters, and also must report exceptions. This annex describes recommended codes to be used for this function. The reader should note that part 9 supports the cross-pollenation of ReadingTypeID, EndDeviceEvent category, and EndDeviceControl type codes. A MeterReading may report an EndDeviceEvent by identifying in the unit of measure that the value should be interpreted as a EndDeviceEvent category. Likewise, there are many simularities between reported meter events and commands. An EndDeviceEvent which reports “Switch Open” can be issued as a command to “Open Switch.”

Note: A code of zero is recommended as a placeholder to indicate that “no event” has happened.

Codes for EndDeviceEvent.category values, as proposed by this annex, are categorized in a manner that divides the code into 4 parts:

# EndDeviceEvent.category := <domain>.<domain part>.<type>.<index>

EndDeviceEvent Domains

At the highest level, it is helpful to categorize event codes by the domain that they occur in.

Example domain codes are described in Table E.1.

# Table E.1 – Example EndDeviceEvent Domain Codes

| Domain Value | Enumeration |
| --- | --- |
| 1 | Communications |
| 2 | Device Asset |
| 3 | Electric meter |
| 4 | Gas meter |
| 5 | Gateway |
| 6 | Grid power |
| 7 | Security |
| 8 | Transformer |
| 9 | Turbine |

EndDeviceEvent Domain Parts

Domains can be subcategorized into parts. Example domain parts are described in Table E.2.

# Table E.2 – Example EndDeviceEvent Domain Part Codes

| Domain Part | Enumeration |
| --- | --- |
| 1 | Access |
| 2 | Battery |
| 3 | Cartridge |
| 4 | Circuit |
| 5 | Control |
| 6 | Current |
| 7 | Customer interface |
| 8 | Demand |
| 9 | DER switch |
| 10 | Enclosure |
| 11 | Firmware |
| 12 | Frequency |
| 13 | Gas metrology |
| 14 | Gateway device |
| 15 | Load control |
| 16 | Load profile |
| 17 | Logs |
| 18 | Memory |
| 19 | Messaging |
| 20 | Meter asset |
| 21 | Metrology |
| 22 | Mode |
| 23 | Network Interface |
| 24 | Password |
| 25 | Phase |
| 26 | Power |
| 27 | Power factor |
| 28 | Power quality |
| 29 | Pressure |
| 30 | Protective device |
| 31 | RCD switch |
| 32 | Security key |
| 33 | Tamper |
| 34 | Tariff |
| 35 | Temperature |
| 36 | Time |
| 37 | Transformer device |
| 38 | Voltage |

EndDeviceEvent types

EndDeviceEvent codes can be further subdivided into “types”. Example types are described in Table E.3.

# Table E.3 – Example EndDeviceEvent Type Codes

| Type Value | Enumeration |
| --- | --- |
| 1 | Alarm |
| 2 | Alarm management |
| 3 | Attribute |
| 4 | Calibration |
| 5 | Check status |
| 6 | Command |
| 7 | Configuration |
| 8 | Credit |
| 9 | End alarm |
| 10 | Identity |
| 11 | Maint mode |
| 12 | Metering mode |
| 13 | Outage |
| 14 | Quality Flag |
| 15 | Read Type |
| 16 | Setting |
| 17 | Status |
| 18 | Status check |
| 19 | Test mode |
| 20 | Requires |
| 21 | Has feature |

EndDeviceEvent Index

The most specific part of the EndDeviceEvent number is its index value. Example EndDeviceEvent indexes are presented in Table E.4.

# Table E.4 – Example EndDeviceEvent Indexes

| Index | Enumeration |
| --- | --- |
| 1 | Abort |
| 2 | Access attempt |
| 3 | Acknowledged |
| 4 | Activated |
| 5 | Adjusted |
| 6 | Alarm cleared |
| 7 | Allocation error |
| 8 | Almost full |
| 9 | Alter option |
| 10 | Alternate phone |
| 11 | Armed for closure |
| 12 | Armed for open |
| 13 | Association failure |
| 14 | Auto registration |
| 15 | Auto registration confirm |
| 16 | Battery charged |
| 17 | Battery failure |
| 18 | Blank |
| 19 | BTU alarm |
| 20 | Cable failed |
| 21 | Calculated |
| 22 | Call-in failure |
| 23 | Certificate expired |
| 24 | Changed |
| 25 | Changed by condition |
| 26 | Changed ID |
| 27 | Change-out |
| 28 | Cleared |
| 29 | Clock failed |
| 30 | Code changed |
| 31 | Cold start |
| 32 | Comm failed |
| 33 | Comm reestablished |
| 34 | Comm terminated |
| 35 | Command accepted |
| 36 | Command error |
| 37 | Command format error |
| 38 | Commanded change |
| 39 | Concentration |
| 40 | Configuration error |
| 41 | Connect failed |
| 42 | Connected |
| 43 | Corrupt data |
| 44 | Cover removed |
| 45 | Cross-phase |
| 46 | Cross-phase cleared |
| 47 | Current loss |
| 48 | Customer alarm |
| 49 | Customer configuration |
| 50 | Daily rate change |
| 51 | DAP failed |
| 52 | Data error |
| 53 | Date changed |
| 54 | Day change error |
| 55 | Day limit |
| 56 | Daylight time |
| 57 | Decreased |
| 58 | Default |
| 59 | Demand Limiting disabled, formula # |
| 60 | Demand Limiting enabled, formula # |
| 61 | Demand reset |
| 62 | Demand reset fail |
| 63 | DER connected |
| 64 | DER disconnected |
| 65 | Deviated |
| 66 | Disabled |
| 67 | Disconnect failed |
| 68 | Disconnected |
| 69 | Display error |
| 70 | Door closed |
| 71 | Door open |
| 72 | Download status |
| 73 | DSP failed |
| 74 | Duplicate |
| 75 | Emergency increase |
| 76 | Enabled |
| 77 | Encoder |
| 78 | EPROM failure |
| 79 | Error |
| 80 | Estimated |
| 81 | Event log cleared |
| 82 | Event log updated |
| 83 | Event log uploaded |
| 84 | EWM failure |
| 85 | Failed |
| 86 | Firmware failure |
| 87 | FPV unreasonable |
| 88 | Frozen |
| 89 | GC failure |
| 90 | Health OK |
| 91 | High distortion |
| 92 | High distortion cleared |
| 93 | High limit |
| 94 | High neutral current |
| 95 | History cleared |
| 96 | History updated |
| 97 | Holiday |
| 98 | Imbalance |
| 99 | Imbalance cleared |
| 100 | Inactive |
| 101 | Inactive cleared |
| 102 | Increased |
| 103 | Initial read |
| 104 | Input error |
| 105 | Installed |
| 106 | Invalid |
| 107 | Invalid attribute |
| 108 | Invalid blank name |
| 109 | Invalid command |
| 110 | Invalid date |
| 111 | Invalid delete |
| 112 | Invalid duplicate name |
| 113 | Invalid gateway ID |
| 114 | Invalid key |
| 115 | Invalid null |
| 116 | Invalid numeric |
| 117 | Invalid parameter |
| 118 | Invalid priority |
| 119 | Invalid return |
| 120 | Invalid search |
| 121 | Invalid serial number |
| 122 | Invalid sigmatic |
| 123 | Invalid time |
| 124 | Invalid time zone |
| 125 | Invalid timeout |
| 126 | Invalid type |
| 127 | Invalid value |
| 128 | Invalid version |
| 129 | Invalid XML |
| 130 | IO mismatch |
| 131 | Key disabled |
| 132 | Key enabled |
| 133 | Key unlocked |
| 134 | KYZ failure |
| 135 | Last read |
| 136 | Last read updated |
| 137 | Leading kvarh |
| 138 | Leading kvarh cleared |
| 139 | Limit exceeded |
| 140 | List cleared |
| 141 | List pointers reset |
| 142 | List pointers updated |
| 143 | Load energized |
| 144 | Load not-energized |
| 145 | Local access |
| 146 | Log error |
| 147 | Login failed |
| 148 | Login failed |
| 149 | Low battery detected |
| 150 | Low limit |
| 151 | Low modem battery |
| 152 | Magnetic |
| 153 | Measured |
| 154 | Memory error |
| 155 | Message error |
| 156 | Message failed |
| 157 | Meter comm failed |
| 158 | Minutes |
| 159 | Mismatch |
| 160 | Missing |
| 161 | Modem Change-out |
| 162 | Modem failed |
| 163 | Modem intialzed |
| 164 | MOL out of range |
| 165 | Momentary |
| 166 | Momentary events |
| 167 | New time |
| 168 | No modem |
| 169 | Node failed |
| 170 | Node link failed |
| 171 | Not initialized |
| 172 | Not Armed |
| 173 | NVRAM failure |
| 174 | Old time |
| 175 | On-demand |
| 176 | Option board error |
| 177 | Overflow |
| 178 | Overload |
| 179 | Parameter change |
| 180 | Partial success |
| 181 | Pending table activation |
| 182 | Pending table clear |
| 183 | Phase restored |
| 184 | Physical |
| 185 | Power out |
| 186 | PQ event ended |
| 187 | PQ event occurred |
| 188 | PQ event started |
| 189 | Prepayment change |
| 190 | Preset |
| 191 | Procedure invoked |
| 192 | Program changed |
| 193 | Program error |
| 194 | Pulse failure |
| 195 | Pushbutton pressed |
| 196 | Questionable |
| 197 | Queue |
| 198 | Radio failed |
| 199 | RAM failure |
| 200 | RAM full |
| 201 | Rate change |
| 202 | Read access |
| 203 | Read Missing |
| 204 | Read secure register |
| 205 | Read secure table |
| 206 | Recoder access |
| 207 | Recording disabled |
| 208 | Recording enabled |
| 209 | Register error |
| 210 | Register failed |
| 211 | Remote access |
| 212 | Removed |
| 213 | Reprogrammed |
| 214 | Reset |
| 215 | Reset error |
| 216 | Restored |
| 217 | Results pending |
| 218 | Returned within limit |
| 219 | Reverse rotation |
| 220 | ROM failure |
| 221 | RTP activated |
| 222 | RTP deactivated |
| 223 | Sag |
| 224 | Sag cleared |
| 225 | Scheduled |
| 226 | Scheduled change |
| 227 | Sealed |
| 228 | Season changed |
| 229 | Seconds |
| 230 | Security event |
| 231 | Self read |
| 232 | Self-test error |
| 233 | Sequence error |
| 234 | Session interrupted |
| 235 | Session too long |
| 236 | Set |
| 237 | Setup disabled |
| 238 | Setup enabled |
| 239 | Special schedule |
| 240 | Specific gravity |
| 241 | Standard time |
| 242 | Started |
| 243 | Stopped |
| 244 | Success |
| 245 | Survey failed |
| 246 | Sustained |
| 247 | Sustained events |
| 248 | Swell |
| 249 | Swell cleared |
| 250 | Synch disabled |
| 251 | Synch enabled |
| 252 | Synch failed |
| 253 | Synched |
| 254 | Synchronized |
| 255 | Table full |
| 256 | Table written |
| 257 | Tamper detected |
| 258 | Test button pushed |
| 259 | Test call |
| 260 | Test mode |
| 261 | Threshold |
| 262 | Tier changed |
| 263 | Tilt |
| 264 | Time changed |
| 265 | Total events |
| 266 | TOU Mismatch |
| 267 | Turbine pulse error |
| 268 | Unprogrammed |
| 269 | Unsealed |
| 270 | Unstable |
| 271 | Unsupported |
| 272 | Upgrade pending |
| 273 | Voltage A Inactive |
| 274 | Voltage B Inactive |
| 275 | Voltage C Inactive |
| 276 | Voltage loss |
| 277 | Volume calc error |
| 278 | Warm start |
| 279 | Watchdog failed |
| 280 | Watchdog Reset |
| 281 | Week rate change |
| 282 | Write access |
| 283 | Demand Limit evaluation time-period, formula # |
| 284 | Demand Limit exceeded, formula # |
| 285 | Demand Limit off-time, formula # |
| 286 | Demand Limit threshold, formula # |
| 287 | Demand Limit warning, formula # |
| 288 | Power limit |
| 289 | Power limit expiration time-perioid |

Numbered Values

Certain attributes require further specification of a particular channel number, alarm number, relay number, port number, formula number, etc.

These can be provided in the code as appropriate in a separate field.

Example EndDeviceEvent Codes

When the domain, domain part, type, and index fields are combined and presented as a single string, yet consists of four comma separated codes. Examples are presented in Table E.5.

# Table E.5 – Example EndDeviceEvent Codes

| End Device Event Code | Domain or Equipment | Domain Part | Type or Issue | Attribute | Meter/Headend Event Codes |
| --- | --- | --- | --- | --- | --- |
| 7.1.1.2. | Security | Access | Alarm | Access attempt | Unauthorized access attempted |
| 3.11.2.3.1 | Electric meter | Firmware | Alarm management | Acknowledged | Alarm acknowledged, alarm # 1 |
| 3.11.2.4.2 | Electric meter | Firmware | Alarm management | Activated | Alarm activated, alarm #2 |
| 3.11.2.4. | Electric meter | Firmware | Alarm management | Activated | Area alarm |
| 3.15.1.1. | Electric meter | Load control | Alarm | Abort | Switch schedule aborted |
| 2.2.1.17. | Device Asset | Battery | Alarm | Battery failure | Battery failed |
| 5.7.9.3.1 | Gateway | Customer interface | End alarm | Acknowledged | Customer alarm #1 end |
| 3.16.1.8. | Electric meter | Load profile | Alarm | Almost full | Load profile data area almost full |
| 3.18.1.7. | Electric meter | Memory | Alarm | Allocation error | Memory allocation error |
| 3.11.7.9. | Electric meter | Firmware | Configuration | Alter option | Alter option command executed |
| 3.18.1.8. | Electric meter | Memory | Alarm | Almost full | Disk almost full |
| 3.11.7.10. | Electric meter | Firmware | Configuration | Alternate phone | Alternate phone number used |
| 3.21.1.6. | Electric meter | Metrology | Alarm | Alarm cleared | kWh received – alarm cleared |
| 1.23.1.13. | Communications | Network Interface | Alarm | Association failure | Network association failure |
| 2.2.18.16. | Device Asset | Battery | Status check | Battery charged | Battery OK |
| 3.3.7.27. | Electric meter | Cartridge | Configuration | Change-out | Cartridge changed |
| 1.19.3.18. | Communications | Messaging | Attribute | Blank | Attribute blank |
| 1.23.1.20. | Communications | Network Interface | Alarm | Cable failed | Cut cable |
| 1.23.1.22. | Communications | Network Interface | Alarm | Call-in failure | Call-in failure |
| 3.34.8.5. | Electric meter | Tariff | Credit | Adjusted | Adjusted the remaining credit |
| 3.11.1.36. | Electric meter | Firmware | Alarm | Command error | Illegal command |
| 3.11.1.36. | Electric meter | Firmware | Alarm | Command error | Delayed command failure |
| 3.31.6.11. | Electric meter | RCD switch | Command | Armed for closure | Arm Remote Connect/Disconnect Switch |
| 3.21.4.24. | Electric meter | Metrology | Calibration | Changed | Calibration change |
| 3.21.1.28.1 | Electric meter | Metrology | Alarm | Cleared | Meter return within limits, channel #1 |
| 2.20.18.14. | Device Asset | Meter asset | Status Check | Auto registration | Auto registration status |
| 2.20.7.26. | Device Asset | Meter asset | Configuration | Changed ID | Meter hard ID changed |
| 2.20.18.15. | Device Asset | Meter asset | Status Check | Auto registration confirm | Auto registration confirmation |
| 2.20.7.27. | Device Asset | Meter asset | Configuration | Change-out | Meter change-out |
| 7.24.1.24. | Security | Password | Alarm | Changed | Password changed |
| 1.23.1.32. | Communications | Network Interface | Alarm | Comm failed | Communications failure |
| 4.13.1.39. | Gas meter | Gas metrology | Alarm | Concentration | Concentration alarm |
| 1.19.1.37. | Communications | Messaging | Alarm | Command format error | Command format error |
| 3.21.14.21. | Electric meter | Metrology | Quality Flag | Calculated | Measurement calculated |
| 6.6.1.47. | Grid power | Current | Alarm | Current loss | Loss of current |
| 3.11.7.40. | Electric meter | Firmware | Configuration | Configuration error | Configuration error |
| 3.15.18.25. | Electric meter | Load control | Status check | Changed by condition | Control point changed by condition |
| 5.7.1.48.1 | Gateway | Customer interface | Alarm | Customer alarm | Customer alarm #1 |
| 7.24.1.30. | Security | Password | Alarm | Code changed | Station code changed |
| 3.11.18.31. | Electric meter | Firmware | Status check | Cold start | Cold start |
| 3.16.1.43. | Electric meter | Load profile | Alarm | Corrupt data | Load profile data corrupt |
| 7.32.1.23. | Security | Security key | Alarm | Certificate expired | Certificate expiration alert |
| 3.11.1.52. | Electric meter | Firmware | Alarm | Data error | Unknown in analysis |
| 2.36.1.29. | Device Asset | Time | Alarm | Clock failed | Clock malfunction |
| 6.25.9.28. | Grid power | Phase | End alarm | Cleared | Phase alert cleared |
| 3.8.1.61. | Electric meter | Demand | Alarm | Demand reset | Demand reset detected |
| 4.13.1.55. | Gas meter | Gas metrology | Alarm | Day limit | Gas day high limit exceeded |
| 1.23.17.33. | Communications | Network Interface | Status | Comm reestablished | Communications re-established |
| 3.8.1.62. | Electric meter | Demand | Alarm | Demand reset fail | Unable to reset demand |
| 3.15.18.38. | Electric meter | Load control | Status check | Commanded change | Control point changed by command |
| 3.18.1.52. | Electric meter | Memory | Alarm | Data error | Data corruption detection |
| 3.8.6.57. | Electric meter | Demand | Command | Decreased | Demand Reduction Signal |
| 1.23.17.34. | Communications | Network Interface | Status | Comm terminated | Communication terminated normally |
| 5.14.7.49. | Gateway | Gateway device | Configuration | Customer configuration | Request customer configuration |
| 1.23.1.51. | Communications | Network Interface | Alarm | DAP failed | DAP error |
| 3.31.1.41. | Electric meter | RCD switch | Alarm | Connect failed | Connect failed |
| 3.31.18.24. | Electric meter | RCD switch | Status check | Changed | Status input change |
| 6.25.1.45. | Grid power | Phase | Alarm | Cross-phase | Cross phase condition |
| 3.8.6.61. | Electric meter | Demand | Command | Demand reset | Reset Demand |
| 3.33.1.44. | Electric meter | Tamper | Alarm | Cover removed | Cover removal detected |
| 3.11.2.66.5 | Electric meter | Firmware | Alarm management | Disabled | Alarm disabled, alarm #5 |
| 3.31.6.42. | Electric meter | RCD switch | Command | Connected | Close Remote Connect/Disconnect Switch |
| 2.10.1.70. | Device Asset | Enclosure | Alarm | Door closed | Door closed |
| 2.10.1.71. | Device Asset | Enclosure | Alarm | Door open | Door opened |
| 3.11.1.69. | Electric meter | Firmware | Alarm | Display error | Display failure |
| 3.3.1.79. | Electric meter | Cartridge | Alarm | Error | Cartridge error |
| 6.25.9.46. | Grid power | Phase | End alarm | Cross-phase cleared | Cross phase cleared |
| 2.9.18.63. | Device Asset | DER switch | Status check | DER connected | Optional input closure, generator |
| 3.11.2.76.2 | Electric meter | Firmware | Alarm management | Enabled | Alarm enabled, alarm #2 |
| 5.14.7.66. | Gateway | Gateway device | Configuration | Disabled | Gateway not enabled |
| 2.9.18.64. | Device Asset | DER switch | Status check | DER disconnected | Optional input opening, generator |
| 2.36.1.54. | Device Asset | Time | Alarm | Day change error | Day change error |
| 3.21.4.65.1 | Electric meter | Metrology | Calibration | Deviated | Calibration over-deviation, #1 |
| 3.31.18.42. | Electric meter | RCD switch | Status check | Connected | Service turn-on |
| 3.3.1.88. | Electric meter | Cartridge | Alarm | Frozen | Cartridge frozen |
| 3.21.14.58. | Electric meter | Metrology | Quality Flag | Default | Measurement default |
| 1.23.1.73. | Communications | Network Interface | Alarm | DSP failed | DSP error |
| 3.34.1.61. | Electric meter | Tariff | Alarm | Demand reset | Unscheduled billing reset |
| 3.31.6.59.1 | Electric meter | RCD switch | Command | Demand Limiting disabled, formula #1 | Disable Demand Limiting for RCD Switch |
| 3.18.1.78. | Electric meter | Memory | Alarm | EPROM failure | EPROM failure |
| 3.31.6.60.1 | Electric meter | RCD switch | Command | Demand Limiting enabled, formula #1 | Enable Demand Limiting for RCD Switch |
| 3.31.1.67. | Electric meter | RCD switch | Alarm | Disconnect failed | Disconnect failed |
| 3.34.8.57. | Electric meter | Tariff | Credit | Decreased | Subtracted from remaining credit |
| 4.13.1.84. | Gas meter | Gas metrology | Alarm | EWM failure | EWM potential failure |
| 3.34.16.50. | Electric meter | Tariff | Setting | Daily rate change | Daily tariff changed |
| 1.19.10.74. | Communications | Messaging | Identity | Duplicate | Duplicate name |
| 3.11.18.72. | Electric meter | Firmware | Status check | Download status | Firmware download status |
| 3.8.1.93. | Electric meter | Demand | Alarm | High limit | Demand threshold caution |
| 4.13.1.87. | Gas meter | Gas metrology | Alarm | FPV unreasonable | FPV calculated unreasonably |
| 2.20.10.74. | Device Asset | Meter asset | Identity | Duplicate | Duplicate device name |
| 2.20.10.74. | Device Asset | Meter asset | Identity | Duplicate | Multiple devices with serial number |
| 2.20.18.66. | Device Asset | Meter asset | Status check | Disabled | Device not enabled |
| 2.20.18.66. | Device Asset | Meter asset | Status check | Disabled | Parent device not enabled |
| 3.31.6.66. | Electric meter | RCD switch | Command | Disabled | Disable RCD Switch |
| 2.36.16.53. | Device Asset | Time | Setting | Date changed | Date setting changed |
| 4.13.1.89. | Gas meter | Gas metrology | Alarm | GC failure | GC analyzer failure |
| 6.6.1.94. | Grid power | Current | Alarm | High neutral current | High neutral current |
| 1.23.10.74. | Communications | Network Interface | Identity | Duplicate | Duplicate network interface ID |
| 3.18.1.86. | Electric meter | Memory | Alarm | Firmware failure | Firmware image corrupted |
| 3.31.6.68. | Electric meter | RCD switch | Command | Disconnected | Open Remote Connect/Disconnect Switch |
| 2.36.16.56. | Device Asset | Time | Setting | Daylight time | Change to Spring daylight savings time |
| 3.33.1.77. | Electric meter | Tamper | Alarm | Encoder | Encoder tamper |
| 3.34.18.61. | Electric meter | Tariff | Status check | Demand reset | Billing reset |
| 3.31.6.76. | Electric meter | RCD switch | Command | Enabled | Enable RCD Switch |
| 6.25.1.85. | Grid power | Phase | Alarm | Failed | Loss of voltage transducer on one phase |
| 6.25.1.85. | Grid power | Phase | Alarm | Failed | Loss of voltage per phase |
| 6.25.1.85. | Grid power | Phase | Alarm | Failed | Phase drop out |
| 2.17.18.81. | Device Asset | Logs | Status check | Event log cleared | Event log cleared |
| 3.21.1.93. | Electric meter | Metrology | Alarm | High limit | High limit alarm |
| 3.21.14.80. | Electric meter | Metrology | Quality Flag | Estimated | Measurement estimated |
| 2.17.18.82. | Device Asset | Logs | Status check | Event log updated | Event log last read entry updated |
| 2.17.18.83. | Device Asset | Logs | Status check | Event log uploaded | Event log uploaded |
| 3.31.18.68. | Electric meter | RCD switch | Status check | Disconnected | Service turn-off |
| 3.34.8.75. | Electric meter | Tariff | Credit | Emergency increase | Pre-payment emergency credit |
| 3.11.18.90. | Electric meter | Firmware | Status check | Health OK | Meter health checked |
| 6.28.1.91. | Grid power | Power quality | Alarm | High distortion | High distortion detected |
| 4.29.1.93. | Gas meter | Pressure | Alarm | High limit | Sensed pressure equals P max |
| 2.35.1.93. | Device Asset | Temperature | Alarm | High limit | Sensed temperature equals T max |
| 2.17.18.95. | Device Asset | Logs | Status check | History cleared | History log cleared |
| 2.17.18.96. | Device Asset | Logs | Status check | History updated | History log last read entry updated |
| 6.28.9.92. | Grid power | Power quality | End alarm | High distortion cleared | High distortion cleared |
| 6.38.1.93. | Grid power | Voltage | Alarm | High limit | High voltage |
| 2.36.16.97. | Device Asset | Time | Setting | Holiday | Holiday changed |
| 6.38.9.99. | Grid power | Voltage | End alarm | Imbalance cleared | Voltage imbalance cleared |
| 6.38.17.98. | Grid power | Voltage | Status | Imbalance | Voltage imbalance condition |
| 3.11.1.104. | Electric meter | Firmware | Alarm | Input error | Sensor malfunction |
| 3.11.1.106. | Electric meter | Firmware | Alarm | Invalid | Invalid down limit |
| 3.21.1.104.1 | Electric meter | Metrology | Alarm | Input error | Form C error, input #1 |
| 3.21.1.106. | Electric meter | Metrology | Alarm | Invalid | Measurement failed |
| 3.21.1.106. | Electric meter | Metrology | Alarm | Invalid | Measurement error detected |
| 1.19.1.111. | Communications | Messaging | Alarm | Invalid delete | Invalid delete data points |
| 6.25.1.100. | Grid power | Phase | Alarm | Inactive | Inactive phase condition |
| 5.14.1.113. | Gateway | Gateway device | Alarm | Invalid gateway ID | Invalid gateway ID |
| 7.24.1.106. | Security | Password | Alarm | Invalid | Invalid password |
| 1.19.1.118. | Communications | Messaging | Alarm | Invalid priority | Invalid priority not supported |
| 4.13.1.122. | Gas meter | Gas metrology | Alarm | Invalid sigmatic | Invalid sigmatic message |
| 2.36.1.110. | Device Asset | Time | Alarm | Invalid date | Invalid installation date |
| 2.36.1.110. | Device Asset | Time | Alarm | Invalid date | Invalid execution date and time |
| 2.36.1.110. | Device Asset | Time | Alarm | Invalid date | Invalid complete date and time range |
| 1.19.1.129. | Communications | Messaging | Alarm | Invalid XML | Invalid XML format |
| 2.2.1.149. | Device Asset | Battery | Alarm | Low battery detected | Battery low condition detected |
| 7.32.1.114. | Security | Security key | Alarm | Invalid key | Invalid security key |
| 1.23.1.130. | Communications | Network Interface | Alarm | IO mismatch | I/O board definition mismatch |
| 7.1.1.147. | Security | Access | Alarm | Login failed | User login failure |
| 3.21.1.134. | Electric meter | Metrology | Alarm | KYZ failure | KYZ alarm |
| 2.36.1.124. | Device Asset | Time | Alarm | Invalid time zone | Invalid time zone ID |
| 2.36.1.124. | Device Asset | Time | Alarm | Invalid time zone | Daylight savings or standard time variance error |
| 6.6.1.150. | Grid power | Current | Alarm | Low limit | Low current limit exceeded |
| 2.36.1.125. | Device Asset | Time | Alarm | Invalid timeout | Invalid timeout date and time |
| 3.21.1.139. | Electric meter | Metrology | Alarm | Limit exceeded | Meter over/under threshold |
| 3.21.1.139. | Electric meter | Metrology | Alarm | Limit exceeded | Limit alarm reported |
| 2.17.1.146. | Device Asset | Logs | Alarm | Log error | Event log error |
| 3.11.1.154. | Electric meter | Firmware | Alarm | Memory error | End of data event table reached |
| 3.11.1.155. | Electric meter | Firmware | Alarm | Message error | Unintelligible message received |
| 3.11.1.155. | Electric meter | Firmware | Alarm | Message error | Parameter error |
| 3.11.1.155. | Electric meter | Firmware | Alarm | Message error | Un-programmed caution |
| 3.8.1.159. | Electric meter | Demand | Alarm | Mismatch | Demand definitions mismatch |
| 6.25.1.139. | Grid power | Phase | Alarm | Limit exceeded | Phase angle limit exceeded |
| 6.27.1.137. | Grid power | Power factor | Alarm | Leading kvarh | Leading kvarh caution |
| 4.29.1.139. | Gas meter | Pressure | Alarm | Limit exceeded | Pressure is out of range |
| 6.27.1.139. | Grid power | Power factor | Alarm | Limit exceeded | Power factor exceeded limits |
| 3.21.1.150. | Electric meter | Metrology | Alarm | Low limit | Low limit alarm |
| 1.23.1.151. | Communications | Network Interface | Alarm | Low modem battery | Power outage modem battery low |
| 1.19.1.156. | Communications | Messaging | Alarm | Message failed | Message failure |
| 2.35.1.139. | Device Asset | Temperature | Alarm | Limit exceeded | Temperature is out of range |
| 2.36.1.139. | Device Asset | Time | Alarm | Limit exceeded | Time change > 10 seconds |
| 2.36.1.139. | Device Asset | Time | Alarm | Limit exceeded | Time variance exceeded limits even after module tries to correct it |
| 2.36.1.139. | Device Asset | Time | Alarm | Limit exceeded | Time variance exceeded limits without attempt to correct automatically |
| 1.19.1.159. | Communications | Messaging | Alarm | Mismatch | Communications mismatch |
| 3.18.1.159. | Electric meter | Memory | Alarm | Mismatch | Family definitions mismatch |
| 3.18.1.159. | Electric meter | Memory | Alarm | Mismatch | Mass memory mismatch |
| 1.23.1.157. | Communications | Network Interface | Alarm | Meter comm failed | Communications between modules within a meter lost |
| 4.13.1.164. | Gas meter | Gas metrology | Alarm | MOL out of range | Total MOL % out of range |
| 4.29.1.150. | Gas meter | Pressure | Alarm | Low limit | Sensed pressure equals P min |
| 6.38.1.139. | Grid power | Voltage | Alarm | Limit exceeded | Voltage exception |
| 1.23.1.162. | Communications | Network Interface | Alarm | Modem failed | Modem failure detected |
| 2.35.1.150. | Device Asset | Temperature | Alarm | Low limit | Sensed temperature equals T min |
| 3.33.1.152. | Electric meter | Tamper | Alarm | Magnetic | Magnetic switch alarm |
| 3.8.1.178. | Electric meter | Demand | Alarm | Overload | Demand overload threshold |
| 3.11.1.176. | Electric meter | Firmware | Alarm | Option board error | Option board error |
| 1.23.1.169. | Communications | Network Interface | Alarm | Node failed | Node failure |
| 1.23.1.170. | Communications | Network Interface | Alarm | Node link failed | Node link failure |
| 3.18.1.173. | Electric meter | Memory | Alarm | NVRAM failure | NVRAM failure |
| 6.38.1.150. | Grid power | Voltage | Alarm | Low limit | Low voltage |
| 3.18.1.177. | Electric meter | Memory | Alarm | Overflow | Buffer overflow/overrun error |
| 3.11.1.193. | Electric meter | Firmware | Alarm | Program error | Program malfunction |
| 3.11.1.193. | Electric meter | Firmware | Alarm | Program error | Illegal command processor state |
| 6.20.1.185. | Grid power | Meter asset | Alarm | Power out | Power outage |
| 3.26.1.185. | Electric meter | Power | Alarm | Power out | Undetected power outage |
| 3.3.1.212. | Electric meter | Cartridge | Alarm | Removed | Cartridge removed |
| 3.21.1.194. | Electric meter | Metrology | Alarm | Pulse failure | Pulse initiator |
| 3.18.1.199. | Electric meter | Memory | Alarm | RAM failure | RAM error |
| 3.33.1.184. | Electric meter | Tamper | Alarm | Physical | Physical tamper |
| 1.23.1.197. | Communications | Network Interface | Alarm | Queue | Queue alarm |
| 3.18.1.200. | Electric meter | Memory | Alarm | RAM full | RAM memory full |
| 6.28.1.187. | Grid power | Power quality | Alarm | PQ event occurred | Generic power quality event |
| 1.23.1.198. | Communications | Network Interface | Alarm | Radio failed | Radio faults |
| 6.28.1.188. | Grid power | Power quality | Alarm | PQ event started | Power quality event start |
| 3.11.1.209. | Electric meter | Firmware | Alarm | Register error | Register processor failure |
| 3.11.1.209. | Electric meter | Firmware | Alarm | Register error | Meter bus alarm |
| 3.21.1.203. | Electric meter | Metrology | Alarm | Read Missing | Expected read missed |
| 3.11.1.214. | Electric meter | Firmware | Alarm | Reset | Metering equipment reset |
| 3.11.1.214. | Electric meter | Firmware | Alarm | Reset | Processor reset |
| 6.37.1.185. | Grid power | Transformer device | Alarm | Power out | Transformer Outage |
| 3.11.1.215. | Electric meter | Firmware | Alarm | Reset error | Unable to reset |
| 3.31.1.195. | Electric meter | RCD switch | Alarm | Pushbutton pressed | RCD Switch pushbutton pressed |
| 3.21.1.209. | Electric meter | Metrology | Alarm | Register error | Register definitions mismatch |
| 3.21.1.209. | Electric meter | Metrology | Alarm | Register error | Register full |
| 3.21.1.209.1 | Electric meter | Metrology | Alarm | Register error | Pulse overflow, channel #1 |
| 3.21.1.209. | Electric meter | Metrology | Alarm | Register error | Register error |
| 1.23.1.210. | Communications | Network Interface | Alarm | Register failed | Intelligent register communication failure |
| 1.23.1.210. | Communications | Network Interface | Alarm | Register failed | Encoder register communication failure |
| 1.23.1.214. | Communications | Network Interface | Alarm | Reset | Reset alarm |
| 7.1.1.230. | Security | Access | Alarm | Security event | Security event |
| 3.18.1.220. | Electric meter | Memory | Alarm | ROM failure | ROM error |
| 6.20.1.216. | Grid power | Meter asset | Alarm | Restored | Meter Restoration |
| 3.11.1.232. | Electric meter | Firmware | Alarm | Self-test error | Diagnostic failure |
| 2.36.1.215. | Device Asset | Time | Alarm | Reset error | Unable to reset time |
| 1.19.1.234. | Communications | Messaging | Alarm | Session interrupted | Communication session interrupted |
| 1.19.1.235. | Communications | Messaging | Alarm | Session too long | Communication session too long |
| 3.33.1.219. | Electric meter | Tamper | Alarm | Reverse rotation | Reverse flow detected |
| 4.13.1.240. | Gas meter | Gas metrology | Alarm | Specific gravity | Specific gravity alarm |
| 6.37.1.216. | Grid power | Transformer device | Alarm | Restored | Transformer Restoration |
| 3.16.1.245. | Electric meter | Load profile | Alarm | Survey failed | Load survey readings failed |
| 6.25.1.233. | Grid power | Phase | Alarm | Sequence error | Phase sequence error |
| 3.18.1.255. | Electric meter | Memory | Alarm | Table full | Data table full |
| 9.5.1.267. | Turbine | Control | Alarm | Turbine pulse error | Turbine pulse error |
| 6.12.1.270. | Grid power | Frequency | Alarm | Unstable | Line frequency unstable |
| 2.36.1.252. | Device Asset | Time | Alarm | Synch failed | Time synchronization error |
| 3.33.1.257. | Electric meter | Tamper | Alarm | Tamper detected | Tamper indication |
| 4.13.1.277. | Gas meter | Gas metrology | Alarm | Volume calc error | Corrected volume calculation error |
| 3.33.1.263. | Electric meter | Tamper | Alarm | Tilt | Tilt detected |
| 1.23.1.279. | Communications | Network Interface | Alarm | Watchdog failed | Watch dog or keep-alive failure detected |
| 3.34.1.266. | Electric meter | Tariff | Alarm | TOU Mismatch | TOU start mismatch |
| 3.34.1.266. | Electric meter | Tariff | Alarm | TOU Mismatch | TOU mismatch |
| 3.34.1.266. | Electric meter | Tariff | Alarm | TOU Mismatch | TOU years mismatch |
| 6.38.1.276. | Grid power | Voltage | Alarm | Voltage loss | Loss of voltage transducer VT |
| 6.38.1.276. | Grid power | Voltage | Alarm | Voltage loss | Low loss potential detected |
| 3.11.2.236.2 | Electric meter | Firmware | Alarm management | Set | Alarm value set, alarm #2 |
| 1.19.3.108. | Communications | Messaging | Attribute | Invalid blank name | Invalid attribute defined value name blank |
| 1.19.3.112. | Communications | Messaging | Attribute | Invalid duplicate name | Invalid attribute defined value duplicate name |
| 1.19.3.115. | Communications | Messaging | Attribute | Invalid null | Invalid null parameter |
| 1.19.3.116. | Communications | Messaging | Attribute | Invalid numeric | Invalid numeric attribute |
| 1.19.3.126. | Communications | Messaging | Attribute | Invalid type | Invalid attribute type |
| 3.21.4.236.3 | Electric meter | Metrology | Calibration | Set | Calibration value set, #3 |
| 6.4.5.185. | Grid power | Circuit | Check Status | Power out | Verify Feeder Power |
| 6.20.5.185. | Grid power | Meter asset | Check Status | Power out | Verify Meter Power |
| 6.30.5.185. | Grid power | Protective device | Check Status | Power out | Verify Section Power |
| 6.37.5.185. | Grid power | Transformer device | Check Status | Power out | Verify Transformer Power |
| 3.34.6.201. | Electric meter | Tariff | Command | Rate change | Price Signal |
| 3.15.6.242. | Electric meter | Load control | Command | Started | Load control initiate |
| 3.15.6.243. | Electric meter | Load control | Command | Stopped | Load control restore |
| 3.3.7.105. | Electric meter | Cartridge | Configuration | Installed | Cartridge installed |
| 5.14.7.105. | Gateway | Gateway device | Configuration | Installed | Gateway installed |
| 2.20.7.105. | Device Asset | Meter asset | Configuration | Installed | Meter installed |
| 3.11.7.117. | Electric meter | Firmware | Configuration | Invalid parameter | Constants invalid |
| 3.11.7.117. | Electric meter | Firmware | Configuration | Invalid parameter | Invalid re-programming data |
| 3.11.7.128. | Electric meter | Firmware | Configuration | Invalid version | Internal device ID mismatch |
| 3.11.7.128. | Electric meter | Firmware | Configuration | Invalid version | Invalid meter software version |
| 3.11.7.159. | Electric meter | Firmware | Configuration | Mismatch | Miscellaneous configuration mismatch |
| 3.11.7.159. | Electric meter | Firmware | Configuration | Mismatch | Invalid device type, e.g. not TOU |
| 3.11.7.171. | Electric meter | Firmware | Configuration | Not initialized | Meter not programmed |
| 3.11.7.213. | Electric meter | Firmware | Configuration | Reprogrammed | Configuration written/changed |
| 3.11.7.213. | Electric meter | Firmware | Configuration | Reprogrammed | Reprogrammed |
| 3.11.7.213. | Electric meter | Firmware | Configuration | Reprogrammed | Meter reconfigured |
| 5.14.7.212. | Gateway | Gateway device | Configuration | Removed | Gateway removed |
| 5.14.7.213. | Gateway | Gateway device | Configuration | Reprogrammed | Gateway reprogrammed |
| 2.20.7.212. | Device Asset | Meter asset | Configuration | Removed | Meter removed |
| 2.20.7.227. | Device Asset | Meter asset | Configuration | Sealed | End device sealed |
| 3.11.7.237. | Electric meter | Firmware | Configuration | Setup disabled | Remote setup disabled |
| 3.11.7.238. | Electric meter | Firmware | Configuration | Setup enabled | Remote setup enabled |
| 3.11.7.250. | Electric meter | Firmware | Configuration | Synch disabled | Remote synch disabled |
| 3.11.7.251. | Electric meter | Firmware | Configuration | Synch enabled | Remote synch enabled |
| 3.11.7.253. | Electric meter | Firmware | Configuration | Synched | Device has been synchronized |
| 3.11.7.272. | Electric meter | Firmware | Configuration | Upgrade pending | Firmware update pending |
| 2.20.7.269. | Device Asset | Meter asset | Configuration | Unsealed | End device unsealed |
| 3.11.7.280. | Electric meter | Firmware | Configuration | Watchdog Reset | Last reset by watchdog |
| 3.34.8.102. | Electric meter | Tariff | Credit | Increased | Added to remaining credit |
| 6.25.9.101. | Grid power | Phase | End alarm | Inactive cleared | Inactive phase cleared |
| 6.27.9.138. | Grid power | Power factor | End alarm | Leading kvarh cleared | Leading kvarh cleared |
| 6.25.9.183. | Grid power | Phase | End alarm | Phase restored | Phase restoration |
| 6.28.9.186. | Grid power | Power quality | End alarm | PQ event ended | Power quality event end |
| 3.26.9.216. | Electric meter | Power | End alarm | Restored | Power on / restored |
| 2.35.9.218. | Device Asset | Temperature | End alarm | Returned within limit | Temperature returns within range |
| 6.38.9.224. | Grid power | Voltage | End alarm | Sag cleared | Voltage sag cleared |
| 6.38.9.249. | Grid power | Voltage | End alarm | Swell cleared | Voltage swell cleared |
| 1.19.10.107. | Communications | Messaging | Identity | Invalid attribute | Invalid attribute ID |
| 2.20.10.106. | Device Asset | Meter asset | Identity | Invalid | Invalid device ID |
| 2.20.10.106. | Device Asset | Meter asset | Identity | Invalid | Invalid serial number |
| 1.19.10.109. | Communications | Messaging | Identity | Invalid command | Invalid command ID |
| 1.19.10.119. | Communications | Messaging | Identity | Invalid return | Invalid information return type ID |
| 1.19.10.120. | Communications | Messaging | Identity | Invalid search | Invalid search ID |
| 1.23.10.121. | Communications | Network Interface | Identity | Invalid serial number | Invalid serial number for network interface |
| 1.19.10.127. | Communications | Messaging | Identity | Invalid value | Invalid defined value ID |
| 8.37.10.106. | Transformer | Transformer device | Identity | Invalid | Invalid transformer ID |
| 2.20.10.160. | Device Asset | Meter asset | Identity | Missing | Missing node |
| 2.20.10.271. | Device Asset | Meter asset | Identity | Unsupported | Unsupported device type ID |
| 3.22.11.242. | Electric meter | Mode | Maint mode | Started | Maintenance mode |
| 3.22.11.242. | Electric meter | Mode | Maint mode | Started | Meter shop mode started |
| 3.22.11.243. | Electric meter | Mode | Maint mode | Stopped | Meter shop mode stopped |
| 3.22.12.242. | Electric meter | Mode | Metering mode | Started | Begin recording meter readings |
| 3.22.12.243. | Electric meter | Mode | Metering mode | Stopped | Metering mode stopped |
| 3.26.13.158. | Electric meter | Power | Outage | Minutes | Outage minutes |
| 3.26.13.165. | Electric meter | Power | Outage | Momentary | Momentary Outage <5 Min |
| 3.26.13.166. | Electric meter | Power | Outage | Momentary events | Number of momentary outages |
| 3.26.13.229. | Electric meter | Power | Outage | Seconds | Outage seconds |
| 3.26.13.246. | Electric meter | Power | Outage | Sustained | Outage > 5 min |
| 3.26.13.247. | Electric meter | Power | Outage | Sustained events | Number of sustained outages |
| 3.26.13.265. | Electric meter | Power | Outage | Total events | Total Outages |
| 3.21.14.103. | Electric meter | Metrology | Quality Flag | Initial read | Measurement initial |
| 3.21.14.135. | Electric meter | Metrology | Quality Flag | Last read | Measurement last |
| 3.21.14.153. | Electric meter | Metrology | Quality Flag | Measured | Measurement measured |
| 3.21.14.190. | Electric meter | Metrology | Quality Flag | Preset | Pre-set register values |
| 3.21.14.196.0 | Electric meter | Metrology | Quality Flag | Questionable | No flow, channel #0 |
| 3.21.14.260. | Electric meter | Metrology | Quality Flag | Test mode | Test mode data |
| 3.21.15.175. | Electric meter | Metrology | Read Type | on-request | Meter readings passed |
| 3.21.15.175. | Electric meter | Metrology | Read Type | on-request | Verify read |
| 3.21.15.225. | Electric meter | Metrology | Read Type | Scheduled | Scheduled call-in |
| 3.21.15.231. | Electric meter | Metrology | Read Type | Self read | Self meter read |
| 2.36.16.167. | Device Asset | Time | Setting | New time | Time setting changed to new time |
| 2.36.16.167. | Device Asset | Time | Setting | New time | DST change to new time |
| 2.36.16.174. | Device Asset | Time | Setting | Old time | Time setting reset to previous time |
| 2.36.16.174. | Device Asset | Time | Setting | Old time | Time setting changed (old time) |
| 2.36.16.174. | Device Asset | Time | Setting | Old time | Working register time set to previous time |
| 2.36.16.174. | Device Asset | Time | Setting | Old time | DST change to previous time |
| 3.34.16.192. | Electric meter | Tariff | Setting | Program changed | Tariff program changed |
| 3.34.16.201. | Electric meter | Tariff | Setting | Rate change | Rate change |
| 6.28.16.207. | Grid power | Power quality | Setting | Recording disabled | Recording disabled |
| 6.28.16.208. | Grid power | Power quality | Setting | Recording enabled | Recording enabled |
| 2.36.16.228. | Device Asset | Time | Setting | Season changed | Season changed |
| 2.36.16.241. | Device Asset | Time | Setting | Standard time | Change to Fall standard time |
| 2.36.16.254. | Device Asset | Time | Setting | Synchronized | Time reset |
| 6.25.16.261. | Grid power | Phase | Setting | Threshold | Phase threshold |
| 3.34.16.262. | Electric meter | Tariff | Setting | Tier changed | Tier changed |
| 2.36.16.264. | Device Asset | Time | Setting | Time changed | Time setting changed |
| 3.34.16.281. | Electric meter | Tariff | Setting | Week rate change | Week tariff changed |
| 7.1.17.145. | Security | Access | Status | Local access | Unit accessed |
| 7.32.17.131. | Security | Security key | Status | Key disabled | Local key disable |
| 7.32.17.132. | Security | Security key | Status | Key enabled | Local key enable |
| 7.32.17.133. | Security | Security key | Status | Key unlocked | Local key unlock |
| 7.32.17.133. | Security | Security key | Status | Key unlocked | Local key enable/disable |
| 1.23.17.161. | Communications | Network Interface | Status | Modem Change-out | Modem change-out |
| 1.23.17.163. | Communications | Network Interface | Status | Modem intialzed | Modem initialized |
| 1.23.17.168. | Communications | Network Interface | Status | No modem | No modem |
| 1.19.17.180. | Communications | Messaging | Status | Partial success | Partial success |
| 7.1.17.202. | Security | Access | Status | Read access | Unit accessed by reader |
| 7.1.17.204. | Security | Access | Status | Read secure register | Read secured register |
| 7.1.17.205. | Security | Access | Status | Read secure table | Read secured table |
| 7.1.17.206. | Security | Access | Status | Recoder access | Unit accessed by recorder |
| 7.1.17.211. | Security | Access | Status | Remote access | Unit accessed remotely |
| 1.19.17.217. | Communications | Messaging | Status | Results pending | Results pending |
| 1.19.17.244. | Communications | Messaging | Status | Success | Succeeded |
| 6.38.17.223. | Grid power | Voltage | Status | Sag | Voltage sag |
| 7.1.17.282. | Security | Access | Status | Write access | End device accessed for write |
| 6.38.17.248. | Grid power | Voltage | Status | Swell | Voltage swell condition |
| 6.38.17.273. | Grid power | Voltage | Status | Voltage A Inactive | Potential A inactive |
| 6.38.17.274. | Grid power | Voltage | Status | Voltage B Inactive | Potential B inactive |
| 6.38.17.275. | Grid power | Voltage | Status | Voltage C Inactive | Potential C inactive |
| 3.21.18.136. | Electric meter | Metrology | Status check | Last read updated | Last read entry updated |
| 3.21.18.140. | Electric meter | Metrology | Status check | List cleared | List cleared |
| 3.21.18.141. | Electric meter | Metrology | Status check | List pointers reset | Reset list pointers |
| 3.21.18.142. | Electric meter | Metrology | Status check | List pointers updated | Update list pointers |
| 3.15.18.165. | Electric meter | Load control | Status check | Momentary | Load control relay momentary closure, relay # |
| 3.15.18.165. | Electric meter | Load control | Status check | Momentary | Output control relay toggled, relay # |
| 3.18.18.179. | Electric meter | Memory | Status check | Parameter change | EPROM read |
| 3.18.18.179. | Electric meter | Memory | Status check | Parameter change | EPROM written |
| 3.18.18.179. | Electric meter | Memory | Status check | Parameter change | Storage medium changed |
| 3.18.18.179. | Electric meter | Memory | Status check | Parameter change | Constants changed |
| 3.18.18.179. | Electric meter | Memory | Status check | Parameter change | Primary constant changed |
| 3.18.18.179. | Electric meter | Memory | Status check | Parameter change | Secondary constant changed |
| 3.18.18.179. | Electric meter | Memory | Status check | Parameter change | Output constant changed |
| 3.11.18.191. | Electric meter | Firmware | Status check | Procedure invoked | Meter procedure invoked |
| 3.21.18.181. | Electric meter | Metrology | Status check | Pending table activation | Pending table activation |
| 3.21.18.182. | Electric meter | Metrology | Status check | Pending table clear | Pending table clear |
| 3.15.18.189. | Electric meter | Load control | Status check | Prepayment change | Control point changed due to prepayment |
| 3.15.18.225. | Electric meter | Load control | Status check | Scheduled | Schedule loaded |
| 3.15.18.226. | Electric meter | Load control | Status check | Scheduled change | Control point changed by schedule |
| 3.34.18.221. | Electric meter | Tariff | Status check | RTP activated | RTP activation |
| 3.34.18.222. | Electric meter | Tariff | Status check | RTP deactivated | RTP deactivation |
| 3.15.18.242. | Electric meter | Load control | Status check | Started | Load control initiate |
| 3.15.18.243. | Electric meter | Load control | Status check | Stopped | Load control restore |
| 3.11.18.259. | Electric meter | Firmware | Status check | Test call | Test call-in |
| 3.34.18.239. | Electric meter | Tariff | Status check | Special schedule | Special schedule activation |
| 2.20.18.258. | Device Asset | Meter asset | Status check | Test button pushed | Test button pushed |
| 3.21.18.256. | Electric meter | Metrology | Status check | Table written | Table written to |
| 3.11.18.278. | Electric meter | Firmware | Status check | Warm start | Warm start |
| 3.22.19.242. | Electric meter | Mode | Test mode | Started | Test mode started |
| 3.22.19.243. | Electric meter | Mode | Test mode | Stopped | Test mode ended |

Example EndDeviceEvent Request codes

Just as the EndDeviceEvent codes offer an enumerated code that can be used in a publication or reply, Part 9 aslo supports the use of EndDeviceEvent codes as part of a request to solict EndDeviceEvent code data in the response. For a request-type query, the header should employ a suitable verb such as “GET”. Example codes are provided in Table E.6.

# Table E.6 – Example EndDeviceEvent Codes

| EndDeviceEvent Code | Domain or Equipment | DomainPart | Type or Issue | Attribute | Meter/Headend Event Codes |
| --- | --- | --- | --- | --- | --- |
| 6.4.5.185. | Grid power | Circuit | Status Check | Power out | Verify Feeder Power |
| 6.20.5.185. | Grid power | Meter asset | Status Check | Power out | Verify Meter Power |
| 6.30.5.185. | Grid power | Protective device | Status Check | Power out | Verify Section Power |
| 6.37.5.185. | Grid power | Transformer device | Status Check | Power out | Verify Transformer Power |
| 3.31.6.11. | Electric meter | RCD switch | Status Check | Armed for closure | Is RCD Armed? |
| 3.31.21.11. | Electric meter | RCD switch | Has feature | Armed for closure | Does the RCD support the “arm for closure” feature? |

(Informative)

Recommended EndDeviceControl Code Enumerations

General

Many Metering Systems have the capability to issue a command to equipment in the field that takes an action. The action might be to perform a demand-reset, open or close a switch, or a number of other activities. This annex describes example codes that may be used for such applications.

The recommended approach is to create EndDeviceEvent codes with that are of the “command” Type. While the response for the same condition is likely to be of an “alarm” type. For example compare the codes for “Demand Reset” in Table F.1, as well as the EndDeviceEvent command codes in Table E.6.

# Table F.1 – Comparison of example Demand Reset Codes

| Domain | DomainPart | Type | Attribute | Comment |
| --- | --- | --- | --- | --- |
| Electric meter | Demand | Alarm | Demand reset | Demand reset detected |
| Electric meter | Demand | Command | Demand reset | Reset Demand |

In addition to changing the “type” of code to a “command”, the requestor must also use a suitable verb in the CIM header such as “CREATE”. Within an XML message, the code is specified using the EndDeviceControl.type element.

Example EndDeviceControl Codes

Example codes, chosed from selected EndDeviceEvent status codes, are listed in Table F.2.

# Table F.2 – Example EndDevice Control Codes

| EndDeviceEvent Code | Domain or Equipment | DomainPart | Type or Issue | Attribute | Meter/Headend Event Codes |
| --- | --- | --- | --- | --- | --- |
| 3.8.6.57. | Electric meter | Demand | Command | Decreased | Demand Reduction Signal |
| 3.8.6.61. | Electric meter | Demand | Command | Demand reset | Reset Demand |
| 3.15.6.242.0 | Electric meter | Load control | Command | Started | Load control initiate, port 0 |
| 3.15.6.243.1 | Electric meter | Load control | Command | Stopped | Load control restore, port 1 |
| 3.31.6.11. | Electric meter | RCD switch | Command | Armed for closure | Arm Remote Connect/Disconnect Switch |
| 3.31.6.42. | Electric meter | RCD switch | Command | Connected | Close Remote Connect/Disconnect Switch |
| 3.31.6.59.1 | Electric meter | RCD switch | Command | Demand Limiting disabled, formula # | Disable Demand Limiting formula #1 for RCD Switch |
| 3.31.6.60.2 | Electric meter | RCD switch | Command | Demand Limiting enabled, formula # | Enable Demand Limiting formula #2 for RCD Switch |
| 3.31.6.66. | Electric meter | RCD switch | Command | Disabled | Disable RCD Switch |
| 3.31.6.68. | Electric meter | RCD switch | Command | Disconnected | Open Remote Connect/Disconnect Switch |
| 3.31.6.76. | Electric meter | RCD switch | Command | Enabled | Enable RCD Switch |
| 3.34.6.201. | Electric meter | Tariff | Command | Rate change | Price Signal |

(Informative)

Recommended procedure for maintaining relationships between objects

General

This annex describes an example of the use of 61968 based messages to maintain synchronization between a MDM system and a MS.

Object Identifiers

# Figure G.1 – Typical CIM Naming Object

Objects should be given a “name” by the system of record by using one of the naming elements. Figure G.1 shows a typical naming object which appears by extension in nearly every class. In some cases, the utility must identify which application they want to have serve as the system of record for given class. If a neutral ID service is available to broker a globally unique ID for the object, it enables use of the “mRID” attribute as the authoritative name. If such a service is not available, the “name” attribute will be used as the authoritative name, however it may be difficult to maintain context in some cases. For uniqueness when using the “name” attribute, it may be necessary to also populate the pathName attribute with the list of classes from the top to the named object (e.g. the xpath). The tradition is to name each class from the top to the bottom of the hierarchy, by listing them left to right, separating them by a slash “/”.

CIM based message exchanges

Initialization

The CIM can be used in very flexible ways. At some installations it may be the practice to send information from one application to another in piecemeal fashion to reflect the current development (in near-real-time) for every aspect of a deployment. Each time a message is transmitted the header can contain a timestamp which indicates when the update took place. Alternatively, some applications (especially MDM systems) tend to have a policy of packaging all of the related data together and sending it all at once to the MS. (The advantage to this approach is that the data consumer can easily check to see if all of the required data are present, and reject the data if it sees any problems.) Regardless of the approach used, it is important that data flow through the applications in the appropriate order. This way, the system of record can be allowed to name the object before it is disseminated.

The CIM header allows one verb to be applied to one noun. This simple arrangement works well to keep the interface understandable, and depending on the noun used, may cause each of the classes of data to be published in separate messages (e.g. meterAsset data is separated from customer data, which is separated from networkDataSets, etc.). The CustomerMeterDataSet message on the other hand allows all of the salient meter installation data to be presented in a single schema. When published, the data producer would say that a the item has been (verb=) CREATED.

Installation

If data is presented to the MS in piecemeal fashion prior to installation, then all that is needed upon installation is a message that ties the pieces together. The CustomerMeterDataSet message is good at this because it captures all of the salient information in a single schema. The CustomerMeterDataSet message can be populated with the name identifiers to indicate the relationship between the particular instances of a meter, customer, premises, etc. Alternatively, if the MDM has a policy of presenting all of the data at once, the CustomerMeterDataSet can be fully populated and presented as a full message.

Updates

General

When a data producer publishes an update, it would say that a particular noun has been CHANGED. Only the items that have changed should be included in the message. The data consumer can treat the naming identifier as an immutable key. All other data presented in the message should be considered “CHANGED”, and the relationships between named identifiers are also changeable.

Change of Tenancy

When a customer moves out of a premises, and a new customer has yet to move in, it is the practice of many utilities to either assign usage to an idle account (typically something like “99999”), or to a new non-existing account that will be assigned to the next tenant. In these cases the CHANGED verb would be an ideal choice. Some may prefer to use the DELETE verb. Such a choice could have ramifications within the system depending on its data retention policies. Some vendors may elect to not support the DELETE verb in certain contexts, and if they do support it, to not actually delete the data, but at most break the relationships between objects. Care should be taken in the use of the DELETE verb.

Example

Table G.1 describes a collection of information that might need to be passed from the MDM to the MS as a result of a meter installation. Certain pieces may be passed early, such as when a meter communication module is installed in a meter, the relation between the two has been established, and the initial configuration is known. This information can be passed through the systems prior to deployment of the new meter, or after installation – depending on the policy of the systems. Likewise, when a meter is removed from service and taken to the meter shop, the meter’s location should change. If the meter is disassembled, and the ComModule removed, the relationship between these two can be broken as well, and the assets assigned a new status and new locations.

# Table G.1 – Example meter relationships

| Description of Item | Value | CIM Location | Type |
| --- | --- | --- | --- |
| This communication module | MCM-ID | EndDeviceAsset.DeviceFunction.ComFunction.amrAddress | name/mRID |
| is servicing this end device | End-device ID | MeterAsset.name | name/mRID |
| (which is let’s say an electricity meter) | End-device type | ServiceDeliveryPoint.serviceType | Attribute |
| using this connection | Port Number | EndDeviceAsset.DeviceFunction.ComPort | Attribute |
|  | Upstream CommAsset | EndDeviceAsset.DeviceFunction. | name/mRID |
| at this location | ServiceDeliveryPoint | ServiceDeliveryPoint.name | name/mRID |
| for this account | Account ID | CustomerAccount.name | name/mRID |
| and this customer | Customer ID | CustomerAccount.Customer.name | name/mRID |
| In this utility | Business Unit |  |  |
| Commencing at this date | Installation date | ActivityRecord.statusDateTime | Attribute |
| Because | “In-Service” | ActivityRecord.status | Attribute |

Note that names (mRID’s) serve as immutable keys – ordinary attributes do not.

(Normative)

XML Schemas for Message Payloads

General

The purpose of this annex is to provide XML schemas for message payloads to augment the descriptions provided earlier in this document. These XML Schemas were defined using profile definitions within CIMTool. These schemas may be extended as needed for specific implementation needs.

CustomerMeterDataSet

<?xml version="1.0" encoding="UTF-8"?>

<xs:schema xmlns:xs="http://www.w3.org/2001/XMLSchema" xmlns:a="http://langdale.com.au/2005/Message#" xmlns:sawsdl="http://www.w3.org/ns/sawsdl" targetNamespace="http://iec.ch/TC57/2009/CustomerMeterDataSet#" elementFormDefault="qualified" attributeFormDefault="unqualified" xmlns="http://langdale.com.au/2005/Message#" xmlns:m="http://iec.ch/TC57/2009/CustomerMeterDataSet#">

<xs:element name="CustomerMeterDataSet" type="m:CustomerMeterDataSet"/>

<xs:complexType name="CustomerMeterDataSet">

<xs:sequence>

<xs:element name="Customer" type="m:Customer" minOccurs="0" maxOccurs="unbounded"/>

<xs:element name="CustomerAccount" type="m:CustomerAccount" minOccurs="0" maxOccurs="unbounded"/>

<xs:element name="CustomerAgreement" type="m:CustomerAgreement" minOccurs="0" maxOccurs="unbounded"/>

<xs:element name="EndDeviceAsset" type="m:EndDeviceAsset" minOccurs="0" maxOccurs="unbounded"/>

<xs:element name="SDPLocation" type="m:SDPLocation" minOccurs="0" maxOccurs="unbounded"/>

<xs:element name="ServiceCategory" type="m:ServiceCategory" minOccurs="0" maxOccurs="unbounded"/>

<xs:element name="ServiceDeliveryPoint" type="m:ServiceDeliveryPoint" minOccurs="0" maxOccurs="unbounded"/>

<xs:element name="ServiceLocation" type="m:ServiceLocation" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="Customer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Customer">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.description"/>

<xs:element name="kind" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Customer.kind">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#CustomerKind">

<xs:restriction base="xs:string">

<xs:enumeration value="commercialIndustrial"/>

<xs:enumeration value="energyServiceScheduler"/>

<xs:enumeration value="energyServiceSupplier"/>

<xs:enumeration value="internalUse"/>

<xs:enumeration value="other"/>

<xs:enumeration value="pumpingLoad"/>

<xs:enumeration value="residential"/>

<xs:enumeration value="residentialAndCommercial"/>

<xs:enumeration value="residentialAndStreetlight"/>

<xs:enumeration value="residentialFarmService"/>

<xs:enumeration value="residentialStreetlightOthers"/>

<xs:enumeration value="windMachine"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="name" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.name"/>

<xs:element name="pucNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Customer.pucNumber"/>

<xs:element name="specialNeed" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Customer.specialNeed"/>

<xs:element name="vip" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Customer.vip"/>

<xs:element name="CustomerAgreements" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Customer.CustomerAgreements">

<xs:complexType sawsdl:modelReference="">

<xs:attribute name="ref" type="xs:string"/>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:complexType name="CustomerAccount" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#CustomerAccount">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="billingCycle" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#CustomerAccount.billingCycle"/>

<xs:element name="budgetBill" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#CustomerAccount.budgetBill"/>

<xs:element name="name" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.name"/>

<xs:element name="CustomerAgreements" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#CustomerAccount.CustomerAgreements">

<xs:complexType sawsdl:modelReference="">

<xs:attribute name="ref" type="xs:string"/>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:complexType name="CustomerAgreement" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#CustomerAgreement">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.name"/>

<xs:element name="ServiceDeliveryPoints" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#CustomerAgreement.ServiceDeliveryPoints">

<xs:complexType sawsdl:modelReference="">

<xs:attribute name="ref" type="xs:string"/>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:complexType name="EndDeviceAsset" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="amrSystem" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset.amrSystem"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="SDPLocation" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#SDPLocation">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="accessMethod" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#SDPLocation.accessMethod"/>

<xs:element name="occupancyDate" minOccurs="0" maxOccurs="1" type="m:AbsoluteDate" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#SDPLocation.occupancyDate"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#SDPLocation.remark"/>

<xs:element name="siteAccessProblem" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#SDPLocation.siteAccessProblem"/>

<xs:element name="mainAddress" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Location.mainAddress">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetAddress">

<xs:sequence>

<xs:element name="status" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetAddress.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="streetDetail" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetAddress.streetDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail">

<xs:sequence>

<xs:element name="addressGeneral" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.addressGeneral"/>

<xs:element name="buildingName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.buildingName"/>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.code"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.name"/>

<xs:element name="number" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.number"/>

<xs:element name="prefix" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.prefix"/>

<xs:element name="suffix" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.suffix"/>

<xs:element name="suiteNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.suiteNumber"/>

<xs:element name="type" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.type"/>

<xs:element name="withinTownLimits" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.withinTownLimits"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="townDetail" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetAddress.townDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TownDetail">

<xs:sequence>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TownDetail.code"/>

<xs:element name="country" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TownDetail.country"/>

<xs:element name="name" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TownDetail.name"/>

<xs:element name="section" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TownDetail.section"/>

<xs:element name="stateOrProvince" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TownDetail.stateOrProvince"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:complexType name="ServiceCategory" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceCategory">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.description"/>

<xs:element name="kind" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceCategory.kind">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceKind">

<xs:restriction base="xs:string">

<xs:enumeration value="electricty"/>

<xs:enumeration value="gas"/>

<xs:enumeration value="heat"/>

<xs:enumeration value="internet"/>

<xs:enumeration value="other"/>

<xs:enumeration value="rates"/>

<xs:enumeration value="refuse"/>

<xs:enumeration value="sewerage"/>

<xs:enumeration value="time"/>

<xs:enumeration value="tvLicence"/>

<xs:enumeration value="water"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="ServiceDeliveryPoint" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="billingCycle" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.billingCycle"/>

<xs:element name="budgetBill" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.budgetBill"/>

<xs:element name="checkBilling" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.checkBilling"/>

<xs:element name="consumptionRealEnergy" minOccurs="0" maxOccurs="1" type="m:RealEnergy" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.consumptionRealEnergy"/>

<xs:element name="ctptReference" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.ctptReference"/>

<xs:element name="estimatedLoad" minOccurs="0" maxOccurs="1" type="m:CurrentFlow" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.estimatedLoad"/>

<xs:element name="grounded" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.grounded"/>

<xs:element name="loadMgmt" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.loadMgmt"/>

<xs:element name="nominalServiceVoltage" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.nominalServiceVoltage"/>

<xs:element name="phaseConfig" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.phaseConfig">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#PhaseConfigurationKind">

<xs:restriction base="xs:string">

<xs:enumeration value="onePhaseThreeWire"/>

<xs:enumeration value="onePhaseTwoWire"/>

<xs:enumeration value="other"/>

<xs:enumeration value="threePhaseFourWire"/>

<xs:enumeration value="threePhaseThreeWire"/>

<xs:enumeration value="threePhaseTwoWire"/>

<xs:enumeration value="twoPhaseThreeWire"/>

<xs:enumeration value="twoPhaseTwoWire"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="ratedCurrent" minOccurs="0" maxOccurs="1" type="m:CurrentFlow" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.ratedCurrent"/>

<xs:element name="ratedPower" minOccurs="0" maxOccurs="1" type="m:ActivePower" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.ratedPower"/>

<xs:element name="serviceDeliveryRemark" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.serviceDeliveryRemark"/>

<xs:element name="servicePriority" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.servicePriority"/>

<xs:element name="EndDeviceAssets" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.EndDeviceAssets">

<xs:complexType sawsdl:modelReference="">

<xs:attribute name="ref" type="xs:string"/>

</xs:complexType>

</xs:element>

<xs:element name="SDPLocations" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.SDPLocations">

<xs:complexType sawsdl:modelReference="">

<xs:attribute name="ref" type="xs:string"/>

</xs:complexType>

</xs:element>

<xs:element name="ServiceCategory" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.ServiceCategory">

<xs:complexType sawsdl:modelReference="">

<xs:attribute name="ref" type="xs:string"/>

</xs:complexType>

</xs:element>

<xs:element name="ServiceLocation" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.ServiceLocation">

<xs:complexType sawsdl:modelReference="">

<xs:attribute name="ref" type="xs:string"/>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:complexType name="ServiceLocation" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceLocation">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="accessMethod" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceLocation.accessMethod"/>

<xs:element name="needsInspection" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceLocation.needsInspection"/>

<xs:element name="siteAccessProblem" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceLocation.siteAccessProblem"/>

<xs:element name="mainAddress" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Location.mainAddress">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetAddress">

<xs:sequence>

<xs:element name="status" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetAddress.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="0" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="streetDetail" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetAddress.streetDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail">

<xs:sequence>

<xs:element name="addressGeneral" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.addressGeneral"/>

<xs:element name="buildingName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.buildingName"/>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.code"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.name"/>

<xs:element name="number" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.number"/>

<xs:element name="prefix" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.prefix"/>

<xs:element name="suffix" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.suffix"/>

<xs:element name="suiteNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.suiteNumber"/>

<xs:element name="type" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.type"/>

<xs:element name="withinTownLimits" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.withinTownLimits"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="townDetail" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetAddress.townDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TownDetail">

<xs:sequence>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TownDetail.code"/>

<xs:element name="country" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TownDetail.country"/>

<xs:element name="name" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TownDetail.name"/>

<xs:element name="section" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TownDetail.section"/>

<xs:element name="stateOrProvince" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TownDetail.stateOrProvince"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:simpleType name="AbsoluteDate" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AbsoluteDate">

<xs:restriction base="xs:string"/>

</xs:simpleType>

<xs:simpleType name="CurrentFlow" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#CurrentFlow">

<xs:restriction base="xs:float"/>

</xs:simpleType>

<xs:simpleType name="RealEnergy" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#RealEnergy">

<xs:restriction base="xs:float"/>

</xs:simpleType>

<xs:simpleType name="ActivePower" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivePower">

<xs:restriction base="xs:float"/>

</xs:simpleType>

</xs:schema>

MeterAssetReading

<?xml version="1.0" encoding="UTF-8"?>

<xs:schema xmlns:xs="http://www.w3.org/2001/XMLSchema" xmlns:a="http://langdale.com.au/2005/Message#" xmlns:sawsdl="http://www.w3.org/ns/sawsdl" targetNamespace="http://iec.ch/TC57/2009/MeterAssetReading#" elementFormDefault="qualified" attributeFormDefault="unqualified" xmlns="http://langdale.com.au/2005/Message#" xmlns:m="http://iec.ch/TC57/2009/MeterAssetReading#">

<xs:element name="MeterAssetReading" type="m:MeterAssetReading"/>

<xs:complexType name="MeterAssetReading">

<xs:sequence>

<xs:element name="MeterServiceWork" type="m:MeterServiceWork" minOccurs="0" maxOccurs="unbounded"/>

<xs:element name="ServiceLocation" type="m:ServiceLocation" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="MeterServiceWork" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterServiceWork">

<xs:sequence>

<xs:element name="kind" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Work.kind">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#WorkKind">

<xs:restriction base="xs:string">

<xs:enumeration value="construction"/>

<xs:enumeration value="disconnect"/>

<xs:enumeration value="inspection"/>

<xs:enumeration value="maintenance"/>

<xs:enumeration value="meter"/>

<xs:enumeration value="other"/>

<xs:enumeration value="reconnect"/>

<xs:enumeration value="service"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="priority" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Work.priority"/>

<xs:element name="requestDateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Work.requestDateTime"/>

<xs:element name="MeterAsset" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterServiceWork.MeterAsset">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterAsset">

<xs:sequence>

<xs:element name="mRID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="serialNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset.serialNumber"/>

<xs:element name="MeterReadings" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterAsset.MeterReadings">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterReading">

<xs:sequence>

<xs:element name="Readings" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterReading.Readings">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Reading">

<xs:sequence>

<xs:element name="timeStamp" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeasurementValue.timeStamp"/>

<xs:element name="value" minOccurs="0" maxOccurs="1" type="xs:float" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Reading.value"/>

<xs:element name="ReadingQualities" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Reading.ReadingQualities">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingQuality">

<xs:sequence>

<xs:element name="quality" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingQuality.quality"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="ReadingType" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Reading.ReadingType">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingType">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="status" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Document.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="0" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:complexType name="ServiceLocation" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceLocation">

<xs:sequence>

<xs:element name="mRID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="accessMethod" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceLocation.accessMethod"/>

<xs:element name="needsInspection" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceLocation.needsInspection"/>

<xs:element name="siteAccessProblem" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceLocation.siteAccessProblem"/>

<xs:element name="mainAddress" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Location.mainAddress">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetAddress">

<xs:sequence>

<xs:element name="streetDetail" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetAddress.streetDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail">

<xs:sequence>

<xs:element name="addressGeneral" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.addressGeneral"/>

<xs:element name="buildingName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.buildingName"/>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.code"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.name"/>

<xs:element name="number" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.number"/>

<xs:element name="prefix" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.prefix"/>

<xs:element name="suffix" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.suffix"/>

<xs:element name="suiteNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.suiteNumber"/>

<xs:element name="type" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.type"/>

<xs:element name="withinTownLimits" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.withinTownLimits"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="townDetail" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetAddress.townDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TownDetail">

<xs:sequence>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TownDetail.code"/>

<xs:element name="country" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TownDetail.country"/>

<xs:element name="name" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TownDetail.name"/>

<xs:element name="section" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TownDetail.section"/>

<xs:element name="stateOrProvince" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TownDetail.stateOrProvince"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:schema>

EndDeviceControls

<?xml version="1.0" encoding="UTF-8"?>

<xs:schema xmlns:xs="http://www.w3.org/2001/XMLSchema" xmlns:a="http://langdale.com.au/2005/Message#" xmlns:sawsdl="http://www.w3.org/ns/sawsdl" targetNamespace="http://iec.ch/TC57/2009/EndDeviceControls#" elementFormDefault="qualified" attributeFormDefault="unqualified" xmlns="http://langdale.com.au/2005/Message#" xmlns:m="http://iec.ch/TC57/2009/EndDeviceControls#">

<xs:element name="EndDeviceControls" type="m:EndDeviceControls"/>

<xs:complexType name="EndDeviceControls">

<xs:sequence>

<xs:element name="EndDeviceControl" type="m:EndDeviceControl" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="EndDeviceControl" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceControl">

<xs:sequence>

<xs:element name="mRID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.description"/>

<xs:element name="drProgramLevel" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceControl.drProgramLevel"/>

<xs:element name="drProgramMandatory" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceControl.drProgramMandatory"/>

<xs:element name="priceSignal" minOccurs="0" maxOccurs="1" type="m:FloatQuantity" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceControl.priceSignal"/>

<xs:element name="type" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceControl.type"/>

<xs:element name="DemandResponseProgram" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceControl.DemandResponseProgram">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#DemandResponseProgram">

<xs:sequence>

<xs:element name="mRID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.name"/>

<xs:element name="type" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#DemandResponseProgram.type"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="EndDeviceAsset" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceControl.EndDeviceAsset">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="EndDeviceGroup" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceControl.EndDeviceGroup">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceGroup">

<xs:sequence>

<xs:element name="mRID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="groupAddress" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceGroup.groupAddress"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="scheduledInterval" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceControl.scheduledInterval">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#DateTimeInterval">

<xs:sequence>

<xs:element name="end" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#DateTimeInterval.end"/>

<xs:element name="start" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#DateTimeInterval.start"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:simpleType name="FloatQuantity" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#FloatQuantity">

<xs:restriction base="xs:float"/>

</xs:simpleType>

</xs:schema>

EndDeviceEvents

<?xml version="1.0" encoding="UTF-8"?>

<xs:schema xmlns:xs="http://www.w3.org/2001/XMLSchema" xmlns:a="http://langdale.com.au/2005/Message#" xmlns:sawsdl="http://www.w3.org/ns/sawsdl" targetNamespace="http://iec.ch/TC57/2009/EndDeviceEvents#" elementFormDefault="qualified" attributeFormDefault="unqualified" xmlns="http://langdale.com.au/2005/Message#" xmlns:m="http://iec.ch/TC57/2009/EndDeviceEvents#">

<xs:element name="EndDeviceEvents" type="m:EndDeviceEvents"/>

<xs:complexType name="EndDeviceEvents">

<xs:sequence>

<xs:element name="EndDeviceEvent" type="m:EndDeviceEvent" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="EndDeviceEvent" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceEvent">

<xs:sequence>

<xs:element name="mRID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="category" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.category"/>

<xs:element name="createdDateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.createdDateTime"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.description"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.reason"/>

<xs:element name="severity" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.severity"/>

<xs:element name="userID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceEvent.userID"/>

<xs:element name="Assets" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.Assets">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="status" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="0" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.reason"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:schema>

MeterReadings

<?xml version="1.0" encoding="UTF-8"?>

<xs:schema xmlns:xs="http://www.w3.org/2001/XMLSchema" xmlns:a="http://langdale.com.au/2005/Message#" xmlns:sawsdl="http://www.w3.org/ns/sawsdl" targetNamespace="http://iec.ch/TC57/2009/MeterReadings#" elementFormDefault="qualified" attributeFormDefault="unqualified" xmlns="http://langdale.com.au/2005/Message#" xmlns:m="http://iec.ch/TC57/2009/MeterReadings#">

<xs:element name="MeterReadings" type="m:MeterReadings"/>

<xs:complexType name="MeterReadings">

<xs:sequence>

<xs:element name="MeterReading" type="m:MeterReading" minOccurs="0" maxOccurs="unbounded"/>

<xs:element name="ReadingType" type="m:ReadingType" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="EndDeviceEvent" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceEvent">

<xs:sequence>

<xs:element name="mRID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="category" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.category"/>

<xs:element name="createdDateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.createdDateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.reason"/>

<xs:element name="severity" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.severity"/>

<xs:element name="userID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceEvent.userID"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="MeterAsset" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterAsset">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="status" minOccurs="0" maxOccurs="1" type="m:Status" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset.status"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="MeterReading" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterReading">

<xs:sequence>

<xs:element name="CustomerAgreement" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterReading.CustomerAgreement">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#CustomerAgreement">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="EndDeviceEvents" minOccurs="0" maxOccurs="unbounded" type="m:EndDeviceEvent" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterReading.EndDeviceEvents"/>

<xs:element name="IntervalBlocks" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterReading.IntervalBlocks">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IntervalBlock">

<xs:sequence>

<xs:element name="IntervalReadings" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IntervalBlock.IntervalReadings">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IntervalReading">

<xs:sequence>

<xs:element name="timeStamp" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeasurementValue.timeStamp"/>

<xs:element name="value" minOccurs="0" maxOccurs="1" type="xs:float" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IntervalReading.value"/>

<xs:element name="ReadingQualities" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IntervalReading.ReadingQualities">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingQuality">

<xs:sequence>

<xs:element name="quality" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingQuality.quality"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="Pending" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IntervalBlock.Pending">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Pending">

<xs:sequence>

<xs:element name="multiplyBeforeAdd" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Pending.multiplyBeforeAdd"/>

<xs:element name="offset" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Pending.offset"/>

<xs:element name="scalarDenominator" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Pending.scalarDenominator"/>

<xs:element name="scalarFloat" minOccurs="0" maxOccurs="1" type="xs:float" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Pending.scalarFloat"/>

<xs:element name="scalarNumerator" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Pending.scalarNumerator"/>

<xs:element name="ReadingType" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Pending.ReadingType">

<xs:complexType sawsdl:modelReference="">

<xs:attribute name="ref" type="xs:string"/>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="ReadingType" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IntervalBlock.ReadingType">

<xs:complexType sawsdl:modelReference="">

<xs:attribute name="ref" type="xs:string"/>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="MeterAsset" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterReading.MeterAsset">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterAsset">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="status" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status">

<xs:sequence>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="Readings" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterReading.Readings">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Reading">

<xs:sequence>

<xs:element name="timeStamp" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeasurementValue.timeStamp"/>

<xs:element name="value" minOccurs="0" maxOccurs="1" type="xs:float" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Reading.value"/>

<xs:element name="ReadingQualities" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Reading.ReadingQualities">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingQuality">

<xs:sequence>

<xs:element name="quality" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingQuality.quality"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="ReadingType" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Reading.ReadingType">

<xs:complexType sawsdl:modelReference="">

<xs:attribute name="ref" type="xs:string"/>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="ServiceDeliveryPoint" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterReading.ServiceDeliveryPoint">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:complexType name="Pending" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Pending">

<xs:sequence>

<xs:element name="multiplyBeforeAdd" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Pending.multiplyBeforeAdd"/>

<xs:element name="offset" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Pending.offset"/>

<xs:element name="scalarDenominator" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Pending.scalarDenominator"/>

<xs:element name="scalarFloat" minOccurs="0" maxOccurs="1" type="xs:float" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Pending.scalarFloat"/>

<xs:element name="scalarNumerator" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Pending.scalarNumerator"/>

<xs:element name="ReadingType" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Pending.ReadingType">

<xs:complexType sawsdl:modelReference="">

<xs:attribute name="ref" type="xs:string"/>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:complexType name="ReadingQuality" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingQuality">

<xs:sequence>

<xs:element name="quality" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingQuality.quality"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="ReadingType" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingType">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.aliasName"/>

<xs:element name="channelNumber" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingType.channelNumber"/>

<xs:element name="defaultQuality" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingType.defaultQuality"/>

<xs:element name="defaultValueDataType" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingType.defaultValueDataType"/>

<xs:element name="dynamicConfiguration" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingType.dynamicConfiguration"/>

<xs:element name="intervalLength" minOccurs="0" maxOccurs="1" type="m:Seconds" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingType.intervalLength"/>

<xs:element name="kind" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingType.kind">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingKind">

<xs:restriction base="xs:string">

<xs:enumeration value="current"/>

<xs:enumeration value="currentAngle"/>

<xs:enumeration value="date"/>

<xs:enumeration value="demand"/>

<xs:enumeration value="energy"/>

<xs:enumeration value="other"/>

<xs:enumeration value="phaseAngle"/>

<xs:enumeration value="power"/>

<xs:enumeration value="powerFactor"/>

<xs:enumeration value="pressure"/>

<xs:enumeration value="time"/>

<xs:enumeration value="voltage"/>

<xs:enumeration value="voltageAngle"/>

<xs:enumeration value="volume"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="multiplier" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingType.multiplier">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#UnitMultiplier">

<xs:restriction base="xs:string">

<xs:enumeration value="G"/>

<xs:enumeration value="M"/>

<xs:enumeration value="T"/>

<xs:enumeration value="c"/>

<xs:enumeration value="d"/>

<xs:enumeration value="k"/>

<xs:enumeration value="m"/>

<xs:enumeration value="micro"/>

<xs:enumeration value="n"/>

<xs:enumeration value="none"/>

<xs:enumeration value="p"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="name" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.name"/>

<xs:element name="reverseChronology" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingType.reverseChronology"/>

<xs:element name="unit" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingType.unit">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#UnitSymbol">

<xs:restriction base="xs:string">

<xs:enumeration value="A"/>

<xs:enumeration value="F"/>

<xs:enumeration value="H"/>

<xs:enumeration value="Hz"/>

<xs:enumeration value="Hz-1"/>

<xs:enumeration value="J"/>

<xs:enumeration value="J/s"/>

<xs:enumeration value="N"/>

<xs:enumeration value="Pa"/>

<xs:enumeration value="S"/>

<xs:enumeration value="V"/>

<xs:enumeration value="V/VAr"/>

<xs:enumeration value="VA"/>

<xs:enumeration value="VAh"/>

<xs:enumeration value="VAr"/>

<xs:enumeration value="VArh"/>

<xs:enumeration value="W"/>

<xs:enumeration value="W/Hz"/>

<xs:enumeration value="W/s"/>

<xs:enumeration value="Wh"/>

<xs:enumeration value="deg"/>

<xs:enumeration value="g"/>

<xs:enumeration value="h"/>

<xs:enumeration value="kg/J"/>

<xs:enumeration value="m"/>

<xs:enumeration value="m2"/>

<xs:enumeration value="m3"/>

<xs:enumeration value="min"/>

<xs:enumeration value="none"/>

<xs:enumeration value="ohm"/>

<xs:enumeration value="rad"/>

<xs:enumeration value="s"/>

<xs:enumeration value="s-1"/>

<xs:enumeration value="ÂºC"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:complexType name="Status" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="0" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.reason"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.value"/>

</xs:sequence>

</xs:complexType>

<xs:simpleType name="Seconds" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Seconds">

<xs:restriction base="xs:float"/>

</xs:simpleType>

</xs:schema>

MeterReadSchedule

<?xml version="1.0" encoding="UTF-8"?>

<xs:schema xmlns:xs="http://www.w3.org/2001/XMLSchema" xmlns:a="http://langdale.com.au/2005/Message#" xmlns:sawsdl="http://www.w3.org/ns/sawsdl" targetNamespace="http://iec.ch/TC57/2009/MeterReadSchedule#" elementFormDefault="qualified" attributeFormDefault="unqualified" xmlns="http://langdale.com.au/2005/Message#" xmlns:m="http://iec.ch/TC57/2009/MeterReadSchedule#">

<xs:element name="MeterReadSchedule" type="m:MeterReadSchedule"/>

<xs:complexType name="MeterReadSchedule">

<xs:sequence>

<xs:element name="CustomerAccount" type="m:CustomerAccount" minOccurs="0" maxOccurs="unbounded"/>

<xs:element name="CustomerAgreement" type="m:CustomerAgreement" minOccurs="0" maxOccurs="unbounded"/>

<xs:element name="EndDeviceAsset" type="m:EndDeviceAsset" minOccurs="0" maxOccurs="unbounded"/>

<xs:element name="EndDeviceGroup" type="m:EndDeviceGroup" minOccurs="0" maxOccurs="unbounded"/>

<xs:element name="ReadingType" type="m:ReadingType" minOccurs="0" maxOccurs="unbounded"/>

<xs:element name="TimeSchedule" type="m:TimeSchedule" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="CustomerAccount" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#CustomerAccount">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="CustomerAgreement" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#CustomerAgreement">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="EndDeviceAsset" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="EndDeviceGroup" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceGroup">

<xs:sequence>

<xs:element name="groupAddress" minOccurs="1" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceGroup.groupAddress"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="ReadingType" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingType">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="TimeSchedule" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TimeSchedule">

<xs:sequence>

<xs:element name="disabled" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TimeSchedule.disabled"/>

<xs:element name="offset" minOccurs="0" maxOccurs="1" type="m:Seconds" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TimeSchedule.offset"/>

<xs:element name="recurrencePattern" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TimeSchedule.recurrencePattern"/>

<xs:element name="recurrencePeriod" minOccurs="0" maxOccurs="1" type="m:Seconds" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TimeSchedule.recurrencePeriod"/>

<xs:element name="scheduleInterval" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TimeSchedule.scheduleInterval">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#DateTimeInterval">

<xs:sequence>

<xs:element name="end" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#DateTimeInterval.end"/>

<xs:element name="start" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#DateTimeInterval.start"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="TimePoints" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TimeSchedule.TimePoints">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TimePoint">

<xs:sequence>

<xs:element name="absoluteTime" minOccurs="0" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TimePoint.absoluteTime"/>

<xs:element name="relativeTimeInterval" minOccurs="0" maxOccurs="1" type="m:Seconds" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TimePoint.relativeTimeInterval"/>

<xs:element name="sequenceNumber" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TimePoint.sequenceNumber"/>

<xs:element name="window" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TimePoint.window">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#DateTimeInterval">

<xs:sequence>

<xs:element name="end" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#DateTimeInterval.end"/>

<xs:element name="start" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#DateTimeInterval.start"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:simpleType name="Seconds" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Seconds">

<xs:restriction base="xs:float"/>

</xs:simpleType>

</xs:schema>

MeterServiceRequest

<?xml version="1.0" encoding="UTF-8"?>

<xs:schema xmlns:xs="http://www.w3.org/2001/XMLSchema" xmlns:a="http://langdale.com.au/2005/Message#" xmlns:sawsdl="http://www.w3.org/ns/sawsdl" targetNamespace="http://iec.ch/TC57/2009/MeterServiceRequests#" elementFormDefault="qualified" attributeFormDefault="unqualified" xmlns="http://langdale.com.au/2005/Message#" xmlns:m="http://iec.ch/TC57/2009/MeterServiceRequests#">

<xs:element name="MeterServiceRequests" type="m:MeterServiceRequests"/>

<xs:complexType name="MeterServiceRequests">

<xs:sequence>

<xs:element name="MeterServiceWork" type="m:MeterServiceWork" minOccurs="0" maxOccurs="unbounded"/>

<xs:element name="ReadingType" type="m:ReadingType" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="MeterAsset" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterAsset">

<xs:sequence>

<xs:element name="amrSystem" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset.amrSystem"/>

<xs:element name="formNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterAsset.formNumber"/>

<xs:element name="kH" minOccurs="0" maxOccurs="1" type="xs:float" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterAsset.kH"/>

<xs:element name="kR" minOccurs="0" maxOccurs="1" type="xs:float" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterAsset.kR"/>

<xs:element name="serialNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset.serialNumber"/>

<xs:element name="MeterReadings" minOccurs="0" maxOccurs="unbounded" type="m:MeterReading" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterAsset.MeterReadings"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="MeterReading" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterReading">

<xs:sequence>

<xs:element name="Readings" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterReading.Readings">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Reading">

<xs:sequence>

<xs:element name="timeStamp" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeasurementValue.timeStamp"/>

<xs:element name="value" minOccurs="0" maxOccurs="1" type="xs:float" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Reading.value"/>

<xs:element name="ReadingQualities" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Reading.ReadingQualities">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingQuality">

<xs:sequence>

<xs:element name="quality" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingQuality.quality"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="ReadingType" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Reading.ReadingType">

<xs:complexType sawsdl:modelReference="">

<xs:attribute name="ref" type="xs:string"/>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:complexType name="MeterServiceWork" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterServiceWork">

<xs:sequence>

<xs:element name="category" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Document.category"/>

<xs:element name="kind" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Work.kind">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#WorkKind">

<xs:restriction base="xs:string">

<xs:enumeration value="construction"/>

<xs:enumeration value="disconnect"/>

<xs:enumeration value="inspection"/>

<xs:enumeration value="maintenance"/>

<xs:enumeration value="meter"/>

<xs:enumeration value="other"/>

<xs:enumeration value="reconnect"/>

<xs:enumeration value="service"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="lastModifiedDateTime" minOccurs="0" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Document.lastModifiedDateTime"/>

<xs:element name="priority" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Work.priority"/>

<xs:element name="requestDateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Work.requestDateTime"/>

<xs:element name="ActivityRecords" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Document.ActivityRecords">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord">

<xs:sequence>

<xs:element name="category" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.category"/>

<xs:element name="createdDateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.createdDateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.reason"/>

<xs:element name="severity" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.severity"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="Customers" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Work.Customers">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Customer">

<xs:sequence>

<xs:element name="kind" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Customer.kind">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#CustomerKind">

<xs:restriction base="xs:string">

<xs:enumeration value="commercialIndustrial"/>

<xs:enumeration value="energyServiceScheduler"/>

<xs:enumeration value="energyServiceSupplier"/>

<xs:enumeration value="internalUse"/>

<xs:enumeration value="other"/>

<xs:enumeration value="pumpingLoad"/>

<xs:enumeration value="residential"/>

<xs:enumeration value="residentialAndCommercial"/>

<xs:enumeration value="residentialAndStreetlight"/>

<xs:enumeration value="residentialFarmService"/>

<xs:enumeration value="residentialStreetlightOthers"/>

<xs:enumeration value="windMachine"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="pucNumber" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Customer.pucNumber"/>

<xs:element name="specialNeed" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Customer.specialNeed"/>

<xs:element name="vip" minOccurs="1" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Customer.vip"/>

<xs:element name="CustomerAgreements" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Customer.CustomerAgreements">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#CustomerAgreement">

<xs:sequence>

<xs:element name="mRID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.name"/>

<xs:element name="ServiceDeliveryPoints" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#CustomerAgreement.ServiceDeliveryPoints">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint">

<xs:sequence>

<xs:element name="billingCycle" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.billingCycle"/>

<xs:element name="budgetBill" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.budgetBill"/>

<xs:element name="checkBilling" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.checkBilling"/>

<xs:element name="consumptionRealEnergy" minOccurs="0" maxOccurs="1" type="m:RealEnergy" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.consumptionRealEnergy"/>

<xs:element name="ctptReference" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.ctptReference"/>

<xs:element name="estimatedLoad" minOccurs="0" maxOccurs="1" type="m:CurrentFlow" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.estimatedLoad"/>

<xs:element name="grounded" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.grounded"/>

<xs:element name="loadMgmt" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.loadMgmt"/>

<xs:element name="nominalServiceVoltage" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.nominalServiceVoltage"/>

<xs:element name="phaseConfig" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.phaseConfig">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#PhaseConfigurationKind">

<xs:restriction base="xs:string">

<xs:enumeration value="onePhaseThreeWire"/>

<xs:enumeration value="onePhaseTwoWire"/>

<xs:enumeration value="other"/>

<xs:enumeration value="threePhaseFourWire"/>

<xs:enumeration value="threePhaseThreeWire"/>

<xs:enumeration value="threePhaseTwoWire"/>

<xs:enumeration value="twoPhaseThreeWire"/>

<xs:enumeration value="twoPhaseTwoWire"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="ratedCurrent" minOccurs="0" maxOccurs="1" type="m:CurrentFlow" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.ratedCurrent"/>

<xs:element name="ratedPower" minOccurs="0" maxOccurs="1" type="m:ActivePower" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.ratedPower"/>

<xs:element name="serviceDeliveryRemark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.serviceDeliveryRemark"/>

<xs:element name="servicePriority" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.servicePriority"/>

<xs:element name="ServiceLocation" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceDeliveryPoint.ServiceLocation">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceLocation">

<xs:sequence>

<xs:element name="accessMethod" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceLocation.accessMethod"/>

<xs:element name="needsInspection" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceLocation.needsInspection"/>

<xs:element name="siteAccessProblem" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ServiceLocation.siteAccessProblem"/>

<xs:element name="mainAddress" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Location.mainAddress">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetAddress">

<xs:sequence>

<xs:element name="streetDetail" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetAddress.streetDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail">

<xs:sequence>

<xs:element name="addressGeneral" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.addressGeneral"/>

<xs:element name="buildingName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.buildingName"/>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.code"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.name"/>

<xs:element name="number" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.number"/>

<xs:element name="prefix" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.prefix"/>

<xs:element name="suffix" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.suffix"/>

<xs:element name="suiteNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.suiteNumber"/>

<xs:element name="type" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.type"/>

<xs:element name="withinTownLimits" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetDetail.withinTownLimits"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="townDetail" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#StreetAddress.townDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TownDetail">

<xs:sequence>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TownDetail.code"/>

<xs:element name="country" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TownDetail.country"/>

<xs:element name="name" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TownDetail.name"/>

<xs:element name="section" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TownDetail.section"/>

<xs:element name="stateOrProvince" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#TownDetail.stateOrProvince"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="status" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Customer.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="0" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="MeterAsset" minOccurs="1" maxOccurs="1" type="m:MeterAsset" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterServiceWork.MeterAsset"/>

<xs:element name="OldMeterAsset" minOccurs="0" maxOccurs="1" type="m:MeterAsset" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterServiceWork.OldMeterAsset"/>

<xs:element name="status" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Document.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="0" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:complexType name="ReadingType" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingType">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="name" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.name"/>

<xs:element name="unit" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingType.unit">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#UnitSymbol">

<xs:restriction base="xs:string">

<xs:enumeration value="A"/>

<xs:enumeration value="F"/>

<xs:enumeration value="H"/>

<xs:enumeration value="Hz"/>

<xs:enumeration value="Hz-1"/>

<xs:enumeration value="J"/>

<xs:enumeration value="J/s"/>

<xs:enumeration value="N"/>

<xs:enumeration value="Pa"/>

<xs:enumeration value="S"/>

<xs:enumeration value="V"/>

<xs:enumeration value="V/VAr"/>

<xs:enumeration value="VA"/>

<xs:enumeration value="VAh"/>

<xs:enumeration value="VAr"/>

<xs:enumeration value="VArh"/>

<xs:enumeration value="W"/>

<xs:enumeration value="W/Hz"/>

<xs:enumeration value="W/s"/>

<xs:enumeration value="Wh"/>

<xs:enumeration value="deg"/>

<xs:enumeration value="g"/>

<xs:enumeration value="h"/>

<xs:enumeration value="kg/J"/>

<xs:enumeration value="m"/>

<xs:enumeration value="m2"/>

<xs:enumeration value="m3"/>

<xs:enumeration value="min"/>

<xs:enumeration value="none"/>

<xs:enumeration value="ohm"/>

<xs:enumeration value="rad"/>

<xs:enumeration value="s"/>

<xs:enumeration value="s-1"/>

<xs:enumeration value="ÂºC"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:simpleType name="CurrentFlow" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#CurrentFlow">

<xs:restriction base="xs:float"/>

</xs:simpleType>

<xs:simpleType name="RealEnergy" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#RealEnergy">

<xs:restriction base="xs:float"/>

</xs:simpleType>

<xs:simpleType name="ActivePower" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivePower">

<xs:restriction base="xs:float"/>

</xs:simpleType>

</xs:schema><?xml version="1.0" encoding="UTF-8"?>

MeterSystemEvent

<?xml version="1.0" encoding="UTF-8"?>

<xs:schema xmlns:xs="http://www.w3.org/2001/XMLSchema" xmlns:a="http://langdale.com.au/2005/Message#" xmlns:sawsdl="http://www.w3.org/ns/sawsdl" targetNamespace="http://iec.ch/TC57/2009/MeterSystemEvents#" elementFormDefault="qualified" attributeFormDefault="unqualified" xmlns="http://langdale.com.au/2005/Message#" xmlns:m="http://iec.ch/TC57/2009/MeterSystemEvents#">

<xs:element name="MeterSystemEvents" type="m:MeterSystemEvents"/>

<xs:complexType name="MeterSystemEvents">

<xs:sequence>

<xs:element name="ComMediaAsset" type="m:ComMediaAsset" minOccurs="0" maxOccurs="unbounded"/>

<xs:element name="EndDeviceAsset" type="m:EndDeviceAsset" minOccurs="0" maxOccurs="unbounded"/>

<xs:element name="EndDeviceEvent" type="m:EndDeviceEvent" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="ComMediaAsset" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ComMediaAsset">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="serialNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset.serialNumber"/>

<xs:element name="status" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="0" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:complexType name="EndDeviceAsset" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="amrSystem" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset.amrSystem"/>

<xs:element name="serialNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset.serialNumber"/>

<xs:element name="status" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="0" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:complexType name="EndDeviceEvent" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceEvent">

<xs:sequence>

<xs:element name="mRID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="category" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.category"/>

<xs:element name="createdDateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.createdDateTime"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.description"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.reason"/>

<xs:element name="severity" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.severity"/>

<xs:element name="userID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceEvent.userID"/>

<xs:element name="Assets" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.Assets">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="serialNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset.serialNumber"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="DeviceFunction" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceEvent.DeviceFunction">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#DeviceFunction">

<xs:sequence>

<xs:element name="configID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetFunction.configID"/>

<xs:element name="disabled" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#DeviceFunction.disabled"/>

<xs:element name="firmwareID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetFunction.firmwareID"/>

<xs:element name="hardwareID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetFunction.hardwareID"/>

<xs:element name="programID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetFunction.programID"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:schema>

EndDeviceAssets

<?xml version="1.0" encoding="UTF-8"?>

<xs:schema xmlns:xs="http://www.w3.org/2001/XMLSchema" xmlns:a="http://langdale.com.au/2005/Message#" xmlns:sawsdl="http://www.w3.org/ns/sawsdl" targetNamespace="http://iec.ch/TC57/2009/EndDeviceAssets#" elementFormDefault="qualified" attributeFormDefault="unqualified" xmlns="http://langdale.com.au/2005/Message#" xmlns:m="http://iec.ch/TC57/2009/EndDeviceAssets#">

<xs:element name="EndDeviceAssets" type="m:EndDeviceAssets"/>

<xs:complexType name="EndDeviceAssets">

<xs:sequence>

<xs:element name="ComFunction" type="m:ComFunction" minOccurs="0" maxOccurs="unbounded"/>

<xs:element name="ConnectDisconnectFunction" type="m:ConnectDisconnectFunction" minOccurs="0" maxOccurs="unbounded"/>

<xs:element name="ElectricMeteringFunction" type="m:ElectricMeteringFunction" minOccurs="0" maxOccurs="unbounded"/>

<xs:element name="EndDeviceAsset" type="m:EndDeviceAsset" minOccurs="0" maxOccurs="unbounded"/>

<xs:element name="ReadingType" type="m:ReadingType" minOccurs="0" maxOccurs="unbounded"/>

<xs:element name="Register" type="m:Register" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="ComFunction" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ComFunction">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="amrAddress" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ComFunction.amrAddress"/>

<xs:element name="amrRouter" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ComFunction.amrRouter"/>

<xs:element name="configID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetFunction.configID"/>

<xs:element name="firmwareID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetFunction.firmwareID"/>

<xs:element name="hardwareID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetFunction.hardwareID"/>

<xs:element name="password" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetFunction.password"/>

<xs:element name="programID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetFunction.programID"/>

<xs:element name="twoWay" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ComFunction.twoWay"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="ConnectDisconnectFunction" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ConnectDisconnectFunction">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="disabled" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#DeviceFunction.disabled"/>

<xs:element name="eventCount" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ConnectDisconnectFunction.eventCount"/>

<xs:element name="isConnected" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ConnectDisconnectFunction.isConnected"/>

<xs:element name="isDelayedDiscon" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ConnectDisconnectFunction.isDelayedDiscon"/>

<xs:element name="isLocalAutoDisconOp" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ConnectDisconnectFunction.isLocalAutoDisconOp"/>

<xs:element name="isLocalAutoReconOp" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ConnectDisconnectFunction.isLocalAutoReconOp"/>

<xs:element name="isRemoteAutoDisconOp" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ConnectDisconnectFunction.isRemoteAutoDisconOp"/>

<xs:element name="isRemoteAutoReconOp" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ConnectDisconnectFunction.isRemoteAutoReconOp"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.name"/>

<xs:element name="rcdInfo" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ConnectDisconnectFunction.rcdInfo">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#RemoteConnectDisconnectInfo">

<xs:sequence>

<xs:element name="armedTimeout" minOccurs="0" maxOccurs="1" type="m:Seconds" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#RemoteConnectDisconnectInfo.armedTimeout"/>

<xs:element name="customerVoltageLimit" minOccurs="0" maxOccurs="1" type="m:Voltage" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#RemoteConnectDisconnectInfo.customerVoltageLimit"/>

<xs:element name="energyLimit" minOccurs="0" maxOccurs="1" type="m:RealEnergy" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#RemoteConnectDisconnectInfo.energyLimit"/>

<xs:element name="energyUsageStartDateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#RemoteConnectDisconnectInfo.energyUsageStartDateTime"/>

<xs:element name="energyUsageWarning" minOccurs="0" maxOccurs="1" type="m:RealEnergy" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#RemoteConnectDisconnectInfo.energyUsageWarning"/>

<xs:element name="isArmConnect" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#RemoteConnectDisconnectInfo.isArmConnect"/>

<xs:element name="isArmDisconnect" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#RemoteConnectDisconnectInfo.isArmDisconnect"/>

<xs:element name="isEnergyLimiting" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#RemoteConnectDisconnectInfo.isEnergyLimiting"/>

<xs:element name="needsPowerLimitCheck" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#RemoteConnectDisconnectInfo.needsPowerLimitCheck"/>

<xs:element name="needsVoltageLimitCheck" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#RemoteConnectDisconnectInfo.needsVoltageLimitCheck"/>

<xs:element name="powerLimit" minOccurs="0" maxOccurs="1" type="m:ActivePower" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#RemoteConnectDisconnectInfo.powerLimit"/>

<xs:element name="usePushbutton" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#RemoteConnectDisconnectInfo.usePushbutton"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="Registers" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#DeviceFunction.Registers">

<xs:complexType sawsdl:modelReference="">

<xs:attribute name="ref" type="xs:string"/>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:complexType name="ElectricMeteringFunction" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricMeteringFunction">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="billingMultiplier" minOccurs="0" maxOccurs="1" type="xs:float" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricMeteringFunction.billingMultiplier"/>

<xs:element name="billingMultiplierApplied" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricMeteringFunction.billingMultiplierApplied"/>

<xs:element name="configID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetFunction.configID"/>

<xs:element name="currentRating" minOccurs="0" maxOccurs="1" type="m:CurrentFlow" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricMeteringFunction.currentRating"/>

<xs:element name="demandMultiplier" minOccurs="0" maxOccurs="1" type="xs:float" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricMeteringFunction.demandMultiplier"/>

<xs:element name="demandMultiplierApplied" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricMeteringFunction.demandMultiplierApplied"/>

<xs:element name="disabled" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#DeviceFunction.disabled"/>

<xs:element name="firmwareID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetFunction.firmwareID"/>

<xs:element name="hardwareID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetFunction.hardwareID"/>

<xs:element name="kWhMultiplier" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricMeteringFunction.kWhMultiplier"/>

<xs:element name="kWMultiplier" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricMeteringFunction.kWMultiplier"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.name"/>

<xs:element name="password" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetFunction.password"/>

<xs:element name="programID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetFunction.programID"/>

<xs:element name="transformerCTRatio" minOccurs="0" maxOccurs="1" type="xs:float" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricMeteringFunction.transformerCTRatio"/>

<xs:element name="transformerRatiosApplied" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricMeteringFunction.transformerRatiosApplied"/>

<xs:element name="transformerVTRatio" minOccurs="0" maxOccurs="1" type="xs:float" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricMeteringFunction.transformerVTRatio"/>

<xs:element name="voltageRating" minOccurs="0" maxOccurs="1" type="m:Voltage" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricMeteringFunction.voltageRating"/>

<xs:element name="Registers" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#DeviceFunction.Registers">

<xs:complexType sawsdl:modelReference="">

<xs:attribute name="ref" type="xs:string"/>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:complexType name="EndDeviceAsset" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="amrSystem" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset.amrSystem"/>

<xs:element name="category" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset.category"/>

<xs:element name="demandResponse" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset.demandResponse"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.description"/>

<xs:element name="disconnect" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset.disconnect"/>

<xs:element name="dstEnabled" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset.dstEnabled"/>

<xs:element name="formNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterAsset.formNumber"/>

<xs:element name="installationDate" minOccurs="0" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset.installationDate"/>

<xs:element name="kH" minOccurs="0" maxOccurs="1" type="xs:float" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterAsset.kH"/>

<xs:element name="kR" minOccurs="0" maxOccurs="1" type="xs:float" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#MeterAsset.kR"/>

<xs:element name="loadControl" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset.loadControl"/>

<xs:element name="lotNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset.lotNumber"/>

<xs:element name="manufacturedDate" minOccurs="0" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset.manufacturedDate"/>

<xs:element name="metrology" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset.metrology"/>

<xs:element name="outageReport" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset.outageReport"/>

<xs:element name="purchasePrice" minOccurs="0" maxOccurs="1" type="m:Money" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset.purchasePrice"/>

<xs:element name="readRequest" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset.readRequest"/>

<xs:element name="relayCapable" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset.relayCapable"/>

<xs:element name="reverseFlowHandling" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset.reverseFlowHandling"/>

<xs:element name="serialNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset.serialNumber"/>

<xs:element name="timeZoneOffset" minOccurs="0" maxOccurs="1" type="m:Minutes" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset.timeZoneOffset"/>

<xs:element name="ActivityRecords" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset.ActivityRecords">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord">

<xs:sequence>

<xs:element name="category" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.category"/>

<xs:element name="createdDateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.createdDateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.reason"/>

<xs:element name="severity" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.severity"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="Customer" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset.Customer">

<xs:complexType sawsdl:modelReference="">

<xs:attribute name="ref" type="xs:string"/>

</xs:complexType>

</xs:element>

<xs:choice minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset.DeviceFunctions">

<xs:element name="ComFunction" minOccurs="1" maxOccurs="1" sawsdl:modelReference="">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ComFunction">

<xs:attribute name="ref" type="xs:string"/>

</xs:complexType>

</xs:element>

<xs:element name="ConnectDisconnectFunction" minOccurs="1" maxOccurs="1" sawsdl:modelReference="">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ConnectDisconnectFunction">

<xs:attribute name="ref" type="xs:string"/>

</xs:complexType>

</xs:element>

<xs:element name="ElectricMeteringFunction" minOccurs="1" maxOccurs="1" sawsdl:modelReference="">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricMeteringFunction">

<xs:attribute name="ref" type="xs:string"/>

</xs:complexType>

</xs:element>

</xs:choice>

<xs:element name="ElectricalInfos" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset.ElectricalInfos">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricalInfo">

<xs:sequence>

<xs:element name="mRID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="b" minOccurs="0" maxOccurs="1" type="m:Susceptance" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricalInfo.b"/>

<xs:element name="b0" minOccurs="0" maxOccurs="1" type="m:Susceptance" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricalInfo.b0"/>

<xs:element name="bil" minOccurs="0" maxOccurs="1" type="m:Voltage" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricalInfo.bil"/>

<xs:element name="frequency" minOccurs="0" maxOccurs="1" type="m:Frequency" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricalInfo.frequency"/>

<xs:element name="g" minOccurs="0" maxOccurs="1" type="m:Conductance" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricalInfo.g"/>

<xs:element name="g0" minOccurs="0" maxOccurs="1" type="m:Conductance" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricalInfo.g0"/>

<xs:element name="phaseCount" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricalInfo.phaseCount"/>

<xs:element name="r" minOccurs="0" maxOccurs="1" type="m:Resistance" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricalInfo.r"/>

<xs:element name="r0" minOccurs="0" maxOccurs="1" type="m:Resistance" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricalInfo.r0"/>

<xs:element name="ratedApparentPower" minOccurs="0" maxOccurs="1" type="m:ApparentPower" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricalInfo.ratedApparentPower"/>

<xs:element name="ratedCurrent" minOccurs="0" maxOccurs="1" type="m:CurrentFlow" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricalInfo.ratedCurrent"/>

<xs:element name="ratedVoltage" minOccurs="0" maxOccurs="1" type="m:Voltage" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricalInfo.ratedVoltage"/>

<xs:element name="wireCount" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricalInfo.wireCount"/>

<xs:element name="x" minOccurs="0" maxOccurs="1" type="m:Reactance" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricalInfo.x"/>

<xs:element name="x0" minOccurs="0" maxOccurs="1" type="m:Reactance" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectricalInfo.x0"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="ElectronicAddresses" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset.ElectronicAddresses">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectronicAddress">

<xs:sequence>

<xs:element name="lan" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectronicAddress.lan"/>

<xs:element name="password" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectronicAddress.password"/>

<xs:element name="radio" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectronicAddress.radio"/>

<xs:element name="userID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ElectronicAddress.userID"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="EndDeviceGroups" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset.EndDeviceGroups">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceGroup">

<xs:sequence>

<xs:element name="groupAddress" minOccurs="1" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceGroup.groupAddress"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="EndDeviceModel" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset.EndDeviceModel">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceModel">

<xs:sequence>

<xs:element name="corporateStandardKind" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetModel.corporateStandardKind">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#CorporateStandardKind">

<xs:restriction base="xs:string">

<xs:enumeration value="experimental"/>

<xs:enumeration value="other"/>

<xs:enumeration value="standard"/>

<xs:enumeration value="underEvaluation"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="modelNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetModel.modelNumber"/>

<xs:element name="modelVersion" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetModel.modelVersion"/>

<xs:element name="usageKind" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetModel.usageKind">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetModelUsageKind">

<xs:restriction base="xs:string">

<xs:enumeration value="customerSubstation"/>

<xs:enumeration value="distributionOverhead"/>

<xs:enumeration value="distributionUnderground"/>

<xs:enumeration value="other"/>

<xs:enumeration value="streetlight"/>

<xs:enumeration value="substation"/>

<xs:enumeration value="transmission"/>

<xs:enumeration value="unknown"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="Seals" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetContainer.Seals">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Seal">

<xs:sequence>

<xs:element name="appliedDateTime" minOccurs="0" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Seal.appliedDateTime"/>

<xs:element name="condition" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Seal.condition">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#SealConditionKind">

<xs:restriction base="xs:string">

<xs:enumeration value="broken"/>

<xs:enumeration value="locked"/>

<xs:enumeration value="missing"/>

<xs:enumeration value="open"/>

<xs:enumeration value="other"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="kind" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Seal.kind">

<xs:complexType sawsdl:modelReference="">

<xs:attribute name="ref" type="xs:string"/>

</xs:complexType>

</xs:element>

<xs:element name="sealNumber" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Seal.sealNumber"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="ServiceLocation" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset.ServiceLocation">

<xs:complexType sawsdl:modelReference="">

<xs:attribute name="ref" type="xs:string"/>

</xs:complexType>

</xs:element>

<xs:element name="status" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="0" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.reason"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:complexType name="ReadingType" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingType">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.aliasName"/>

<xs:element name="channelNumber" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingType.channelNumber"/>

<xs:element name="defaultQuality" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingType.defaultQuality"/>

<xs:element name="defaultValueDataType" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingType.defaultValueDataType"/>

<xs:element name="dynamicConfiguration" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingType.dynamicConfiguration"/>

<xs:element name="intervalLength" minOccurs="0" maxOccurs="1" type="m:Seconds" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingType.intervalLength"/>

<xs:element name="kind" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingType.kind">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingKind">

<xs:restriction base="xs:string">

<xs:enumeration value="current"/>

<xs:enumeration value="currentAngle"/>

<xs:enumeration value="date"/>

<xs:enumeration value="demand"/>

<xs:enumeration value="energy"/>

<xs:enumeration value="other"/>

<xs:enumeration value="phaseAngle"/>

<xs:enumeration value="power"/>

<xs:enumeration value="powerFactor"/>

<xs:enumeration value="pressure"/>

<xs:enumeration value="time"/>

<xs:enumeration value="voltage"/>

<xs:enumeration value="voltageAngle"/>

<xs:enumeration value="volume"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="multiplier" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingType.multiplier">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#UnitMultiplier">

<xs:restriction base="xs:string">

<xs:enumeration value="G"/>

<xs:enumeration value="M"/>

<xs:enumeration value="T"/>

<xs:enumeration value="c"/>

<xs:enumeration value="d"/>

<xs:enumeration value="k"/>

<xs:enumeration value="m"/>

<xs:enumeration value="micro"/>

<xs:enumeration value="n"/>

<xs:enumeration value="none"/>

<xs:enumeration value="p"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.name"/>

<xs:element name="reverseChronology" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingType.reverseChronology"/>

<xs:element name="unit" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ReadingType.unit">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#UnitSymbol">

<xs:restriction base="xs:string">

<xs:enumeration value="A"/>

<xs:enumeration value="F"/>

<xs:enumeration value="H"/>

<xs:enumeration value="Hz"/>

<xs:enumeration value="Hz-1"/>

<xs:enumeration value="J"/>

<xs:enumeration value="J/s"/>

<xs:enumeration value="N"/>

<xs:enumeration value="Pa"/>

<xs:enumeration value="S"/>

<xs:enumeration value="V"/>

<xs:enumeration value="V/VAr"/>

<xs:enumeration value="VA"/>

<xs:enumeration value="VAh"/>

<xs:enumeration value="VAr"/>

<xs:enumeration value="VArh"/>

<xs:enumeration value="W"/>

<xs:enumeration value="W/Hz"/>

<xs:enumeration value="W/s"/>

<xs:enumeration value="Wh"/>

<xs:enumeration value="deg"/>

<xs:enumeration value="g"/>

<xs:enumeration value="h"/>

<xs:enumeration value="kg/J"/>

<xs:enumeration value="m"/>

<xs:enumeration value="m2"/>

<xs:enumeration value="m3"/>

<xs:enumeration value="min"/>

<xs:enumeration value="none"/>

<xs:enumeration value="ohm"/>

<xs:enumeration value="rad"/>

<xs:enumeration value="s"/>

<xs:enumeration value="s-1"/>

<xs:enumeration value="ÂºC"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:complexType name="Register" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Register">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="leftDigitCount" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Register.leftDigitCount"/>

<xs:element name="rightDigitCount" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Register.rightDigitCount"/>

<xs:element name="ReadingType" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Register.ReadingType">

<xs:complexType sawsdl:modelReference="">

<xs:attribute name="ref" type="xs:string"/>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:simpleType name="Conductance" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Conductance">

<xs:restriction base="xs:float"/>

</xs:simpleType>

<xs:simpleType name="ApparentPower" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ApparentPower">

<xs:restriction base="xs:float"/>

</xs:simpleType>

<xs:simpleType name="Money" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Money">

<xs:restriction base="xs:float"/>

</xs:simpleType>

<xs:simpleType name="Reactance" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Reactance">

<xs:restriction base="xs:float"/>

</xs:simpleType>

<xs:simpleType name="Frequency" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Frequency">

<xs:restriction base="xs:float"/>

</xs:simpleType>

<xs:simpleType name="Susceptance" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Susceptance">

<xs:restriction base="xs:float"/>

</xs:simpleType>

<xs:simpleType name="ActivePower" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivePower">

<xs:restriction base="xs:float"/>

</xs:simpleType>

<xs:simpleType name="Voltage" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Voltage">

<xs:restriction base="xs:float"/>

</xs:simpleType>

<xs:simpleType name="CurrentFlow" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#CurrentFlow">

<xs:restriction base="xs:float"/>

</xs:simpleType>

<xs:simpleType name="Resistance" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Resistance">

<xs:restriction base="xs:float"/>

</xs:simpleType>

<xs:simpleType name="Seconds" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Seconds">

<xs:restriction base="xs:float"/>

</xs:simpleType>

<xs:simpleType name="Minutes" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Minutes">

<xs:restriction base="xs:float"/>

</xs:simpleType>

<xs:simpleType name="RealEnergy" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#RealEnergy">

<xs:restriction base="xs:float"/>

</xs:simpleType>

</xs:schema>

EndDeviceFirmware

<?xml version="1.0" encoding="UTF-8"?>

<xs:schema xmlns:xs="http://www.w3.org/2001/XMLSchema" xmlns:a="http://langdale.com.au/2005/Message#" xmlns:sawsdl="http://www.w3.org/ns/sawsdl" targetNamespace="http://iec.ch/TC57/2009/EndDeviceFirmware#" elementFormDefault="qualified" attributeFormDefault="unqualified" xmlns="http://langdale.com.au/2005/Message#" xmlns:m="http://iec.ch/TC57/2009/EndDeviceFirmware#">

<xs:element name="EndDeviceFirmware" type="m:EndDeviceFirmware"/>

<xs:complexType name="EndDeviceFirmware">

<xs:sequence>

<xs:element name="EndDeviceAsset" type="m:EndDeviceAsset" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="EndDeviceAsset" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="amrSystem" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset.amrSystem"/>

<xs:element name="category" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset.category"/>

<xs:element name="serialNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset.serialNumber"/>

<xs:element name="ActivityRecords" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset.ActivityRecords">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord">

<xs:sequence>

<xs:element name="category" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.category"/>

<xs:element name="createdDateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.createdDateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.reason"/>

<xs:element name="severity" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.severity"/>

<xs:element name="status" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#ActivityRecord.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="0" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="DeviceFunctions" minOccurs="1" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#EndDeviceAsset.DeviceFunctions">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#DeviceFunction">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#IdentifiedObject.mRID"/>

<xs:element name="application" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset.application"/>

<xs:element name="category" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#Asset.category"/>

<xs:element name="configID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetFunction.configID"/>

<xs:element name="disabled" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#DeviceFunction.disabled"/>

<xs:element name="firmwareID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetFunction.firmwareID"/>

<xs:element name="hardwareID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetFunction.hardwareID"/>

<xs:element name="password" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetFunction.password"/>

<xs:element name="programID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/CIM-generic#AssetFunction.programID"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:schema>

SupplierConfig

<?xml version="1.0" encoding="UTF-8"?>

<xs:schema xmlns:xs="http://www.w3.org/2001/XMLSchema" xmlns:a="http://langdale.com.au/2005/Message#" xmlns:sawsdl="http://www.w3.org/ns/sawsdl" targetNamespace="http://iec.ch/TC57/2009/SupplierConfig#" elementFormDefault="qualified" attributeFormDefault="unqualified" xmlns="http://langdale.com.au/2005/Message#" xmlns:m="http://iec.ch/TC57/2009/SupplierConfig#">

<xs:element name="SupplierConfig" type="m:SupplierConfig"/>

<xs:complexType name="SupplierConfig">

<xs:sequence>

<xs:element name="ServiceSupplier" type="m:ServiceSupplier" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="ServiceSupplier" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceSupplier">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="issuerIdentificationNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceSupplier.issuerIdentificationNumber"/>

<xs:element name="kind" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceSupplier.kind">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#SupplierKind">

<xs:restriction base="xs:string">

<xs:enumeration value="other"/>

<xs:enumeration value="retailer"/>

<xs:enumeration value="utility"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="ElectronicAddresses" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#Organisation.ElectronicAddresses">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="email" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.email"/>

<xs:element name="lan" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.lan"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="password" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.password"/>

<xs:element name="radio" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.radio"/>

<xs:element name="userID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.userID"/>

<xs:element name="web" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.web"/>

<xs:element name="status" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="postalAddress" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Organisation.postalAddress">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#PostalAddress">

<xs:sequence>

<xs:element name="poBox" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#PostalAddress.poBox"/>

<xs:element name="postalCode" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#PostalAddress.postalCode"/>

<xs:element name="streetDetail" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#PostalAddress.streetDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail">

<xs:sequence>

<xs:element name="addressGeneral" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.addressGeneral"/>

<xs:element name="buildingName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.buildingName"/>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.code"/>

<xs:element name="name" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.name"/>

<xs:element name="number" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.number"/>

<xs:element name="prefix" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.prefix"/>

<xs:element name="suffix" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.suffix"/>

<xs:element name="suiteNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.suiteNumber"/>

<xs:element name="type" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.type"/>

<xs:element name="withinTownLimits" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.withinTownLimits"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="townDetail" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#PostalAddress.townDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail">

<xs:sequence>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.code"/>

<xs:element name="country" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.country"/>

<xs:element name="name" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.name"/>

<xs:element name="section" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.section"/>

<xs:element name="stateOrProvince" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.stateOrProvince"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="streetAddress" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Organisation.streetAddress">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#StreetAddress">

<xs:sequence>

<xs:element name="status" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetAddress.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="streetDetail" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetAddress.streetDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail">

<xs:sequence>

<xs:element name="addressGeneral" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.addressGeneral"/>

<xs:element name="buildingName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.buildingName"/>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.code"/>

<xs:element name="name" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.name"/>

<xs:element name="number" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.number"/>

<xs:element name="prefix" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.prefix"/>

<xs:element name="suffix" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.suffix"/>

<xs:element name="suiteNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.suiteNumber"/>

<xs:element name="type" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.type"/>

<xs:element name="withinTownLimits" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.withinTownLimits"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="townDetail" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetAddress.townDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail">

<xs:sequence>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.code"/>

<xs:element name="country" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.country"/>

<xs:element name="name" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.name"/>

<xs:element name="section" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.section"/>

<xs:element name="stateOrProvince" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.stateOrProvince"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="TelephoneNumbers" minOccurs="1" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#Organisation.TelephoneNumbers">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#TelephoneNumber">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="areaCode" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TelephoneNumber.areaCode"/>

<xs:element name="cityCode" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TelephoneNumber.cityCode"/>

<xs:element name="countryCode" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TelephoneNumber.countryCode"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="extension" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TelephoneNumber.extension"/>

<xs:element name="localNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TelephoneNumber.localNumber"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:schema>

CustomerConfig

<?xml version="1.0" encoding="UTF-8"?>

<xs:schema xmlns:xs="http://www.w3.org/2001/XMLSchema" xmlns:a="http://langdale.com.au/2005/Message#" xmlns:sawsdl="http://www.w3.org/ns/sawsdl" targetNamespace="http://iec.ch/TC57/2009/CustomerConfig#" elementFormDefault="qualified" attributeFormDefault="unqualified" xmlns="http://langdale.com.au/2005/Message#" xmlns:m="http://iec.ch/TC57/2009/CustomerConfig#">

<xs:element name="CustomerConfig" type="m:CustomerConfig"/>

<xs:complexType name="CustomerConfig">

<xs:sequence>

<xs:element name="Customer" type="m:Customer" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="Customer" sawsdl:modelReference="http://iec.ch/TC57/2009#Customer">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="kind" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Customer.kind">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#CustomerKind">

<xs:restriction base="xs:string">

<xs:enumeration value="commercialIndustrial"/>

<xs:enumeration value="energyServiceScheduler"/>

<xs:enumeration value="energyServiceSupplier"/>

<xs:enumeration value="internalUse"/>

<xs:enumeration value="other"/>

<xs:enumeration value="pumpingLoad"/>

<xs:enumeration value="residential"/>

<xs:enumeration value="residentialAndCommercial"/>

<xs:enumeration value="residentialAndStreetlight"/>

<xs:enumeration value="residentialFarmService"/>

<xs:enumeration value="residentialStreetlightOthers"/>

<xs:enumeration value="windMachine"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="pucNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Customer.pucNumber"/>

<xs:element name="specialNeed" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Customer.specialNeed"/>

<xs:element name="vip" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#Customer.vip"/>

<xs:element name="ElectronicAddresses" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#Organisation.ElectronicAddresses">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="email" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.email"/>

<xs:element name="lan" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.lan"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="password" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.password"/>

<xs:element name="radio" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.radio"/>

<xs:element name="userID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.userID"/>

<xs:element name="web" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.web"/>

<xs:element name="status" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="postalAddress" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Organisation.postalAddress">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#PostalAddress">

<xs:sequence>

<xs:element name="poBox" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#PostalAddress.poBox"/>

<xs:element name="postalCode" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#PostalAddress.postalCode"/>

<xs:element name="streetDetail" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#PostalAddress.streetDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail">

<xs:sequence>

<xs:element name="addressGeneral" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.addressGeneral"/>

<xs:element name="buildingName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.buildingName"/>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.code"/>

<xs:element name="name" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.name"/>

<xs:element name="number" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.number"/>

<xs:element name="prefix" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.prefix"/>

<xs:element name="suffix" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.suffix"/>

<xs:element name="suiteNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.suiteNumber"/>

<xs:element name="type" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.type"/>

<xs:element name="withinTownLimits" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.withinTownLimits"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="townDetail" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#PostalAddress.townDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail">

<xs:sequence>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.code"/>

<xs:element name="country" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.country"/>

<xs:element name="name" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.name"/>

<xs:element name="section" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.section"/>

<xs:element name="stateOrProvince" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.stateOrProvince"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="status" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Customer.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="streetAddress" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Organisation.streetAddress">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#StreetAddress">

<xs:sequence>

<xs:element name="status" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetAddress.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="streetDetail" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetAddress.streetDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail">

<xs:sequence>

<xs:element name="addressGeneral" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.addressGeneral"/>

<xs:element name="buildingName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.buildingName"/>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.code"/>

<xs:element name="name" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.name"/>

<xs:element name="number" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.number"/>

<xs:element name="prefix" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.prefix"/>

<xs:element name="suffix" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.suffix"/>

<xs:element name="suiteNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.suiteNumber"/>

<xs:element name="type" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.type"/>

<xs:element name="withinTownLimits" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.withinTownLimits"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="townDetail" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetAddress.townDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail">

<xs:sequence>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.code"/>

<xs:element name="country" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.country"/>

<xs:element name="name" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.name"/>

<xs:element name="section" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.section"/>

<xs:element name="stateOrProvince" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.stateOrProvince"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="TelephoneNumbers" minOccurs="1" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#Organisation.TelephoneNumbers">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#TelephoneNumber">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="areaCode" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TelephoneNumber.areaCode"/>

<xs:element name="cityCode" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TelephoneNumber.cityCode"/>

<xs:element name="countryCode" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TelephoneNumber.countryCode"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="extension" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TelephoneNumber.extension"/>

<xs:element name="localNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TelephoneNumber.localNumber"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:schema>

ServiceCategoryConfig

<?xml version="1.0" encoding="UTF-8"?>

<xs:schema xmlns:xs="http://www.w3.org/2001/XMLSchema" xmlns:a="http://langdale.com.au/2005/Message#" xmlns:sawsdl="http://www.w3.org/ns/sawsdl" targetNamespace="http://iec.ch/TC57/2009/ServiceCategoryConfig#" elementFormDefault="qualified" attributeFormDefault="unqualified" xmlns="http://langdale.com.au/2005/Message#" xmlns:m="http://iec.ch/TC57/2009/ServiceCategoryConfig#">

<xs:element name="ServiceCategoryConfig" type="m:ServiceCategoryConfig"/>

<xs:complexType name="ServiceCategoryConfig">

<xs:sequence>

<xs:element name="ServiceCategory" type="m:ServiceCategory" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="ServiceCategory" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceCategory">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="kind" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceCategory.kind">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceKind">

<xs:restriction base="xs:string">

<xs:enumeration value="electricty"/>

<xs:enumeration value="gas"/>

<xs:enumeration value="heat"/>

<xs:enumeration value="internet"/>

<xs:enumeration value="other"/>

<xs:enumeration value="rates"/>

<xs:enumeration value="refuse"/>

<xs:enumeration value="sewerage"/>

<xs:enumeration value="time"/>

<xs:enumeration value="tvLicence"/>

<xs:enumeration value="water"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:schema>

PricingStructureConfig

<?xml version="1.0" encoding="UTF-8"?>

<xs:schema xmlns:xs="http://www.w3.org/2001/XMLSchema" xmlns:a="http://langdale.com.au/2005/Message#" xmlns:sawsdl="http://www.w3.org/ns/sawsdl" targetNamespace="http://iec.ch/TC57/2009/PricingStructureConfig#" elementFormDefault="qualified" attributeFormDefault="unqualified" xmlns="http://langdale.com.au/2005/Message#" xmlns:m="http://iec.ch/TC57/2009/PricingStructureConfig#">

<xs:element name="PricingStructureConfig" type="m:PricingStructureConfig"/>

<xs:complexType name="PricingStructureConfig">

<xs:sequence>

<xs:element name="PricingStructure" type="m:PricingStructure" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="PricingStructure" sawsdl:modelReference="http://iec.ch/TC57/2009#PricingStructure">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="category" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.category"/>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#PricingStructure.code"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="revenueKind" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#PricingStructure.revenueKind">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#RevenueKind">

<xs:restriction base="xs:string">

<xs:enumeration value="commercial"/>

<xs:enumeration value="industrial"/>

<xs:enumeration value="irrigation"/>

<xs:enumeration value="nonResidential"/>

<xs:enumeration value="other"/>

<xs:enumeration value="residential"/>

<xs:enumeration value="streetLight"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="revisionNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.revisionNumber"/>

<xs:element name="title" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.title"/>

<xs:element name="docStatus" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.docStatus">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="ServiceCategory" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#PricingStructure.ServiceCategory">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceCategory">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="status" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="Tariffs" minOccurs="1" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#PricingStructure.Tariffs">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Tariff">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="category" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.category"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="endDate" minOccurs="1" maxOccurs="1" type="m:AbsoluteDate" sawsdl:modelReference="http://iec.ch/TC57/2009#Tariff.endDate"/>

<xs:element name="lastModifiedDateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.lastModifiedDateTime"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="revisionNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.revisionNumber"/>

<xs:element name="startDate" minOccurs="1" maxOccurs="1" type="m:AbsoluteDate" sawsdl:modelReference="http://iec.ch/TC57/2009#Tariff.startDate"/>

<xs:element name="title" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.title"/>

<xs:element name="docStatus" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.docStatus">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="status" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="TariffProfiles" minOccurs="1" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#Tariff.TariffProfiles">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#TariffProfile">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="category" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.category"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="lastModifiedDateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.lastModifiedDateTime"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="revisionNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.revisionNumber"/>

<xs:element name="tariffCycle" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TariffProfile.tariffCycle"/>

<xs:element name="title" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.title"/>

<xs:element name="ConsumptionTariffIntervals" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#TariffProfile.ConsumptionTariffIntervals">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#ConsumptionTariffInterval">

<xs:sequence>

<xs:element name="sequenceNumber" minOccurs="1" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/2009#ConsumptionTariffInterval.sequenceNumber"/>

<xs:element name="startValue" minOccurs="1" maxOccurs="1" type="m:RealEnergy" sawsdl:modelReference="http://iec.ch/TC57/2009#ConsumptionTariffInterval.startValue"/>

<xs:element name="Charges" minOccurs="1" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#ConsumptionTariffInterval.Charges">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Charge">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="kind" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Charge.kind">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#ChargeKind">

<xs:restriction base="xs:string">

<xs:enumeration value="auxiliaryCharge"/>

<xs:enumeration value="consumptionCharge"/>

<xs:enumeration value="demandCharge"/>

<xs:enumeration value="other"/>

<xs:enumeration value="taxCharge"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="variablePortion" minOccurs="1" maxOccurs="1" type="m:PerCent" sawsdl:modelReference="http://iec.ch/TC57/2009#Charge.variablePortion"/>

<xs:element name="ChildCharges" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#Charge.ChildCharges">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Charge">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="kind" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Charge.kind">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#ChargeKind">

<xs:restriction base="xs:string">

<xs:enumeration value="auxiliaryCharge"/>

<xs:enumeration value="consumptionCharge"/>

<xs:enumeration value="demandCharge"/>

<xs:enumeration value="other"/>

<xs:enumeration value="taxCharge"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="variablePortion" minOccurs="1" maxOccurs="1" type="m:PerCent" sawsdl:modelReference="http://iec.ch/TC57/2009#Charge.variablePortion"/>

<xs:element name="fixedPortion" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Charge.fixedPortion">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit">

<xs:sequence>

<xs:element name="energyUnit" minOccurs="0" maxOccurs="1" type="m:RealEnergy" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit.energyUnit"/>

<xs:element name="monetaryUnit" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit.monetaryUnit">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#Currency">

<xs:restriction base="xs:string">

<xs:enumeration value="AUD"/>

<xs:enumeration value="CAD"/>

<xs:enumeration value="CHF"/>

<xs:enumeration value="CNY"/>

<xs:enumeration value="DKK"/>

<xs:enumeration value="EUR"/>

<xs:enumeration value="GBP"/>

<xs:enumeration value="INR"/>

<xs:enumeration value="JPY"/>

<xs:enumeration value="NOK"/>

<xs:enumeration value="RUR"/>

<xs:enumeration value="SEK"/>

<xs:enumeration value="USD"/>

<xs:enumeration value="other"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="multiplier" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit.multiplier">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#UnitMultiplier">

<xs:restriction base="xs:string">

<xs:enumeration value="G"/>

<xs:enumeration value="M"/>

<xs:enumeration value="T"/>

<xs:enumeration value="c"/>

<xs:enumeration value="d"/>

<xs:enumeration value="k"/>

<xs:enumeration value="m"/>

<xs:enumeration value="micro"/>

<xs:enumeration value="n"/>

<xs:enumeration value="none"/>

<xs:enumeration value="p"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:float" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="fixedPortion" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Charge.fixedPortion">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit">

<xs:sequence>

<xs:element name="energyUnit" minOccurs="0" maxOccurs="1" type="m:RealEnergy" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit.energyUnit"/>

<xs:element name="monetaryUnit" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit.monetaryUnit">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#Currency">

<xs:restriction base="xs:string">

<xs:enumeration value="AUD"/>

<xs:enumeration value="CAD"/>

<xs:enumeration value="CHF"/>

<xs:enumeration value="CNY"/>

<xs:enumeration value="DKK"/>

<xs:enumeration value="EUR"/>

<xs:enumeration value="GBP"/>

<xs:enumeration value="INR"/>

<xs:enumeration value="JPY"/>

<xs:enumeration value="NOK"/>

<xs:enumeration value="RUR"/>

<xs:enumeration value="SEK"/>

<xs:enumeration value="USD"/>

<xs:enumeration value="other"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="multiplier" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit.multiplier">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#UnitMultiplier">

<xs:restriction base="xs:string">

<xs:enumeration value="G"/>

<xs:enumeration value="M"/>

<xs:enumeration value="T"/>

<xs:enumeration value="c"/>

<xs:enumeration value="d"/>

<xs:enumeration value="k"/>

<xs:enumeration value="m"/>

<xs:enumeration value="micro"/>

<xs:enumeration value="n"/>

<xs:enumeration value="none"/>

<xs:enumeration value="p"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:float" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="docStatus" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.docStatus">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="status" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="TimeTariffIntervals" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#TariffProfile.TimeTariffIntervals">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#TimeTariffInterval">

<xs:sequence>

<xs:element name="sequenceNumber" minOccurs="1" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/2009#TimeTariffInterval.sequenceNumber"/>

<xs:element name="startDateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#TimeTariffInterval.startDateTime"/>

<xs:element name="Charges" minOccurs="1" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#TimeTariffInterval.Charges">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Charge">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="kind" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Charge.kind">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#ChargeKind">

<xs:restriction base="xs:string">

<xs:enumeration value="auxiliaryCharge"/>

<xs:enumeration value="consumptionCharge"/>

<xs:enumeration value="demandCharge"/>

<xs:enumeration value="other"/>

<xs:enumeration value="taxCharge"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="variablePortion" minOccurs="1" maxOccurs="1" type="m:PerCent" sawsdl:modelReference="http://iec.ch/TC57/2009#Charge.variablePortion"/>

<xs:element name="ChildCharges" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#Charge.ChildCharges">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Charge">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="kind" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Charge.kind">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#ChargeKind">

<xs:restriction base="xs:string">

<xs:enumeration value="auxiliaryCharge"/>

<xs:enumeration value="consumptionCharge"/>

<xs:enumeration value="demandCharge"/>

<xs:enumeration value="other"/>

<xs:enumeration value="taxCharge"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="variablePortion" minOccurs="1" maxOccurs="1" type="m:PerCent" sawsdl:modelReference="http://iec.ch/TC57/2009#Charge.variablePortion"/>

<xs:element name="fixedPortion" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Charge.fixedPortion">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit">

<xs:sequence>

<xs:element name="energyUnit" minOccurs="0" maxOccurs="1" type="m:RealEnergy" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit.energyUnit"/>

<xs:element name="monetaryUnit" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit.monetaryUnit">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#Currency">

<xs:restriction base="xs:string">

<xs:enumeration value="AUD"/>

<xs:enumeration value="CAD"/>

<xs:enumeration value="CHF"/>

<xs:enumeration value="CNY"/>

<xs:enumeration value="DKK"/>

<xs:enumeration value="EUR"/>

<xs:enumeration value="GBP"/>

<xs:enumeration value="INR"/>

<xs:enumeration value="JPY"/>

<xs:enumeration value="NOK"/>

<xs:enumeration value="RUR"/>

<xs:enumeration value="SEK"/>

<xs:enumeration value="USD"/>

<xs:enumeration value="other"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="multiplier" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit.multiplier">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#UnitMultiplier">

<xs:restriction base="xs:string">

<xs:enumeration value="G"/>

<xs:enumeration value="M"/>

<xs:enumeration value="T"/>

<xs:enumeration value="c"/>

<xs:enumeration value="d"/>

<xs:enumeration value="k"/>

<xs:enumeration value="m"/>

<xs:enumeration value="micro"/>

<xs:enumeration value="n"/>

<xs:enumeration value="none"/>

<xs:enumeration value="p"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:float" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="fixedPortion" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Charge.fixedPortion">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit">

<xs:sequence>

<xs:element name="energyUnit" minOccurs="0" maxOccurs="1" type="m:RealEnergy" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit.energyUnit"/>

<xs:element name="monetaryUnit" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit.monetaryUnit">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#Currency">

<xs:restriction base="xs:string">

<xs:enumeration value="AUD"/>

<xs:enumeration value="CAD"/>

<xs:enumeration value="CHF"/>

<xs:enumeration value="CNY"/>

<xs:enumeration value="DKK"/>

<xs:enumeration value="EUR"/>

<xs:enumeration value="GBP"/>

<xs:enumeration value="INR"/>

<xs:enumeration value="JPY"/>

<xs:enumeration value="NOK"/>

<xs:enumeration value="RUR"/>

<xs:enumeration value="SEK"/>

<xs:enumeration value="USD"/>

<xs:enumeration value="other"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="multiplier" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit.multiplier">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#UnitMultiplier">

<xs:restriction base="xs:string">

<xs:enumeration value="G"/>

<xs:enumeration value="M"/>

<xs:enumeration value="T"/>

<xs:enumeration value="c"/>

<xs:enumeration value="d"/>

<xs:enumeration value="k"/>

<xs:enumeration value="m"/>

<xs:enumeration value="micro"/>

<xs:enumeration value="n"/>

<xs:enumeration value="none"/>

<xs:enumeration value="p"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:float" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:simpleType name="RealEnergy" sawsdl:modelReference="http://iec.ch/TC57/2009#RealEnergy">

<xs:restriction base="xs:float"/>

</xs:simpleType>

<xs:simpleType name="PerCent" sawsdl:modelReference="http://iec.ch/TC57/2009#PerCent">

<xs:restriction base="xs:float"/>

</xs:simpleType>

<xs:simpleType name="AbsoluteDate" sawsdl:modelReference="http://iec.ch/TC57/2009#AbsoluteDate">

<xs:restriction base="xs:string"/>

</xs:simpleType>

</xs:schema>

CustomerAccountConfig

<?xml version="1.0" encoding="UTF-8"?>

<xs:schema xmlns:xs="http://www.w3.org/2001/XMLSchema" xmlns:a="http://langdale.com.au/2005/Message#" xmlns:sawsdl="http://www.w3.org/ns/sawsdl" targetNamespace="http://iec.ch/TC57/2009/CustomerAccountConfig#" elementFormDefault="qualified" attributeFormDefault="unqualified" xmlns="http://langdale.com.au/2005/Message#" xmlns:m="http://iec.ch/TC57/2009/CustomerAccountConfig#">

<xs:element name="CustomerAccountConfig" type="m:CustomerAccountConfig"/>

<xs:complexType name="CustomerAccountConfig">

<xs:sequence>

<xs:element name="CustomerAccount" type="m:CustomerAccount" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="CustomerAccount" sawsdl:modelReference="http://iec.ch/TC57/2009#CustomerAccount">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="billingCycle" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#CustomerAccount.billingCycle"/>

<xs:element name="budgetBill" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#CustomerAccount.budgetBill"/>

<xs:element name="category" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.category"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="lastModifiedDateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.lastModifiedDateTime"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="title" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.title"/>

<xs:element name="docStatus" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.docStatus">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="status" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:schema>

CustomerAgreementConfig

<?xml version="1.0" encoding="UTF-8"?>

<xs:schema xmlns:xs="http://www.w3.org/2001/XMLSchema" xmlns:a="http://langdale.com.au/2005/Message#" xmlns:sawsdl="http://www.w3.org/ns/sawsdl" targetNamespace="http://iec.ch/TC57/2009/CustomerAgreementConfig#" elementFormDefault="qualified" attributeFormDefault="unqualified" xmlns="http://langdale.com.au/2005/Message#" xmlns:m="http://iec.ch/TC57/2009/CustomerAgreementConfig#">

<xs:element name="CustomerAgreementConfig" type="m:CustomerAgreementConfig"/>

<xs:complexType name="CustomerAgreementConfig">

<xs:sequence>

<xs:element name="CustomerAgreement" type="m:CustomerAgreement" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="CustomerAgreement" sawsdl:modelReference="http://iec.ch/TC57/2009#CustomerAgreement">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="category" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.category"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="lastModifiedDateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.lastModifiedDateTime"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="signDate" minOccurs="0" maxOccurs="1" type="m:AbsoluteDate" sawsdl:modelReference="http://iec.ch/TC57/2009#Agreement.signDate"/>

<xs:element name="title" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.title"/>

<xs:element name="Customer" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#CustomerAgreement.Customer">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Customer">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="CustomerAccount" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#CustomerAgreement.CustomerAccount">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#CustomerAccount">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="docStatus" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.docStatus">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="PricingStructures" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#CustomerAgreement.PricingStructures">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#PricingStructure">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="Tariffs" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#PricingStructure.Tariffs">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Tariff">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="TariffProfiles" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#Tariff.TariffProfiles">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#TariffProfile">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="ServiceSupplier" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#CustomerAgreement.ServiceSupplier">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceSupplier">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="status" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="validityInterval" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Agreement.validityInterval">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#DateTimeInterval">

<xs:sequence>

<xs:element name="end" minOccurs="0" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#DateTimeInterval.end"/>

<xs:element name="start" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#DateTimeInterval.start"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:simpleType name="AbsoluteDate" sawsdl:modelReference="http://iec.ch/TC57/2009#AbsoluteDate">

<xs:restriction base="xs:string"/>

</xs:simpleType>

</xs:schema>

AuxilaryAgreementConfig

<?xml version="1.0" encoding="UTF-8"?>

<xs:schema xmlns:xs="http://www.w3.org/2001/XMLSchema" xmlns:a="http://langdale.com.au/2005/Message#" xmlns:sawsdl="http://www.w3.org/ns/sawsdl" targetNamespace="http://iec.ch/TC57/2009/AuxiliaryAgreementConfig#" elementFormDefault="qualified" attributeFormDefault="unqualified" xmlns="http://langdale.com.au/2005/Message#" xmlns:m="http://iec.ch/TC57/2009/AuxiliaryAgreementConfig#">

<xs:element name="AuxiliaryAgreementConfig" type="m:AuxiliaryAgreementConfig"/>

<xs:complexType name="AuxiliaryAgreementConfig">

<xs:sequence>

<xs:element name="AuxiliaryAgreement" type="m:AuxiliaryAgreement" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="AuxiliaryAgreement" sawsdl:modelReference="http://iec.ch/TC57/2009#AuxiliaryAgreement">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="arrearsInterest" minOccurs="1" maxOccurs="1" type="m:PerCent" sawsdl:modelReference="http://iec.ch/TC57/2009#AuxiliaryAgreement.arrearsInterest"/>

<xs:element name="auxCycle" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#AuxiliaryAgreement.auxCycle"/>

<xs:element name="auxPriorityCode" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#AuxiliaryAgreement.auxPriorityCode"/>

<xs:element name="auxRef" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#AuxiliaryAgreement.auxRef"/>

<xs:element name="category" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.category"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="fixedAmount" minOccurs="1" maxOccurs="1" type="m:Money" sawsdl:modelReference="http://iec.ch/TC57/2009#AuxiliaryAgreement.fixedAmount"/>

<xs:element name="lastModifiedDateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.lastModifiedDateTime"/>

<xs:element name="minAmount" minOccurs="1" maxOccurs="1" type="m:Money" sawsdl:modelReference="http://iec.ch/TC57/2009#AuxiliaryAgreement.minAmount"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="payCycle" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#AuxiliaryAgreement.payCycle"/>

<xs:element name="signDate" minOccurs="0" maxOccurs="1" type="m:AbsoluteDate" sawsdl:modelReference="http://iec.ch/TC57/2009#Agreement.signDate"/>

<xs:element name="subCategory" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#AuxiliaryAgreement.subCategory"/>

<xs:element name="title" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.title"/>

<xs:element name="vendPortion" minOccurs="1" maxOccurs="1" type="m:PerCent" sawsdl:modelReference="http://iec.ch/TC57/2009#AuxiliaryAgreement.vendPortion"/>

<xs:element name="vendPortionArrear" minOccurs="1" maxOccurs="1" type="m:PerCent" sawsdl:modelReference="http://iec.ch/TC57/2009#AuxiliaryAgreement.vendPortionArrear"/>

<xs:element name="AuxiliaryAccounts" minOccurs="1" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#AuxiliaryAgreement.AuxiliaryAccounts">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#AuxiliaryAccount">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="balance" minOccurs="1" maxOccurs="1" type="m:Money" sawsdl:modelReference="http://iec.ch/TC57/2009#AuxiliaryAccount.balance"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="principleAmount" minOccurs="1" maxOccurs="1" type="m:Money" sawsdl:modelReference="http://iec.ch/TC57/2009#AuxiliaryAccount.principleAmount"/>

<xs:element name="title" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.title"/>

<xs:element name="Charges" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#AuxiliaryAccount.Charges">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Charge">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="kind" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Charge.kind">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#ChargeKind">

<xs:restriction base="xs:string">

<xs:enumeration value="auxiliaryCharge"/>

<xs:enumeration value="consumptionCharge"/>

<xs:enumeration value="demandCharge"/>

<xs:enumeration value="other"/>

<xs:enumeration value="taxCharge"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="variablePortion" minOccurs="1" maxOccurs="1" type="m:PerCent" sawsdl:modelReference="http://iec.ch/TC57/2009#Charge.variablePortion"/>

<xs:element name="ChildCharges" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#Charge.ChildCharges">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Charge">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="kind" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Charge.kind">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#ChargeKind">

<xs:restriction base="xs:string">

<xs:enumeration value="auxiliaryCharge"/>

<xs:enumeration value="consumptionCharge"/>

<xs:enumeration value="demandCharge"/>

<xs:enumeration value="other"/>

<xs:enumeration value="taxCharge"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="variablePortion" minOccurs="1" maxOccurs="1" type="m:PerCent" sawsdl:modelReference="http://iec.ch/TC57/2009#Charge.variablePortion"/>

<xs:element name="fixedPortion" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Charge.fixedPortion">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit">

<xs:sequence>

<xs:element name="energyUnit" minOccurs="0" maxOccurs="1" type="m:RealEnergy" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit.energyUnit"/>

<xs:element name="monetaryUnit" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit.monetaryUnit">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#Currency">

<xs:restriction base="xs:string">

<xs:enumeration value="AUD"/>

<xs:enumeration value="CAD"/>

<xs:enumeration value="CHF"/>

<xs:enumeration value="CNY"/>

<xs:enumeration value="DKK"/>

<xs:enumeration value="EUR"/>

<xs:enumeration value="GBP"/>

<xs:enumeration value="INR"/>

<xs:enumeration value="JPY"/>

<xs:enumeration value="NOK"/>

<xs:enumeration value="RUR"/>

<xs:enumeration value="SEK"/>

<xs:enumeration value="USD"/>

<xs:enumeration value="other"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="multiplier" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit.multiplier">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#UnitMultiplier">

<xs:restriction base="xs:string">

<xs:enumeration value="G"/>

<xs:enumeration value="M"/>

<xs:enumeration value="T"/>

<xs:enumeration value="c"/>

<xs:enumeration value="d"/>

<xs:enumeration value="k"/>

<xs:enumeration value="m"/>

<xs:enumeration value="micro"/>

<xs:enumeration value="n"/>

<xs:enumeration value="none"/>

<xs:enumeration value="p"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:float" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="fixedPortion" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Charge.fixedPortion">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit">

<xs:sequence>

<xs:element name="energyUnit" minOccurs="0" maxOccurs="1" type="m:RealEnergy" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit.energyUnit"/>

<xs:element name="monetaryUnit" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit.monetaryUnit">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#Currency">

<xs:restriction base="xs:string">

<xs:enumeration value="AUD"/>

<xs:enumeration value="CAD"/>

<xs:enumeration value="CHF"/>

<xs:enumeration value="CNY"/>

<xs:enumeration value="DKK"/>

<xs:enumeration value="EUR"/>

<xs:enumeration value="GBP"/>

<xs:enumeration value="INR"/>

<xs:enumeration value="JPY"/>

<xs:enumeration value="NOK"/>

<xs:enumeration value="RUR"/>

<xs:enumeration value="SEK"/>

<xs:enumeration value="USD"/>

<xs:enumeration value="other"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="multiplier" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit.multiplier">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#UnitMultiplier">

<xs:restriction base="xs:string">

<xs:enumeration value="G"/>

<xs:enumeration value="M"/>

<xs:enumeration value="T"/>

<xs:enumeration value="c"/>

<xs:enumeration value="d"/>

<xs:enumeration value="k"/>

<xs:enumeration value="m"/>

<xs:enumeration value="micro"/>

<xs:enumeration value="n"/>

<xs:enumeration value="none"/>

<xs:enumeration value="p"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:float" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountingUnit.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="docStatus" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.docStatus">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="due" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#AuxiliaryAccount.due">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Due">

<xs:sequence>

<xs:element name="arrears" minOccurs="1" maxOccurs="1" type="m:Money" sawsdl:modelReference="http://iec.ch/TC57/2009#Due.arrears"/>

<xs:element name="current" minOccurs="1" maxOccurs="1" type="m:Money" sawsdl:modelReference="http://iec.ch/TC57/2009#Due.current"/>

<xs:element name="interest" minOccurs="1" maxOccurs="1" type="m:Money" sawsdl:modelReference="http://iec.ch/TC57/2009#Due.interest"/>

<xs:element name="principle" minOccurs="1" maxOccurs="1" type="m:Money" sawsdl:modelReference="http://iec.ch/TC57/2009#Due.principle"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="lastCredit" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#AuxiliaryAccount.lastCredit">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#AccountMovement">

<xs:sequence>

<xs:element name="amount" minOccurs="1" maxOccurs="1" type="m:Money" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountMovement.amount"/>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountMovement.dateTime"/>

<xs:element name="reason" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountMovement.reason"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="lastDebit" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#AuxiliaryAccount.lastDebit">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#AccountMovement">

<xs:sequence>

<xs:element name="amount" minOccurs="1" maxOccurs="1" type="m:Money" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountMovement.amount"/>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountMovement.dateTime"/>

<xs:element name="reason" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#AccountMovement.reason"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="status" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="CustomerAgreement" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#AuxiliaryAgreement.CustomerAgreement">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#CustomerAgreement">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="docStatus" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.docStatus">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="status" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Document.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="validityInterval" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Agreement.validityInterval">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#DateTimeInterval">

<xs:sequence>

<xs:element name="end" minOccurs="0" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#DateTimeInterval.end"/>

<xs:element name="start" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#DateTimeInterval.start"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:simpleType name="RealEnergy" sawsdl:modelReference="http://iec.ch/TC57/2009#RealEnergy">

<xs:restriction base="xs:float"/>

</xs:simpleType>

<xs:simpleType name="PerCent" sawsdl:modelReference="http://iec.ch/TC57/2009#PerCent">

<xs:restriction base="xs:float"/>

</xs:simpleType>

<xs:simpleType name="AbsoluteDate" sawsdl:modelReference="http://iec.ch/TC57/2009#AbsoluteDate">

<xs:restriction base="xs:string"/>

</xs:simpleType>

<xs:simpleType name="Money" sawsdl:modelReference="http://iec.ch/TC57/2009#Money">

<xs:restriction base="xs:float"/>

</xs:simpleType>

</xs:schema>

MeterAssetConfig

<?xml version="1.0" encoding="UTF-8"?>

<xs:schema xmlns:xs="http://www.w3.org/2001/XMLSchema" xmlns:a="http://langdale.com.au/2005/Message#" xmlns:sawsdl="http://www.w3.org/ns/sawsdl" targetNamespace="http://iec.ch/TC57/2009/MeterAssetConfig#" elementFormDefault="qualified" attributeFormDefault="unqualified" xmlns="http://langdale.com.au/2005/Message#" xmlns:m="http://iec.ch/TC57/2009/MeterAssetConfig#">

<xs:element name="MeterAssetConfig" type="m:MeterAssetConfig"/>

<xs:complexType name="MeterAssetConfig">

<xs:sequence>

<xs:element name="MeterAsset" type="m:MeterAsset" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="MeterAsset" sawsdl:modelReference="http://iec.ch/TC57/2009#MeterAsset">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="amrSystem" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#EndDeviceAsset.amrSystem"/>

<xs:element name="application" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Asset.application"/>

<xs:element name="category" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Asset.category"/>

<xs:element name="demandResponse" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#EndDeviceAsset.demandResponse"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="disconnect" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#EndDeviceAsset.disconnect"/>

<xs:element name="dstEnabled" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#EndDeviceAsset.dstEnabled"/>

<xs:element name="formNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#MeterAsset.formNumber"/>

<xs:element name="initialCondition" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Asset.initialCondition"/>

<xs:element name="initialLossOfLife" minOccurs="0" maxOccurs="1" type="m:PerCent" sawsdl:modelReference="http://iec.ch/TC57/2009#Asset.initialLossOfLife"/>

<xs:element name="installationDate" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Asset.installationDate"/>

<xs:element name="kH" minOccurs="0" maxOccurs="1" type="xs:float" sawsdl:modelReference="http://iec.ch/TC57/2009#MeterAsset.kH"/>

<xs:element name="kR" minOccurs="0" maxOccurs="1" type="xs:float" sawsdl:modelReference="http://iec.ch/TC57/2009#MeterAsset.kR"/>

<xs:element name="loadControl" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#EndDeviceAsset.loadControl"/>

<xs:element name="lotNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Asset.lotNumber"/>

<xs:element name="manufacturedDate" minOccurs="0" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Asset.manufacturedDate"/>

<xs:element name="metrology" minOccurs="1" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#EndDeviceAsset.metrology"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="outageReport" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#EndDeviceAsset.outageReport"/>

<xs:element name="readRequest" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#EndDeviceAsset.readRequest"/>

<xs:element name="relayCapable" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#EndDeviceAsset.relayCapable"/>

<xs:element name="reverseFlowHandling" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#EndDeviceAsset.reverseFlowHandling"/>

<xs:element name="serialNumber" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Asset.serialNumber"/>

<xs:element name="timeZoneOffset" minOccurs="0" maxOccurs="1" type="m:Minutes" sawsdl:modelReference="http://iec.ch/TC57/2009#EndDeviceAsset.timeZoneOffset"/>

<xs:element name="utcNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Asset.utcNumber"/>

<xs:element name="Seals" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#AssetContainer.Seals">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Seal">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="appliedDateTime" minOccurs="0" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Seal.appliedDateTime"/>

<xs:element name="condition" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Seal.condition">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#SealConditionKind">

<xs:restriction base="xs:string">

<xs:enumeration value="broken"/>

<xs:enumeration value="locked"/>

<xs:enumeration value="missing"/>

<xs:enumeration value="open"/>

<xs:enumeration value="other"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="kind" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Seal.kind">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#SealKind">

<xs:restriction base="xs:string">

<xs:enumeration value="lead"/>

<xs:enumeration value="lock"/>

<xs:enumeration value="other"/>

<xs:enumeration value="steel"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="sealNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Seal.sealNumber"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="ServiceDeliveryPoint" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#EndDeviceAsset.ServiceDeliveryPoint">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceDeliveryPoint">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="ServiceLocation" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#EndDeviceAsset.ServiceLocation">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceLocation">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="status" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Asset.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:simpleType name="Minutes" sawsdl:modelReference="http://iec.ch/TC57/2009#Minutes">

<xs:restriction base="xs:float"/>

</xs:simpleType>

<xs:simpleType name="PerCent" sawsdl:modelReference="http://iec.ch/TC57/2009#PerCent">

<xs:restriction base="xs:float"/>

</xs:simpleType>

</xs:schema>

ServiceDeliveryPointConfig

<?xml version="1.0" encoding="UTF-8"?>

<xs:schema xmlns:xs="http://www.w3.org/2001/XMLSchema" xmlns:a="http://langdale.com.au/2005/Message#" xmlns:sawsdl="http://www.w3.org/ns/sawsdl" targetNamespace="http://iec.ch/TC57/2009/ServiceDeliveryPointConfig#" elementFormDefault="qualified" attributeFormDefault="unqualified" xmlns="http://langdale.com.au/2005/Message#" xmlns:m="http://iec.ch/TC57/2009/ServiceDeliveryPointConfig#">

<xs:element name="ServiceDeliveryPointConfig" type="m:ServiceDeliveryPointConfig"/>

<xs:complexType name="ServiceDeliveryPointConfig">

<xs:sequence>

<xs:element name="ServiceDeliveryPoint" type="m:ServiceDeliveryPoint" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="ServiceDeliveryPoint" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceDeliveryPoint">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="billingCycle" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceDeliveryPoint.billingCycle"/>

<xs:element name="budgetBill" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceDeliveryPoint.budgetBill"/>

<xs:element name="checkBilling" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceDeliveryPoint.checkBilling"/>

<xs:element name="consumptionRealEnergy" minOccurs="0" maxOccurs="1" type="m:RealEnergy" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceDeliveryPoint.consumptionRealEnergy"/>

<xs:element name="ctptReference" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceDeliveryPoint.ctptReference"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="estimatedLoad" minOccurs="0" maxOccurs="1" type="m:CurrentFlow" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceDeliveryPoint.estimatedLoad"/>

<xs:element name="grounded" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceDeliveryPoint.grounded"/>

<xs:element name="loadMgmt" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceDeliveryPoint.loadMgmt"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="nominalServiceVoltage" minOccurs="1" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceDeliveryPoint.nominalServiceVoltage"/>

<xs:element name="phaseConfig" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceDeliveryPoint.phaseConfig">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#PhaseConfigurationKind">

<xs:restriction base="xs:string">

<xs:enumeration value="onePhaseThreeWire"/>

<xs:enumeration value="onePhaseTwoWire"/>

<xs:enumeration value="other"/>

<xs:enumeration value="threePhaseFourWire"/>

<xs:enumeration value="threePhaseThreeWire"/>

<xs:enumeration value="threePhaseTwoWire"/>

<xs:enumeration value="twoPhaseThreeWire"/>

<xs:enumeration value="twoPhaseTwoWire"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="ratedCurrent" minOccurs="1" maxOccurs="1" type="m:CurrentFlow" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceDeliveryPoint.ratedCurrent"/>

<xs:element name="ratedPower" minOccurs="1" maxOccurs="1" type="m:ActivePower" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceDeliveryPoint.ratedPower"/>

<xs:element name="serviceDeliveryRemark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceDeliveryPoint.serviceDeliveryRemark"/>

<xs:element name="servicePriority" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceDeliveryPoint.servicePriority"/>

<xs:element name="CustomerAgreement" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceDeliveryPoint.CustomerAgreement">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#CustomerAgreement">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="PricingStructures" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceDeliveryPoint.PricingStructures">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#PricingStructure">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="Tariffs" minOccurs="1" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#PricingStructure.Tariffs">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Tariff">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="TariffProfiles" minOccurs="1" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#Tariff.TariffProfiles">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#TariffProfile">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="SDPLocations" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceDeliveryPoint.SDPLocations">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#SDPLocation">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="ServiceCategory" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceDeliveryPoint.ServiceCategory">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceCategory">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="ServiceLocation" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceDeliveryPoint.ServiceLocation">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceLocation">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="ServiceSupplier" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceDeliveryPoint.ServiceSupplier">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceSupplier">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:simpleType name="RealEnergy" sawsdl:modelReference="http://iec.ch/TC57/2009#RealEnergy">

<xs:restriction base="xs:float"/>

</xs:simpleType>

<xs:simpleType name="ActivePower" sawsdl:modelReference="http://iec.ch/TC57/2009#ActivePower">

<xs:restriction base="xs:float"/>

</xs:simpleType>

<xs:simpleType name="CurrentFlow" sawsdl:modelReference="http://iec.ch/TC57/2009#CurrentFlow">

<xs:restriction base="xs:float"/>

</xs:simpleType>

</xs:schema>

ServiceLocationConfig

<?xml version="1.0" encoding="UTF-8"?>

<xs:schema xmlns:xs="http://www.w3.org/2001/XMLSchema" xmlns:a="http://langdale.com.au/2005/Message#" xmlns:sawsdl="http://www.w3.org/ns/sawsdl" targetNamespace="http://iec.ch/TC57/2009/ServiceLocationConfig#" elementFormDefault="qualified" attributeFormDefault="unqualified" xmlns="http://langdale.com.au/2005/Message#" xmlns:m="http://iec.ch/TC57/2009/ServiceLocationConfig#">

<xs:element name="ServiceLocationConfig" type="m:ServiceLocationConfig"/>

<xs:complexType name="ServiceLocationConfig">

<xs:sequence>

<xs:element name="ServiceLocation" type="m:ServiceLocation" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="ServiceLocation" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceLocation">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="accessMethod" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceLocation.accessMethod"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="category" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Location.category"/>

<xs:element name="corporateCode" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Location.corporateCode"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="direction" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Location.direction"/>

<xs:element name="geoInfoReference" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Location.geoInfoReference"/>

<xs:element name="isPolygon" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#Location.isPolygon"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="needsInspection" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceLocation.needsInspection"/>

<xs:element name="siteAccessProblem" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceLocation.siteAccessProblem"/>

<xs:element name="CustomerAgreements" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#ServiceLocation.CustomerAgreements">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#CustomerAgreement">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="ElectronicAddresses" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#Location.ElectronicAddresses">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="email" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.email"/>

<xs:element name="lan" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.lan"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="password" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.password"/>

<xs:element name="radio" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.radio"/>

<xs:element name="userID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.userID"/>

<xs:element name="web" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.web"/>

<xs:element name="status" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="mainAddress" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Location.mainAddress">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#StreetAddress">

<xs:sequence>

<xs:element name="status" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetAddress.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="streetDetail" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetAddress.streetDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail">

<xs:sequence>

<xs:element name="addressGeneral" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.addressGeneral"/>

<xs:element name="buildingName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.buildingName"/>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.code"/>

<xs:element name="name" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.name"/>

<xs:element name="number" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.number"/>

<xs:element name="prefix" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.prefix"/>

<xs:element name="suffix" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.suffix"/>

<xs:element name="suiteNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.suiteNumber"/>

<xs:element name="type" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.type"/>

<xs:element name="withinTownLimits" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.withinTownLimits"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="townDetail" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetAddress.townDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail">

<xs:sequence>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.code"/>

<xs:element name="country" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.country"/>

<xs:element name="name" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.name"/>

<xs:element name="section" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.section"/>

<xs:element name="stateOrProvince" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.stateOrProvince"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="PositionPoints" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#Location.PositionPoints">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#PositionPoint">

<xs:sequence>

<xs:element name="sequenceNumber" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/2009#PositionPoint.sequenceNumber"/>

<xs:element name="xPosition" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#PositionPoint.xPosition"/>

<xs:element name="yPosition" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#PositionPoint.yPosition"/>

<xs:element name="zPosition" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#PositionPoint.zPosition"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="secondaryAddress" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Location.secondaryAddress">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#StreetAddress">

<xs:sequence>

<xs:element name="status" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetAddress.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="streetDetail" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetAddress.streetDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail">

<xs:sequence>

<xs:element name="addressGeneral" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.addressGeneral"/>

<xs:element name="buildingName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.buildingName"/>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.code"/>

<xs:element name="name" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.name"/>

<xs:element name="number" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.number"/>

<xs:element name="prefix" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.prefix"/>

<xs:element name="suffix" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.suffix"/>

<xs:element name="suiteNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.suiteNumber"/>

<xs:element name="type" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.type"/>

<xs:element name="withinTownLimits" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.withinTownLimits"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="townDetail" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetAddress.townDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail">

<xs:sequence>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.code"/>

<xs:element name="country" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.country"/>

<xs:element name="name" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.name"/>

<xs:element name="section" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.section"/>

<xs:element name="stateOrProvince" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.stateOrProvince"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="status" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Location.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="TelephoneNumbers" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#Location.TelephoneNumbers">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#TelephoneNumber">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="areaCode" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TelephoneNumber.areaCode"/>

<xs:element name="cityCode" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TelephoneNumber.cityCode"/>

<xs:element name="countryCode" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TelephoneNumber.countryCode"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="extension" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TelephoneNumber.extension"/>

<xs:element name="localNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TelephoneNumber.localNumber"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:schema>

SDPLocationConfig

<?xml version="1.0" encoding="UTF-8"?>

<xs:schema xmlns:xs="http://www.w3.org/2001/XMLSchema" xmlns:a="http://langdale.com.au/2005/Message#" xmlns:sawsdl="http://www.w3.org/ns/sawsdl" targetNamespace="http://iec.ch/TC57/2009/SDPLocationConfig#" elementFormDefault="qualified" attributeFormDefault="unqualified" xmlns="http://langdale.com.au/2005/Message#" xmlns:m="http://iec.ch/TC57/2009/SDPLocationConfig#">

<xs:element name="SDPLocationConfig" type="m:SDPLocationConfig"/>

<xs:complexType name="SDPLocationConfig">

<xs:sequence>

<xs:element name="SDPLocation" type="m:SDPLocation" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="SDPLocation" sawsdl:modelReference="http://iec.ch/TC57/2009#SDPLocation">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="accessMethod" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#SDPLocation.accessMethod"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="category" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Location.category"/>

<xs:element name="corporateCode" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Location.corporateCode"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="direction" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Location.direction"/>

<xs:element name="geoInfoReference" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Location.geoInfoReference"/>

<xs:element name="isPolygon" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#Location.isPolygon"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="occupancyDate" minOccurs="0" maxOccurs="1" type="m:AbsoluteDate" sawsdl:modelReference="http://iec.ch/TC57/2009#SDPLocation.occupancyDate"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#SDPLocation.remark"/>

<xs:element name="siteAccessProblem" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#SDPLocation.siteAccessProblem"/>

<xs:element name="ElectronicAddresses" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#Location.ElectronicAddresses">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="email" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.email"/>

<xs:element name="lan" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.lan"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="password" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.password"/>

<xs:element name="radio" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.radio"/>

<xs:element name="userID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.userID"/>

<xs:element name="web" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.web"/>

<xs:element name="status" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#ElectronicAddress.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="mainAddress" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Location.mainAddress">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#StreetAddress">

<xs:sequence>

<xs:element name="status" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetAddress.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="streetDetail" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetAddress.streetDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail">

<xs:sequence>

<xs:element name="addressGeneral" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.addressGeneral"/>

<xs:element name="buildingName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.buildingName"/>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.code"/>

<xs:element name="name" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.name"/>

<xs:element name="number" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.number"/>

<xs:element name="prefix" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.prefix"/>

<xs:element name="suffix" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.suffix"/>

<xs:element name="suiteNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.suiteNumber"/>

<xs:element name="type" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.type"/>

<xs:element name="withinTownLimits" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.withinTownLimits"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="townDetail" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetAddress.townDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail">

<xs:sequence>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.code"/>

<xs:element name="country" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.country"/>

<xs:element name="name" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.name"/>

<xs:element name="section" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.section"/>

<xs:element name="stateOrProvince" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.stateOrProvince"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="PositionPoints" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#Location.PositionPoints">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#PositionPoint">

<xs:sequence>

<xs:element name="sequenceNumber" minOccurs="0" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/2009#PositionPoint.sequenceNumber"/>

<xs:element name="xPosition" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#PositionPoint.xPosition"/>

<xs:element name="yPosition" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#PositionPoint.yPosition"/>

<xs:element name="zPosition" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#PositionPoint.zPosition"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="secondaryAddress" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Location.secondaryAddress">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#StreetAddress">

<xs:sequence>

<xs:element name="status" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetAddress.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="streetDetail" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetAddress.streetDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail">

<xs:sequence>

<xs:element name="addressGeneral" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.addressGeneral"/>

<xs:element name="buildingName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.buildingName"/>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.code"/>

<xs:element name="name" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.name"/>

<xs:element name="number" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.number"/>

<xs:element name="prefix" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.prefix"/>

<xs:element name="suffix" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.suffix"/>

<xs:element name="suiteNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.suiteNumber"/>

<xs:element name="type" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.type"/>

<xs:element name="withinTownLimits" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetDetail.withinTownLimits"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="townDetail" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#StreetAddress.townDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail">

<xs:sequence>

<xs:element name="code" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.code"/>

<xs:element name="country" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.country"/>

<xs:element name="name" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.name"/>

<xs:element name="section" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.section"/>

<xs:element name="stateOrProvince" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TownDetail.stateOrProvince"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="status" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Location.status">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Status">

<xs:sequence>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.dateTime"/>

<xs:element name="reason" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.reason"/>

<xs:element name="remark" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.remark"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Status.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="TelephoneNumbers" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#Location.TelephoneNumbers">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#TelephoneNumber">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="areaCode" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TelephoneNumber.areaCode"/>

<xs:element name="cityCode" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TelephoneNumber.cityCode"/>

<xs:element name="countryCode" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TelephoneNumber.countryCode"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="extension" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TelephoneNumber.extension"/>

<xs:element name="localNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#TelephoneNumber.localNumber"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:simpleType name="AbsoluteDate" sawsdl:modelReference="http://iec.ch/TC57/2009#AbsoluteDate">

<xs:restriction base="xs:string"/>

</xs:simpleType>

</xs:schema>

ReceiptRecord

<?xml version="1.0" encoding="UTF-8"?>

<xs:schema xmlns:xs="http://www.w3.org/2001/XMLSchema" xmlns:a="http://langdale.com.au/2005/Message#" xmlns:sawsdl="http://www.w3.org/ns/sawsdl" targetNamespace="http://iec.ch/TC57/2009/ReceiptRecord#" elementFormDefault="qualified" attributeFormDefault="unqualified" xmlns="http://langdale.com.au/2005/Message#" xmlns:m="http://iec.ch/TC57/2009/ReceiptRecord#">

<xs:element name="ReceiptRecord" type="m:ReceiptRecord"/>

<xs:complexType name="ReceiptRecord">

<xs:sequence>

<xs:element name="Receipt" type="m:Receipt" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="Receipt" sawsdl:modelReference="http://iec.ch/TC57/2009#Receipt">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="isBankable" minOccurs="1" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#Receipt.isBankable"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="CashierShift" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Receipt.CashierShift">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#CashierShift">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="activityInterval" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Shift.activityInterval">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#DateTimeInterval">

<xs:sequence>

<xs:element name="end" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#DateTimeInterval.end"/>

<xs:element name="start" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#DateTimeInterval.start"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="Cashier" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#CashierShift.Cashier">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Cashier">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="PointOfSale" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#CashierShift.PointOfSale">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#PointOfSale">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="location" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#PointOfSale.location"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="line" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Receipt.line">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#LineDetail">

<xs:sequence>

<xs:element name="amount" minOccurs="1" maxOccurs="1" type="m:Money" sawsdl:modelReference="http://iec.ch/TC57/2009#LineDetail.amount"/>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#LineDetail.dateTime"/>

<xs:element name="note" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#LineDetail.note"/>

<xs:element name="rounding" minOccurs="1" maxOccurs="1" type="m:Money" sawsdl:modelReference="http://iec.ch/TC57/2009#LineDetail.rounding"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="Tenders" minOccurs="1" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#Receipt.Tenders">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Tender">

<xs:sequence>

<xs:element name="Card" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Tender.Card">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Card">

<xs:sequence>

<xs:element name="accountHolderName" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Card.accountHolderName"/>

<xs:element name="cvNumber" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Card.cvNumber"/>

<xs:element name="expiryDate" minOccurs="1" maxOccurs="1" type="m:AbsoluteDate" sawsdl:modelReference="http://iec.ch/TC57/2009#Card.expiryDate"/>

<xs:element name="pan" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Card.pan"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="Cheque" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Tender.Cheque">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Cheque">

<xs:sequence>

<xs:element name="chequeNumber" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Cheque.chequeNumber"/>

<xs:element name="date" minOccurs="1" maxOccurs="1" type="m:AbsoluteDate" sawsdl:modelReference="http://iec.ch/TC57/2009#Cheque.date"/>

<xs:element name="kind" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Cheque.kind">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#ChequeKind">

<xs:restriction base="xs:string">

<xs:enumeration value="bankOrder"/>

<xs:enumeration value="other"/>

<xs:enumeration value="postalOrder"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="micrNumber" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Cheque.micrNumber"/>

<xs:element name="bankAccountDetail" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Cheque.bankAccountDetail">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#BankAccountDetail">

<xs:sequence>

<xs:element name="accountNumber" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#BankAccountDetail.accountNumber"/>

<xs:element name="bankName" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#BankAccountDetail.bankName"/>

<xs:element name="branchCode" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#BankAccountDetail.branchCode"/>

<xs:element name="holderID" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#BankAccountDetail.holderID"/>

<xs:element name="holderName" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#BankAccountDetail.holderName"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="VendorShift" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Receipt.VendorShift">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#VendorShift">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="merchantDebitAmount" minOccurs="0" maxOccurs="1" type="m:Money" sawsdl:modelReference="http://iec.ch/TC57/2009#VendorShift.merchantDebitAmount"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="posted" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#VendorShift.posted"/>

<xs:element name="activityInterval" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Shift.activityInterval">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#DateTimeInterval">

<xs:sequence>

<xs:element name="end" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#DateTimeInterval.end"/>

<xs:element name="start" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#DateTimeInterval.start"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="MerchantAccount" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#VendorShift.MerchantAccount">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#MerchantAccount">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="currentBalance" minOccurs="1" maxOccurs="1" type="m:Money" sawsdl:modelReference="http://iec.ch/TC57/2009#MerchantAccount.currentBalance"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="provisionalBalance" minOccurs="1" maxOccurs="1" type="m:Money" sawsdl:modelReference="http://iec.ch/TC57/2009#MerchantAccount.provisionalBalance"/>

<xs:element name="MerchantAgreement" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#MerchantAccount.MerchantAgreement">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#MerchantAgreement">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="Transactors" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#MerchantAccount.Transactors">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Transactor">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="Vendor" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#VendorShift.Vendor">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Vendor">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:simpleType name="AbsoluteDate" sawsdl:modelReference="http://iec.ch/TC57/2009#AbsoluteDate">

<xs:restriction base="xs:string"/>

</xs:simpleType>

<xs:simpleType name="Money" sawsdl:modelReference="http://iec.ch/TC57/2009#Money">

<xs:restriction base="xs:float"/>

</xs:simpleType>

</xs:schema>

TransactionRecord

<?xml version="1.0" encoding="UTF-8"?>

<xs:schema xmlns:xs="http://www.w3.org/2001/XMLSchema" xmlns:a="http://langdale.com.au/2005/Message#" xmlns:sawsdl="http://www.w3.org/ns/sawsdl" targetNamespace="http://iec.ch/TC57/2009/TransactionRecord#" elementFormDefault="qualified" attributeFormDefault="unqualified" xmlns="http://langdale.com.au/2005/Message#" xmlns:m="http://iec.ch/TC57/2009/TransactionRecord#">

<xs:element name="TransactionRecord" type="m:TransactionRecord"/>

<xs:complexType name="TransactionRecord">

<xs:sequence>

<xs:element name="Transaction" type="m:Transaction" minOccurs="0" maxOccurs="unbounded"/>

</xs:sequence>

</xs:complexType>

<xs:complexType name="Transaction" sawsdl:modelReference="http://iec.ch/TC57/2009#Transaction">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="diverseReference" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Transaction.diverseReference"/>

<xs:element name="donorReference" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Transaction.donorReference"/>

<xs:element name="kind" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Transaction.kind">

<xs:simpleType sawsdl:modelReference="http://iec.ch/TC57/2009#TransactionKind">

<xs:restriction base="xs:string">

<xs:enumeration value="accountPayment"/>

<xs:enumeration value="auxiliaryChargePayment"/>

<xs:enumeration value="diversePayment"/>

<xs:enumeration value="meterConfigurationToken"/>

<xs:enumeration value="other"/>

<xs:enumeration value="serviceChargePayment"/>

<xs:enumeration value="taxChargePayment"/>

<xs:enumeration value="tokenCancellation"/>

<xs:enumeration value="tokenExchange"/>

<xs:enumeration value="tokenFreeIssue"/>

<xs:enumeration value="tokenGrant"/>

<xs:enumeration value="tokenSalePayment"/>

<xs:enumeration value="transactionReversal"/>

</xs:restriction>

</xs:simpleType>

</xs:element>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="receiverReference" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Transaction.receiverReference"/>

<xs:element name="reversedId" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#Transaction.reversedId"/>

<xs:element name="serviceUnitsEnergy" minOccurs="0" maxOccurs="1" type="m:RealEnergy" sawsdl:modelReference="http://iec.ch/TC57/2009#Transaction.serviceUnitsEnergy"/>

<xs:element name="serviceUnitsError" minOccurs="0" maxOccurs="1" type="m:RealEnergy" sawsdl:modelReference="http://iec.ch/TC57/2009#Transaction.serviceUnitsError"/>

<xs:element name="AuxiliaryAccount" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Transaction.AuxiliaryAccount">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#AuxiliaryAccount">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="Charges" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#AuxiliaryAccount.Charges">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Charge">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="ChildCharges" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#Charge.ChildCharges">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Charge">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="CashierShift" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Transaction.CashierShift">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#CashierShift">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="activityInterval" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Shift.activityInterval">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#DateTimeInterval">

<xs:sequence>

<xs:element name="end" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#DateTimeInterval.end"/>

<xs:element name="start" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#DateTimeInterval.start"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="Cashier" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#CashierShift.Cashier">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Cashier">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="PointOfSale" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#CashierShift.PointOfSale">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#PointOfSale">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="location" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#PointOfSale.location"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="CustomerAccount" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Transaction.CustomerAccount">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#CustomerAccount">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="line" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Transaction.line">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#LineDetail">

<xs:sequence>

<xs:element name="amount" minOccurs="1" maxOccurs="1" type="m:Money" sawsdl:modelReference="http://iec.ch/TC57/2009#LineDetail.amount"/>

<xs:element name="dateTime" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#LineDetail.dateTime"/>

<xs:element name="note" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#LineDetail.note"/>

<xs:element name="rounding" minOccurs="1" maxOccurs="1" type="m:Money" sawsdl:modelReference="http://iec.ch/TC57/2009#LineDetail.rounding"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="MeterAsset" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Transaction.MeterAsset">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#MeterAsset">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="PricingStructure" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Transaction.PricingStructure">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#PricingStructure">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="Tariffs" minOccurs="1" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#PricingStructure.Tariffs">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Tariff">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="TariffProfiles" minOccurs="1" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#Tariff.TariffProfiles">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#TariffProfile">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="Receipt" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Transaction.Receipt">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Receipt">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="UserAttributes" minOccurs="0" maxOccurs="unbounded" sawsdl:modelReference="http://iec.ch/TC57/2009#Transaction.UserAttributes">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#UserAttribute">

<xs:sequence>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#UserAttribute.name"/>

<xs:element name="sequenceNumber" minOccurs="1" maxOccurs="1" type="xs:integer" sawsdl:modelReference="http://iec.ch/TC57/2009#UserAttribute.sequenceNumber"/>

<xs:element name="value" minOccurs="1" maxOccurs="1" type="m:StringQuantity" sawsdl:modelReference="http://iec.ch/TC57/2009#UserAttribute.value"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="VendorShift" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Transaction.VendorShift">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#VendorShift">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="merchantDebitAmount" minOccurs="0" maxOccurs="1" type="m:Money" sawsdl:modelReference="http://iec.ch/TC57/2009#VendorShift.merchantDebitAmount"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="posted" minOccurs="0" maxOccurs="1" type="xs:boolean" sawsdl:modelReference="http://iec.ch/TC57/2009#VendorShift.posted"/>

<xs:element name="activityInterval" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#Shift.activityInterval">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#DateTimeInterval">

<xs:sequence>

<xs:element name="end" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#DateTimeInterval.end"/>

<xs:element name="start" minOccurs="1" maxOccurs="1" type="xs:dateTime" sawsdl:modelReference="http://iec.ch/TC57/2009#DateTimeInterval.start"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="MerchantAccount" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#VendorShift.MerchantAccount">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#MerchantAccount">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="currentBalance" minOccurs="1" maxOccurs="1" type="m:Money" sawsdl:modelReference="http://iec.ch/TC57/2009#MerchantAccount.currentBalance"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

<xs:element name="provisionalBalance" minOccurs="1" maxOccurs="1" type="m:Money" sawsdl:modelReference="http://iec.ch/TC57/2009#MerchantAccount.provisionalBalance"/>

<xs:element name="MerchantAgreement" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#MerchantAccount.MerchantAgreement">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#MerchantAgreement">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="Transactors" minOccurs="0" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#MerchantAccount.Transactors">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Transactor">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

<xs:element name="Vendor" minOccurs="1" maxOccurs="1" sawsdl:modelReference="http://iec.ch/TC57/2009#VendorShift.Vendor">

<xs:complexType sawsdl:modelReference="http://iec.ch/TC57/2009#Vendor">

<xs:sequence>

<xs:element name="mRID" minOccurs="1" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.mRID"/>

<xs:element name="aliasName" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.aliasName"/>

<xs:element name="description" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.description"/>

<xs:element name="name" minOccurs="0" maxOccurs="1" type="xs:string" sawsdl:modelReference="http://iec.ch/TC57/2009#IdentifiedObject.name"/>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

</xs:element>

</xs:sequence>

</xs:complexType>

<xs:simpleType name="RealEnergy" sawsdl:modelReference="http://iec.ch/TC57/2009#RealEnergy">

<xs:restriction base="xs:float"/>

</xs:simpleType>

<xs:simpleType name="StringQuantity" sawsdl:modelReference="http://iec.ch/TC57/2009#StringQuantity">

<xs:restriction base="xs:string"/>

</xs:simpleType>

<xs:simpleType name="Money" sawsdl:modelReference="http://iec.ch/TC57/2009#Money">

<xs:restriction base="xs:float"/>

</xs:simpleType>

</xs:schema>

(Informative)

Mappings to ebIX

General

There are many official, defacto and draft standards being developed for the exchange of meter data. A common reality is that when integrating systems it is often necessary to map information between different models.  In order to recognize this, this annex is intended to describe some of the mappings between messages for meter readings between IEC 61968-9 and the European forum for energy Business Information eXchange (ebIX). The information in the annex was provided by ebIX.

The modelling results for the exchange of metered data for reconciliation process are to be found in a separate document (Measure for Reconciliation, www.ebix.org ).

The modelling results for the imbalance settlement process have been modelled by ETSO and are to be found in separate document (www.edi.etso-net.org ).

The modelling results for the reconciliation process are to be found in another separate document (Settle, Reconciliation, www.ebix.org ).

The following figure is a diagram of the structure of the ebIX XML Schema for metered data.

Figure I.1 - ebIX XML Schema

Figure I.1 - ebIX XML Schema (continued)

The following UML diagram provides a description of the related ebIX UML model.

Figure I.2 - ebIX Metered Data as UML Class Diagram

Table I.3 - Meter Reading: Mapping ebIX Metered Data to IEC MeterReadings

| IEC |  | ebIX |
| --- | --- | --- |
| MeterReading |  |  |  |  | MeteredData (TimeSeries) | ObservationPeriod |  |  |  |
|  |  |  |  |  |  | ObservationPeriod |  |  |  |
|  | EndDeviceEvent | category |  |  | X |  |  |  |  |
|  |  | reason |  |  | X |  |  |  |  |
|  |  | severity |  |  | X |  |  |  |  |
|  |  | timestamp |  |  | X |  |  |  |  |
|  |  | userID |  |  | X |  |  |  |  |
|  |  | Status |  |  | X |  |  |  |  |
|  | IntervalBlock | IntervalReading | timeStamp |  | MeteredData (TimeSeries) | Data (VolumeObservation) | Position |  |  |
|  |  |  | value |  |  |  | Quantity |  |  |
|  |  |  | ReadingQualities |  |  |  | QuantityQuality |  |  |
|  |  |  |  |  |  |  | EstimateQuality |  |  |
|  |  | ReadingType |  |  |  |  |  |  |  |
|  | MeterAsset | mRID |  |  | MeteredData (TimeSeries) | Register (Installation) | MeterIdentification |  |  |
|  | Reading | ReadingType |  |  |  |  | RegisterIdentification |  |  |
|  | Reading | timeStamp |  |  | MeteredData (TimeSeries) | Energy (Product) | Register (Installation) | Register (Reading) | Position |
|  |  |  |  |  |  |  |  |  | RegistrationDateTime |
|  |  | Value |  |  |  |  |  |  | Quantity |
|  |  | ReadingQuality | quality |  |  |  |  |  | Origin |
|  |  | ReadingType |  |  |  |  |  |  |  |
|  | ServiceDeliveryPoint | mRID |  |  | MeteredData (TimeSeries) | MeteringPoint (Domain) | Identification |  |  |
| ReadingType | mRID |  |  |  | MeteredData (TimeSeries) | Identification |  |  |  |
|  | name |  |  |  |  | AncillaryRole |  |  |  |
|  |  |  |  |  |  | ReasonForTransaction |  |  |  |
|  |  |  |  |  |  | BusinessSector |  |  |  |
|  |  |  |  |  |  | Function |  |  |  |
|  |  |  |  |  |  | Resolution |  |  |  |
| X |  |  |  |  | MeteredData (TimeSeries) | Energy (Product) | Identifier |  |  |
| X |  |  |  |  |  |  | Unit |  |  |
| X |  |  |  |  | MeteredData (TimeSeries) | RegistrationDateTime |  |  |  |
| X |  |  |  |  |  | LatestUpdateDate |  |  |  |
| X |  |  |  |  | MeteredData (TimeSeries) | MeteringPoint (Domain) | Delivery (Contract) | StartDate |  |
| X |  |  |  |  |  |  |  | EndDate |  |
| X |  |  |  |  |  |  | Type (Characteristics) | TypeOfMeteringPoint |  |
| X |  |  |  |  |  |  |  | StandardLoadProfile |  |
| X |  |  |  |  |  |  |  | MeteringMethod |  |
| X |  |  |  |  |  |  |  | SettlementMethod |  |
| X |  |  |  |  | MeteredData (TimeSeries) | InArea (Domain) | Identification |  |  |
| X |  |  |  |  |  | OutArea (Domain) | Identification |  |  |
| X |  |  |  |  |  | MeteringGridArea (Domain) | Identification |  |  |
| X |  |  |  |  |  | BalanceResponsible (Party) | Identification |  |  |
| X |  |  |  |  |  | BalanceSupplier (Party) | Identification |  |  |
| X |  |  |  |  |  | ReconciliationAccountable (Party) | Identification |  |  |
| X |  |  |  |  | MeteredData (TimeSeries) | Aggregation (Characteristics) | TypeOfMeteringPoint |  |  |
| X |  |  |  |  |  |  | StandardLoadProfile |  |  |
| X |  |  |  |  |  |  | MeteringMethod |  |  |
| X |  |  |  |  |  |  | SettlementMethod |  |  |
| X |  |  |  |  |  |  | BalanceGroup (Domain) | Identification |  |
| X |  |  |  |  |  |  | BalanceResponsible (Party) | Identification |  |

(Informative)

Request Parameters

General

The purpose of this annex is to describe filters that can be used for ‘GET’ requests in order to filter the contents of the payload that is returned on the REPLY message. If needed, these filters can be defined as contextual profiles in a manner similar to those used to define payloads. Those structures are then realized as XML schemas. The payloads would be used in the ‘any ##other’ element of the Request structure in a request message.

Figure J.1 - Message Request Structure

The ‘StartTime’ and ‘EndTime’ tags are often used to narrow the results to a given time interval. The ‘ID’ tags can be used to specify the mRIDs for a set of objects of interest. The ‘Option’ parameter can also be used to meet specific application needs. Other qualifiers can be specified using the ‘any ##other’ element as needed.

GetMeterReadings

The following structure is a contextual profile that can be used to qualify ‘GET MeterReadings’ requests.

Figure J.2 - GetMeterReadings

GetEndDeviceAssets

The following structure is a contextual profile that can be used to qualify ‘GET EndDeviceAssets’ requests.

Figure J.3 - GetEndDeviceAssets

GetCustomerMeterDataSet

The following structure is a contextual profile that can be used to qualify ‘GET CustomerMeterDataSet’ requests.

Figure J.4 - 	GetCustomerMeterDataSet

# Footnotes

See Annex B for a Recommended message structure.

# Text boxes

End Device

- Metrology

- Communications

- Connect /Disconnect

- Load Control

- Demand Response

- Relays