# PRECOMMISSIONING & COMMISSIONING PROCEDURE

# PRE-COMMISSIONING CHECKS FOR DIGITAL VOLTAGE REGULATOR FOR M/S AES, KELANITISSA, Colombo SRILANKA

- Inspect Digital Voltage Regulator panel. Remove tools, conductor strands and any other material lying loose.

- Use vacuum cleaner to remove dust small particles. Don’t use air hoses, which may contain oil, moisture etc.

- Check all power and control circuit connections at terminal blocks, cable terminals, contactor terminals and bus bolts for tightness.

- Plug all unused holes and openings, including those for cable entries.

- In case, meters and relays are packed separately, mount these on the respective cutouts and connect them. Refer the GA/Schematic diagrams and terminal chart before connecting the meters and relays.

- While dispatching the panel, secondaries of CTs are shorted. Remove these shorting while connecting relays /meters.

- Check that fuses are fitted in main and auxiliary circuit and that ratings are appropriate for the circuit.

- Close all access plates, doors and openings before the Voltage Regulator is energized.

- Ensure that wires are not hanging loose. Anchor them firmly, preferably with plastic clamps.

- Temporary connections made during testing should be removed.

- A thorough check of control and protection scheme is essential before commissioning.

- Ensure that all outgoing switches are in the OFF position before energizing the Voltage Regulator Panel.

- Recommended clearance on front and rear of the panel is 1.5 meter.

- Ensure ‘0’Volt Earth & Screen Earth of AVR shall preferably be earthed to separate Electronic Earth points in the Plant before charging the panel.

- Checking of cable connectors

- Check cable connectors: - AT ONE END ONLY

  - AA-X01-218

  - AA-X01-226

  - AA-X05-230

  - AA-X29-222

  - AA-X37-218

  - AA-X37-226

  - AA-X41-230

  - AA-X65-222

  - AB-X01-218

  - AB-X01-226

  - AB-X25-218

  - AB-X33-210

- Check cable connectors:- AT BOTH ENDS

  - AB-X21-202 TO AA-X61-210

  - AB-X21-210 TO AA-X41-210

  - AB-X21-218 TO AA-X41-218

  - AB-X21-226 TO AA-X61-218

  - AB-x25-202 TO AA-X65-214

  - AB-X25-206 TO AA-X29-214

  - AB-X25-210   TO AA-X65-202

  - AB-X25-226 TO AA-X29-202

  - AB-X33-218 TO AD-X21-02

  - AB-X33-226 TO AD-X21-10

  - AA-X53-206 TO AB-X77-202

  - AA-X41-226 TO AB-X17-202

  - AB-X53-218 TO A01

  - AB-X53-202 TO A02

  - AB-X49-202 TO A03

  - AB-X49-226 TO A51

  - AB-X45-226   TO A52

  - AA-X53-226   TO U1

  - AA-X65-230   TO U1

  - AA-X29-230   TO U2

3.Check all cards, burg jumpers, switch settings etc. as per the test report no.: 205/02/033 as below:

- UNC4660a-p – Measuring value processing for channel-1 (Auto): DE010/U1

- UNC0661	- Interrupt Unit for Channel-1: AA53

- UN0610 – Analog Input/Output unit for Channel-1: AA57

- UN0662 – Binary Input / Output unit for channel-1: AA61

- UN0663 – Gate control unit for channel-1: AA65

- Un0809 – Pulse final stage for channel-1: AG01

- UN0660 – Computer unit for channel-1: AA49

- Un0664 – Power supply unit for channel-1: AA37

- UNC4660a-p - Measuring value processing for channel-2(Manual) : DE020/U2

- UN0663 – Gate control unit for channel- 2: AA29

- UN0809 – Pulse final stage for channel-2: AG03

- UN0664 – Power supply unit for channel-2: AA01

- Un0664 – Power supply unit for PLC: AB01

- KX 9180 –48 V Supply unit: AG06

- KX 9180 –48 V Supply unit: AG16

- UN0660 – Computer unit for PLC: AB13

- UNC4661 – Digital Input interface for PLC: REG A01

- UNC4661 – Digital Input interface for PLC: REG A02

- UNC4661 – Digital Input interface for PLC: REG A03

- UNC4662a-p – Digital Output interface used for PLC: REG- 51

- UNC4662a-p – Digital Output interface used for PLC: REG-A52

- UN0662 – Binary Input / Output unit for PLC: AB21

- UN0662 – Binary Input / Output unit for PLC: AB25

- UN0662 – Binary Input / Output unit for PLC: AB33

- UN0662 – Binary Input / Output unit for PLC: AB45

- UN0662 – Binary Input / Output unit for PLC: AB49

- UN0662 – Binary Input / Output unit for PLC: AB53

- Un0662 – Alarm indication unit: AB61

- UN0611 – Analog Input/Output unit for monitoring: AB17

- Un0660 – Computer unit for Monitoring: AB73

- UN0611 – Analog Input/Output unit for monitoring: AB77

- UN0662 – Binary Input / Output unit for monitoring: AB81

4.Lists of Parameters for separate functional groups: Check Software address as per the test report.

      - AVR Channel-1: Software versions HIER 452555 (AA49)

      - PLC HIER 452 562 (AB13)

      - Monitoring function HIER 452561 (AB73)

5. AC and DC power supply circuits:

a) Station AC Aux. Supply: 3-Phase, 50 Hz, 415 V with Neutral

TBR- 9,10,11,12

b) Station battery supply TBR – 14,15

c) Generator PT supply –3-ph, 50 Hz, 110 V AC, TBR-17, 18,19

d) Generator CT supply – 1 A TBR-21 to 26

e) PMG Supply –3-ph, 220 V ac, 150 Hz –TBR-4, 5,6

f) Heater and illumination supply: 1-ph, 240 V AC, TBR-7, 8

6.Checking of Logic sequence scheme:

- Field breaker ‘ON’

a) Local								ok

b) Remote								ok

2.Field breaker ‘OFF’

a) Local								ok

b) Remote								0k

3. Excitation ‘ON/OFF’							ok

4.Channel Changeover auto to manual

a) Local								ok

b) Remote 								ok

c) Protections							ok

5. Control of Auto/man reference

a) Local								ok

b) Remote								ok

6.Field breaker trip for all trip faults as per scheme		ok

7.Light load test of AVR:

Switch S865/1 of UN0663 of manual channel (AA29) set in pos.-1.After test normalize the same.

Control characteristics:

Vac: 415 V, 3-ph, 50 Hz

## Connect load: 1000 Watt Halogen Lamp

Converter limit: 10 deg

Inverter limit: 170 deg.

V. Synchronizing: 110V, 3-ph, 50 Hz.

Manual Channel:

| Sl. No. | Control Voltage Ust (DC) | DVR Voltmeter DC Volts | DVR Ammeter DC Amps | Terminal Voltage (1R & 2R) DC Volts |
| --- | --- | --- | --- | --- |
| 1 | 0.007 | 13 | 1.1 | 13.18 |
| 2 | 0.994 | 20 | 1.2 | 18.80 |
| 3 | 2.001 | 26 | 1.4 | 25.38 |
| 4 | 2.998 | 33 | 1.6 | 33.00 |
| 5 | 4.00 | 42 | 1.8 | 41.78 |
| 6 | 5.00 | 51 | 2.0 | 51.67 |
| 7 | 6.01 | 62 | 2.2 | 62.17 |
| 8 | 7.01 | 72 | 2.3 | 72.6 |
| 9 | 8.01 | 83 | 2.6 | 85.14 |
| 10 | 9.02 | 90 | 2.7 | 90.12 |
| 11 | 9.80 | 95 | 2.8 | 96.65 |

Auto Channel:

| Sl. No. | Control Voltage, Ust DC Volts | DVR Voltmeter DC Volts | DVR Ammeter DC Amps | Terminal Voltage (1R & 2R) DC Volts |
| --- | --- | --- | --- | --- |
| 1 | 0.00 | 15 | 1.1 | 13.20 |
| 2 | 0.999 | 20 | 1.2 | 18.54 |
| 3 | 2.00 | 26 | 1.5 | 25.01 |
| 4 | 3.01 | 33 | 1.7 | 32.90 |
| 5 | 4.01 | 42 | 1.85 | 41.5 |
| 6 | 5.00 | 51 | 1.9 | 51.2 |
| 7 | 6.01 | 53 | 1.95 | 53.00 |
| 8 | 7.00 | 56 | 2.0 | 55.85 |
| 9 | 8.02 | 68 | 2.1 | 66.4 |
| 10 | 9.02 | 79 | 2.5 | 79.6 |
| 11 | 9.80 | 92 | 2.8 | 96.0 |

MCB’s Settings:

| Regulation cubicle | Range | Recommended settings |
| --- | --- | --- |
| F56 F51 TO F55, F57 F71 F91, F92 F72, F73, F81 F82, F75, 78 F74, F79, F80 | 25 A 3 A 9-14 A 12.5A to 16A 0.63 to 1 A 0.1 to 0.16 A 2.5 TO 4 A | FIXED FIXED 12 A 12.5 A 0.63 A 0.1 A 2.5 A |

M/S BHEL					M/S L&T				M/S AES