# SECTION 14200

# ELEVATORS

# PART 1 - GENERAL:

- DESCRIPTION:

  - Work Included in This Section:  Provide electric traction elevators complete as shown and specified. Section of the new machine room and hoistway wall fronts will have a 15 inch expansion joint to the existing building and section of the machine room. Contractor shall provide flexible conduits and wiring when crossing the expansion joint.

  - Related Work Not Included in This Section:

    - Hoistways:  Construction of hoistways, screens/ unperforated wall between hoistways, waterproof pits, machine room and controller areas, all properly framed, enclosed and adequately ventilated as shown.

    - Access:  Legal access consisting of self-closing and locking access doors, roof ladders, gratings and stairs to machine rooms, controller areas and hoistways.

    - Supports:  Providing supports as shown to carry structural reactions, impact and uplift loads imposed by elevator equipment.

    - Sill Supports:  Support full width of hoistway at edge of slab for attachment of sill support angles to be provided and installed by Elevator Contractor.

    - Grouting:  Grouting behind entrance frames where concrete walls occur.

    - Entrances: Infill sheet rock to entrance frame to provide required enclosure fire rating per Building Code.

    - Patching:  Patching of floors, walls and surfaces constituting final finishes.

    - Block-Outs: Block-outs, pockets and chases in walls and floors for entrances, signals, fixtures, cables and conduits.

    - Electrical Work:

      - Power Feeders:  Installation and connection of three phase power through fused disconnects lockable switches and extended to terminals of controllers per code requirements. Provide continuous ground conductor from building ground to elevator controllers.

      - Power Disconnecting Means: Where sprinklers are provided in elevator machine rooms and hoistways, means shall be provided to automatically disconnect the main line power supply to the affected elevator prior to the application of water.  This means shall not be self-resetting.  The activation of sprinklers outside of the hoistway or machine room shall not disconnect the main line power supply.

      - Light and Auxiliary Circuits: Separate single-phase circuit through over current protected lockable disconnect and extended to controller for car lights and fan for each elevator.

      - Emergency Communication Circuit:  Emergency telephone circuit for each elevator, terminated at junction box of each controller.

      - Convenience Outlets & Illumination: Lights, light switches and convenience outlets in pits, machine rooms, controller areas, overhead sheave and governor spaces.

      - Conduit:  Installation of electrical conduits, pull boxes with pull wire between hoistways and remote locations of each indicator and control panel.  Additional conduit and pull boxes required for the complete installation shall be included under this Section.  Wire and final connections by the Elevator Installer.

      - Temporary Power:  Electric power during construction for installation.

      - Common Circuit:  Dedicated pollution free single phase 20-ampere circuit through fused mainline switch or circuit breaker and extended to common group controller for each bank of two elevators or more.

      - Standby Power:  Automatic transfer of emergency power and lighting supply through normal feeders with means of absorbing regenerative power. Two No. 14 wires from contacts on transfer switch to designated controller to elevator machine rooms to signal transfer of power.

      - Sensing Devices:  Smoke detectors and heat sensors in elevator lobbies, machine rooms and hoistways with circuits terminated at junction box in machine rooms for emergency fire service operation. When devices are located at top of hoistways, a separate means of access to service the devices are to be provided.

      - Life Safety Circuits:  Circuits terminated at junction box at each controller for life safety speakers in each elevator car and fireman's phone communication.

      - Intercommunication System Circuit:  Single-phase 10 ampere circuit terminated at junction box in each elevator machine room for intercom system amplifier.

      - Cameras: Provision of cameras, mounting boxes, mounting brackets in cars and wiring to location outside of elevator machine room for connection to wiring by elevator contractor to each car camera.

    - Barricades:  Protection of open hoistways during construction as required by governing authority.

    - Painting:  Field painting of prime finish items constituting final finishes.

    - Pit Ladders Support: Provide structure support for the elevator pit ladders, installed by Elevator Contractor.

  - Related Work Interfaced With This Section:

    - Life Safety or Public Address Speakers:  Furnished by others; wire from machine room to car, accommodations and installation in car canopy by this Section.

    - Card/Fob Readers:  Furnished by others; wire from machine room to car, interfacing with elevator controls and installation in elevator car by this Section.  Connection in machine room and testing by others.

    - Close Circuit Cameras:  Furnished by others; wire from machine room to elevator cars by this Section.  Connection in machine room and testing by others.

    - Key Cylinders:  Furnished by Owner; installed under this Section.

  - Definitions:

    - Main Lobby: Ground Floor

    - Terminal Dispatch Floor: Ground Floor

    - Fire Recall Floor:  Ground Floor

    - Alternate Fire Recall Floor:  To be selected by Fire Marshal

- QUALITY ASSURANCE:

  - Qualifications of Bidders:

    - Manufacturer's Qualifications:  The design, engineering and manufacture of major elevator components such as machines, motors, motor drive units, controllers, car door operators, safeties, governors, selectors, etc. shall be non proprietary design and from manufactures that have been in the business for the last ten years. Acceptable non proprietary controller manufacturers and models are as follows:

Motion Control Engineering Model IMC VVVFAC

Elevator Controls Corp. Model V800 Type VF-CL PVF

Computerized Elevator Controls, Model Futura 2000

Equipment proposed must have a history of successful operation in similar size buildings and similar conditions for the last two (2) years.

    - Installer and Maintenance Qualifications:  Installer must be a licensed Elevator Contractor in the State of California.

      - Show evidence of successful experience in complete installation and maintenance of proposed manufacturer's elevator equipment for at least two (2) years.

      - Directly employ sufficient competent personnel within 50 miles of project to handle construction and maintenance duties.

      - Maintain local stock of parts adequate for replacement on permanent or emergency basis.

      - Respond to trouble calls within one hour.  30 minutes.

      - Offer the Owner agreement for continuing maintenance after expiration of maintenance period under this contract.

    - Elevator Cars and Entrances: One of the following or accepted equal:

      - The Elevator Manufacturer.

      - Hauenstein and Burmeister.

      - Tyler Elevator Products.

  - Requirements of Regulatory Agencies:

    - Codes:  In accordance with the latest applicable edition requirements of the following, at the date of contract award and as specified:

      - A.D.A.:  Americans with Disabilities Act.

      - CBC:  Title 24; California Building Codes.

      - CCR:  Titles 8; California Code of Regulations.

      - NEC:  National Electric Code.

      - UBC:  Uniform Building Code.

      - All local codes which govern.

    - Plans Review & Permits:  Provide all necessary drawings and documentation to obtain Permit to erect. Arrange and pay for inspections by governing authorities and obtain operating permits.

- SUBMITTALS:

  - Shop Drawings: Submit as required by the Architect or as specified.  The Architect reserves the right to require any details of any portion of the equipment.

    - Layouts:  Plan and section of hoistways, pits and machinery spaces; include impact and static loads imposed on building structure location of hoistway ventilation and required clearances around equipment.

    - Details:  Submit details of cabs, fixtures and entrances.

    - Data:  Indicate on layouts or separate data sheets; machine spaces heat release, power requirements, conduit runs outside of hoistways and machine rooms, car and counterweight roller guides, slide guides and car door operators.

  - Samples:  Provide samples of materials and finishes exposed to public view and additional, if specifically requested, 6 inch x 6 inch panels, 12 inch lengths or full size if smaller, as applicable.

  - Operating Instructions:  Submit manufacturer's literature describing system operations and special operations as specified.

- PRODUCT DELIVERY, STORAGE AND HANDLING:  Protect equipment during transportation, erection and construction.  Store under cover to prevent damage due to weather conditions.  Replace damaged equipment with new equipment or materials.

- SEQUENCING AND SCHEDULING:  Schedule and be responsible for coordinating related work with other trades to avoid omissions and delays in job progress.

- WARRANTY:  Provide special project warranty, signed by Contractor, Installer and Manufacturer, agreeing to replace/repair/restore defective materials and workmanship of elevator work which may develop within one (1) year from final date of completion and acceptance of the entire installation.  "Defective" is hereby defined to include, but not by way of limitation, operation or control system failures, performances below required minimums, excessive wear, unusual deterioration or aging of materials or finishes, unsafe conditions, the need for excessive maintenance, abnormal noise or vibration and similar unusual, unexpected and unsatisfactory conditions.

- ALTERNATES:

  - Alternate No. 1; Continuing Full Maintenance Contract:

    - Quote cost and submit manufacturer's proposal for full maintenance contract for a period of five (5) years after expiration of 12-month maintenance provided with this new installation.

    - Provide weekly examinations, lubrication and replacements in accordance with manufacturer’s standard practice.  Include a minimum of one and one-half hour per traction elevator per visit performing only preventative maintenance.  Any work required to perform repairs or answer trouble calls shall be in addition to the preventative maintenance hours.

    - Provide 24-hour emergency call back (entrapments) service and trouble call-backs after hours during normal working hours at no cost to Owner. Trouble call backs after hours shall be billable for the premium time portion only.

# PART 2 - PRODUCTS:

- DESCRIPTION OF SYSTEMS:

  - Elevator Nos. 1 & 2

    - Type:			Geared or Gearless Traction

    - Capacity:		2500 Pounds

    - Speed:		350 FPM

    - Stops:		9: B, G, 2-8

    - Openings:	          	9 all on same face

    - Travel:		As Shown

    - Control:		DC/SCR  or  AC/VVVF

    - Operation:		Duplex Group Operation

    - Machine Location:	Overhead with expansion joint

    - Controllers Location:	To west of machine room joint

    - Compensation:	Encapsulated Chain

    - Special Operations:

      - Independent Service

      - Fire Emergency Service

      - Standby Emerg. Power

      - Anti-Nuisance Service

      - Security Cameras

      - Remote monitoring

      - Floor passing voice signal

    - Car  Enclosure Type:	Passenger

      - Platform Size	7’-0” W by 5’-0” D by 8’-0”H

      - Inside Clear	6’-8” W by 4’-3” D by 7’-5” H

    - Signals and Fixtures	Design as Specified

      - Car Operating Panels	1 Per Car; Applied Type

      - Car Position Indicator	Integral with Car Operating Panel

      - Communication Sys.	Integral with Car Panel

      - Service Cabinet	Integral with Car Panel

      - Hall Pushbuttons	1 Riser

      - Hall Lanterns	All Floors

      - In-Car Lanterns	In nominated Jamb

      - Hall Pos. Indicators	All Floors

    - Passenger Entrance Type	Side Open, Single Speed

      - Size		3’-6” W by  7’-0” H

      - Frames

        - Main Floor	Stainless Steel

        - Typical Floors	Stainless Steel

      - Doors

        - Main Floor	Stainless Steel

        - Typical Floors	Stainless Steel

      - Sills

        - Main Floor	Aluminum

        - Typical Floors	Aluminum

    - Miscellaneous Items:

      - Disabled Access Requirements

      - Key Operated Hoistway Access

      - Earthquake Requirements Zone 4

      - Card Reader Provisions

      - Hoistway pit ladders

- MATERIALS:

  - Aluminum:  Alloy and temper best suited for anodizing finish specified.

  - Plywood:  PS-1, A-D exterior Grade Douglas Fir, fire retardant treated.

  - Sheet Steel:  ASTM A366, uncoated, pickled, free from defects.

  - Sound Deadener:  Fire retardant; spray, roller or adhesive applied; 3/16 inch thick.

  - Stainless Steel:  ASTM A167; type 302 or 304.

- FINISHES:

  - Exposed-to-View Surfaces.  Provide as follows unless otherwise specified.

    - Aluminum:  Clear anodized finish.

    - Sheet Steel:

      - Shop Prime:  Degrease clean of foreign substances and apply one coat of corrosion inhibiting primer compatible with finish paint selected.  Hoistway and car items visible to public shall be painted one additional coat of black paint.

      - Finish Paint:  Factory applied baked enamel or powder coat; color as selected.

    - Stainless Steel:

      - Plain:  Satin, No. 4 unless otherwise specified.

      - Patterned:  Rigidized Metal's 5WL and No. 7.DL, or RIMEX Metals equal.

    - Touch-Up:

      - Prime Surfaces:  Use same paint as factory for field touch-up.

      - Finish Painted Surfaces:  Refinish whole panel with shop prime and finish paint as specified above.

  - Non-Exposed-to-View Surfaces:  Degrease and shop paint manufacturer's standard corrosion inhibiting primer.

- AUTOMATIC OPERATION:

  - General Operation of Individual Elevators:

    - Provide a non-proprietary microprocessor-controlled dispatching system designed to monitor all types of traffic and sufficiently flexible so that it can be modified to accommodate changes in traffic patterns. Include hardware necessary to protect hoist motors, motor drives and door operators.  Software shall control group and simplex program operations.

    - The system shall continuously monitor the demand based on real time calculations to assign and reassign the elevators to handle the traffic in the most efficient manner.

    - Design the control system to accept reprogramming with no shutdown of system.

    - The system shall be flexible irrespective of the number of elevators in normal service.

    - Individual elevators shall operate on the basis of directional single cancellation collective automatic control in accordance with the following:

      - The control and indicating devices and supplementary service modes to be provided, together with the basic functioning of these and of power doors, door protective devices and similar items, are detailed in the relevant paragraphs of this specification.

      - Car and landing calls in each direction of travel shall be answered in the order in which required floors are approached by the car, provided that the call is registered sufficiently in advance of the car's arrival to permit a stop to be made.

      - Provide "anti-nuisance service" whereby all car calls will be cancelled if the load weighing device detects that an abnormal number of calls are registered given the number of passengers in the car.  System using false call answering to accomplish this is not acceptable.

    - Machine Room Monitor & Fault Diagnostic System:  Provide all hardware such as on board computer or laptop, keyboard and colored monitor to retrieve and display the following:

      - Diagnostic system shall be capable of determining faults most difficult to find.  It shall constantly monitor the condition of all car computers.  When variances occur from the normal mode, the change or fault shall be detected, the location of the elevator, time of day, number of times fault occurred, along with fault code message shall be stored on memory.  This information shall be retrievable to a minimum of the last 200 entries and shall be displayed on a colored 14 inch monitor in the machine room.

      - Car position and direction.

      - Registered car calls.

      - Registered hall calls.

      - Indication that a car is parked and is the next available car for dispatch.

      - Display for each car indicating load-weighing device is actuated, percent of load in car and bypassing hall calls.

      - Performance of hall call waiting analysis.

  - Group Automatic Operation; For Two or More Cars:

    - Provide an "on-demand" hall call response system that will continuously scan the hall calls and assign the closest elevator in time to respond to that call. The system shall be capable of reassigning the elevator if demand changes the real time calculation.

    - A car with no car calls registered arriving at a floor where both "up" and "down" hall calls are registered shall respond to the hall call in the direction of travel and illuminate the appropriate lantern.  If no car call is registered for that direction, the lantern shall be extinguished, the lantern for the other direction shall light and the car shall respond to the call in that direction.  The doors shall not close and reopen.

    - The system shall be capable of monitoring hall and car calls to monitor coincidental calls.  The cars will continuously scan the whole system to determine the closest elevator in time taking into account the coincidental car and hall call.

    - Other Required Features:

      - Should a car be delayed from leaving a floor for any reason, other car shall respond to the hall calls at that floor and shall be dispatched in a normal manner.

      - Provide each car with an adjustable load weighing device which will immediately dispatch cars and bypass hall calls when car is loaded to predetermined load.

    - General Program Adjustments:

      - After group of elevators have been placed in regular service and the building substantially occupied, the elevators shall be regularly observed under normal operating conditions and minor adjustments shall be made as found necessary to ensure that the elevators operate at maximum efficiency.

      - If zones are employed, arrangements shall be made in the control circuits of the elevators for the division between each zone to be raised or lowered if found necessary due to uneven distribution of traffic between the zones and/or staffing requirements.

- SPECIAL OPERATIONS:

  - Inspection Operation:  Provide key-operated hoistway access device and car top operating device.  Key switches shall be mounted in door frames with only ferrule exposed at terminal landings.

  - Independent Service:  Independent service operation shall be provided so that, by means of a switch located in the car service cabinet, the car can be removed from automatic operation and be operated by an attendant.  The attendant shall have full control of the opening and closing of car doors, starting, stopping and direction of car travel.  The car shall respond to car buttons only. The hall signals for the car on independent service shall not operate.

  - Operation Under Fire or Other Emergency Conditions:  Provide special emergency service to comply with CCR Title 8 and local codes having jurisdiction.  Provide Phase 1 recall switch at Main Floor Elevator Lobby and Fire Control Life Safety Room.  Interlock recall switches to prevent simultaneous activation.  Key switches at main floor shall be integrated in hall button station with engraved instructions.

  - Operation Under Earthquake Conditions:  Provide seismic operation in accordance with ASME A17.1 and CCR Title 8.  Provide a dual ring and string, continuously monitoring type counterweight displacement device for each counterweight with rings mounted on diagonal corners of frame. Provide a seismic switch device measuring both horizontal and vertical accelerations for each group of elevators located per manufacturer's recommendations.

    - Upon activation of displacement device or seismic switch, elevators that are in motion shall either slow to a speed not greater than 150 FPM and proceed to next floor in direction of travel, stop and open doors, or, stop and then proceed to next floor at a speed not greater than 150 FPM in a direction away from the counterweight, stop and open doors.

  - Operation Under Standby Power System:

    - General:  The Standby power system is sized to operate one elevator in each group simultaneously.  Elevators shall be grouped as follows:

Group 1 = Elevators Nos. 1 & 2

      - When normal power fails and standby power becomes available, a signal will be given to the controllers, both elevators will shut down, and all car lights, etc., will be extinguished.

      - When emergency power comes onto the line, power for lighting car fan and alarm bell shall be automatically transferred and cars on automatic operation shall be sequentially returned one at a time to the main floor.

      - After both cars are parked at main floor, one car shall resume normal operation.

      - Provide behind a locked cabinet at the Ground floor a selector switch to permit the selection of elevators to run on emergency power, switch shall be left in the Auto position and marked. Provide illuminated jewel to show which elevator is operating on emergency power. Provide manual selection of desired elevator to operate on emergency power.

      - When normal power fails and emergency power is used, or when normal power is restored, the Elevator Manufacturer shall provide all circuitry necessary, including time delay or auxiliary relays required to accomplish safe, continuous elevator operation.  The cars will start in sequence, not simultaneously; allow 10 seconds between starts.

      - Fire service and derailment devices shall be operable when system is on emergency power operation.

  - Remote Monitoring:  Provide a monitor, computer tower and keyboard in First Floor Front Desk for staff to view status of elevators and capable to control operation of the elevators, by enable and disable car call buttons as follows:

    - Function which locks out cars so that all car buttons are inoperative except the main floor.

    - Function which locks out any selected car button for all each elevator serving any selected floor.

    - Remote Monitoring security operations can be overridden by cars on independent, any special emergency service or card reader.

- CAR DOOR OPERATION:

  - Passenger Type Horizontal Sliding:

    - Door Operator: Provide heavy-duty master type operators with direct current motor mounted on structural support independent of car enclosure.  Provide closed-loop door operators, equal to Otis ATX-400, Thyssen HD93, GAL-MOVFR or Schindler QKS-14   For two-speed center-opening doors, arrange operator linkage to drive both door panels.

      - Provide door times available as specified under "Design Criteria".

      - Car and hoistway doors shall open and close simultaneously, quietly and smoothly; door movement shall be cushioned at both limits of travel.  Door operation shall not cause cars to move appreciably.

      - Door hold open times shall be readily and independently adjustable when car stops for a car or hall call.  Main floor door hold times shall be adjustable independent of other floors.

    - Hangers and Tracks:  Sheave type with two-point suspension.  Steel sheaves with flanged groove and resilient sound-absorbing tires.  Minimum 2-1/2 inch diameter for hoistway, 3 inch for car.  Manufacturer's heavy-duty tracks and ball or roller bearing with adjustable upthrusts.

  - Door Protection; Passenger Type:

    - Electronic Scanning Type:

      - Provide a door protective system which does not rely on physical contact with a person or object to inhibit door movement or initiate door reversal.  Provide system equal to the Otis "Lambda III", Techtonics 3D or Janus "Panaforty" 3D. The module shall extend to the full height of the car door

      - The system shall be able to detect a 1-inch diameter rod introduced at any position within the door movement and between the height of 2 inches and 63 inches above sill level.

      - Detection of intrusion into the protected area shall cause the doors, if fully open, to be held in the open position and, if closing, to reverse to fully open position.

      - If doors are prevented from closing for an adjustable period of 15 to 45 seconds or upon activation of Fire Emergency Service, they shall proceed to close at reduced speed and a loud buzzer shall sound.  Door closing force shall not exceed 2-1/2 ft.-lbs. when door re-opening device is not in operation.

      - For side-opening doors, the detector for the strike jamb side shall be recessed, flush with strike jamb.

- SIGNALS AND OPERATING FIXTURES:

  - General:  Provide signals and fixtures as shown and specified.  Location and arrangement of fixtures shall comply with handicap requirements.

    - Passenger Car Buttons:  Provide vandal-resistant stainless steel minimum 1 inch diameter mechanical buttons, raised 1/8 inch from surrounding surface with square shoulders and integral illumination equal to Adams, EPCO or GAL fixtures.  Operation of car or hall button shall cause button to illuminate.  Response of car to car call or hall button shall cause corresponding button to extinguish and have detectable motion.

    - Passenger Hall Buttons:  Provide vandal-resistant 1 inch diameter mechanical buttons, raised 1/8 inch from surrounding surface with square shoulders and full face of button to illuminate when registered equal to Adams, EPCO or Innovation fixtures. Operation of car or hall button shall cause button to illuminate.  Response of car to hall or car call shall cause corresponding button to extinguish and have detectable motion.

    - Switches: Toggle type typically in service cabinet or key operated where noted on car panel.

    - Faceplates:  Provide of material and finish as indicated and specified; 1/8 inch minimum thickness with sharp edges relieved. Provide stainless steel for all faceplates.

    - Fastenings:  Provide with flush tamper-proof screws of material and finish matching faceplates countersunk into the faceplates.

    - Cabinets:  Provide with pulls, concealed hinges and doors mounted flush with hairline joints to adjacent surface.

    - Arrangement:  Arrangement of fixtures shall generally conform to that specified, but components may be rearranged, if desired, subject to Architect's approval.

    - Engraving:  Of size indicated; color backfill with epoxy paint in contrasting color as selected.

    - Lamps:  Miniature LED type.

    - Audible Chimes:  Electronic adjustable audible chimes; bell type gong not acceptable.

    - Provide floor passing signal of the adjustable electronic audible chime type.

    - Tactile Markings: Provide raised Braille and alpha characters, numerals or symbols to the left of operating buttons and devices used by the public. Indications may be engraved directly on faceplates or separate plates flush mounted with hairline joints and concealed mechanical fasteners.  Plates shall be of same size and shape as buttons.  Raised characters shall be white on a black background with Braille designation directly below the character.

  - Car Operating Panels:

    - General:  Provide buttons numbered to conform to floors served and the following:

      - Locate top operating button at 48 inches above floor; maximum 54 inches when required.

      - Locate emergency stop and illuminated alarm button in bottom row at 35 inches above floor.  Wire emergency stop to ring alarm bell.

      - Provide "Door Open” and "Door Close" & alarm buttons of the same design located above emergency stop key switch.

      - Engrave main panel with capacity, number of passengers, elevator number in 1/4-inch letters and No Smoking in 1 inch letters.  All other signage required by elevator and local codes shall be engraved in type as directed by Owner's representative.

      - Provide fire emergency key switch, engraved instructions and call cancel button with audible/visual signals located per code. Provide fire department phone jack located below emergency stop and alarm.                .

    - Applied Type:  Integrate cabinets, buttons and engraving into hinge single piece faceplate mounted to front return panel.

  - Car Position Indicators:  Provide car position indicators with indications corresponding to floor designations with matching direction arrows and floor passing chimes. Provide 1-1/2 inch digital type direct readout indicator with minimum one-inch high indications mounted integral with each car operating panel at 6’-6” above floor.

  - Service Cabinet:  Provide cabinet door with a security lock and concealed hinge as an integral part of car operating panel mounted with flush hairline joints.  Cabinet door shall be provided with a flush glazed window of required size to hold elevator operating permit.  Inspection key switch combination to be different to all other key combinations. Service cabinet shall contain the following:

    - Independent service key switch.

    - Two-speed ventilation three position switch.

    - Light switch and dimmer as applicable.

    - Inspection key switch, key operated.

    - Duplex convenience outlet.

    - Buzzers as required.

    - Test switch for emergency car lighting.

  - Emergency Communication Device:  Provide a complete communication system in compliance with A.D.A. regulations consisting of a combination speaker/microphone, amplifier, automatic dialer, pushbutton to activate system and acknowledgement lights.  Mount behind a pattern of holes as selected as an integral part of car operating panel. Automatic dialer shall be programmed as directed by Owner.

  - In-Car Voice Announcement: Provide voice announcement function which will sound when car passes a floor or is stopping at a floor. The audible level shall be adjustable between 20 to 70 decibels.

  - Hall Button Fixtures: Each fixture shall contain buttons which light to indicate hall call registration and extinguish when call is answered.  Engrave fire exiting instructions on faceplates.

    - Provide rectangular shaped faceplates fabricated from stainless steel No. 4 finish.

  - Hall Lanterns:  Provide with single chime for up and double chime for down direction.  Lantern illuminates white for up and red for down.  As car approaches floor, lantern shall illuminate and chime approximately 4 seconds prior to doors opening to indicate next direction of travel.

    - Provide at all floors, manufacturer's standard 2-1/2 inch equilateral triangular lenses without faceplates in a stainless steel No. 4 finish faceplate.

  - Hall Position Indicators:  Provide Digital type with 2-inch high indications in a stainless steel    faceplate. Combine with hall lanterns fixture above.

- WIRING:

  - General:  Provide all necessary wiring with 15% or a minimum of four spares between cars and controllers and to all remote control stations.  Furnish shielded wires in cables for all communications, cameras, and speakers. Include two additional pairs of shielded spares for each car.

  - Traveling Cables:  Use minimum number of traveling cables with flame retarding and moisture resisting covers.  Include shielded wires and spares as noted above.  Cord thoroughly and protect cables from rubbing against hoistways or car items.  Provide with steel cable core and properly anchored to relieve strain on individual conductors.

  - Work Light and Convenience Outlet:  Provide two work lights on top of car with wire lamp guard. Provide dual convenience outlet on car top with GFI protection.

  - Stop Switch:  Provide in each pit and on top of car.

  - Alarm Gong:  Six-inch size, 110 volt.  Provide on top of each car and one per group inside of hoistway at main landing to be actuated by corresponding alarm button or emergency stop switch.

  - Auxiliary Disconnect Switches:  Provide as required in remote controller rooms or at remote equipment not in view of mainline switches; include all wiring and conduit.

  - Coaxial Circuit:  Provide for cameras in each elevator.  Run from elevator car to machine room location.

  - Building Expansion Joint: Provide flexible conduit connections in hoistway and machine room to allow for the 15 inch expansion joint between the new hoistways and section of the machine room.

- CAR ENCLOSURES:

  - General:  Fabricate finish work smooth and free from warps, buckles, squeaks and rattles; joints lightproof.  Car shall be sound isolated from car frame.  Apply outside of car with 3/16-inch thick fire rated sound deadener material.  No visible fastenings, except as indicated.

  - Passenger Cars;

    - Steel Shell:  Fabricate walls of 14-gauge sheet steel from floor to canopy.  Canopy 12 gauge reinforced. Paint shell in color as selected by Owner's Representative.

    - Emergency Exit:  Top of car per code.

    - Ventilation:  Three-speed squirrel cage exhaust blower, Morrison model OE or equal, with 3/8 inch thick sound isolation mounting onto canopy.  Provide natural concealed vents above base and ceiling as required by code.

    - Car Doors:  Fabricate from 16-gauge sheet steel on front and back of each panel sufficiently reinforced with steel to insure rigidity and sound deadened. Provide two guides per panel located one inch from each end.  Provide full length neoprene astragals.  Mount doors on structural header, not on car enclosure.  Finish car side with patterned stainless steel 5WL design and return the material finish 1/2 inch around edge of doors.

    - Protective Pads:  Provide one set of heavy quilted fire rated protection pads for each size of elevator.  Total (1) one set of pads per elevator cab required.  Pads shall cover all walls with cut-out sections for car operating panels.  Provide pads with rubber-coated 'J' type hooks sewn into top of pad for mounting to top of return jamb above the removable panels.

    - Front Return Panels:  Provide full integral fixed type front return panels fabricated from 14 gauge stainless steel 5WL pattern.

    - Interior Panels:  Provide removable panels of 3/4-inch particle board core with balance sheet; align joints with ceiling grid.  Face and edge with stainless steel pattern No. 7.DL material.

    - Base and Metal Trim:  Provide base below removable panels, vertical joints between panels and other metal fabricated from stainless steel No.4 finish.

    - Ceiling and Lighting:  Provide a suspended ceiling fabricated from stainless steel No. 4        finish applied to particle board as shown.  Provide six (6) equally spaced low loss fluorescent bulbs with electronic ballast, down lights in ceiling as shown. With dimmer switch controls located in car service cabinet.  Install drop ceiling at seven (7) inches below canopy.

    - Handrail:  Provide handrail on rear wall.  Fabricate from 1-1/2 inch diameter stainless steel  with matching brackets.  Securely attached to car shell with concealed fasteners.

    - Sills:  Provide extruded aluminum threshold plate.  Mount with concealed mechanical fasteners.  Allow ½ inch for installation of finish tile flooring.

    - Finish Flooring: Provided by others.  Allow for 3/8 inch tile flooring on soft set material as selected by Owner's Representative.

  - Emergency Lighting:  Provide an emergency car lighting unit mounted on top of car, battery driven and self-rechargeable. Upon outage of normal power the unit shall, within 5 seconds, light two lamps as part of normal car lighting or separate lights mounted above drop ceiling and above the car operating panel.  The unit shall have sufficient capacity to keep the lights in continuous operation for four hours and also the alarm bell for one hour.  Provide a readily accessible means for testing the unit in service cabinet.  Light fixtures mounted in car front returns or operating panels are not acceptable.

- HOISTWAY ENTRANCES; PASSENGER TYPE:

  - General:  Fabricate finish work smooth with flush surfaces and free from warps and buckles.  Entrance assemblies shall bear 1-1/2 hour U.L. rating.  Provide entrances of size and type as scheduled.

  - Struts and Closer Angles:  As required for entrance installation and door closer mechanism.  Use full length struts. Hanger headers, minimum 3/16 inch material extending from strut to strut.

  - Dust and Hanger Covers:  Provide as required of minimum 16 gauge sheet steel.  Provide hanger cover plates extending full length of door track. Paint black.

  - Fascia, Toe and Head Guards: Minimum 16 gauge sheet steel; reinforce fascia.  Paint black.  Provide blind fascia in express zones or for reverse openings as required.

  - Sills:  Extruded sills with non-slip surfaces and grooves suitable for guides.  Extend strut to strut and mount without exposed screws.  Provide all support angles and levelers for a complete installation.  Sill material as scheduled.

  - Frames:  Fabricate from 14-gauge material with side jambs in one continuous piece from sill to head section.  Head and jamb flush bolted with hairline joint to provide unit frames with neat appearance from corridor side. Material and finish of frames as scheduled.

  - Doors:  Fabricate from 16 gauge material sufficiently reinforced with steel to insure rigidity and sound deadened.  Provide two guides per panel which will remain engaged in sill if guiding member is destroyed.  Provide full length neoprene astragals on leading edge and non-vision wings of material and finish to match doors. There shall be no keyholes in the door unless required by governing authority.  Corridor side of door panel material and finish as scheduled.  Return finish a minimum of 1/2 inch around edges of door.

  - Tactile Markings:  Provide raised Braille and alpha characters, numerals or symbols similar to those for car stations of size required by governing authority. Locate on each entrance jamb at 60 inches above floor indicating floor designation.  Material and finish of plates shall have contrasting background and mounting means similar to those on car panels.  Braille designation shall be to the left of the raised character.

- TRACTION ELEVATOR EQUIPMENT:

  - Design Criteria:

    - Performance:

      - Contract Speed:  Maximum five percent (5%) speed variation under any loading condition in either direction.

      - Motion Time:  Brake release to brake set as measured in both directions for a typical, 11 feet, single floor run under any loading condition.  After make-up of hoistway door interlock, initiate movement of car within 0.3 second for geared or gearless elevators.

        - Elevator Nos.  1& 2 :     5.5   seconds.

      - Door Open Times:

        - Elevator Nos.   1&2:       1.8  seconds.

      - Door Close Times:  Minimum, without exceeding kinetic energy and closing force, allowed by code.

      - Door Dwell Times:  Comply with A.D.A. formula and provide separate adjustable timers with initial settings as follows:

        - Main Lobby Hall Call:  5.0 seconds.

        - Upper Lobby Hall Call:  5.0 seconds

        - Car Call:  5.0 seconds.

        - Interruption of Door Protective Device:  Reduce dwell to 1.0 second after all ADA requirements have been met.

      - Leveling:  Within 1/4 inch under any loading condition.  Level into floor at all times, do not overrun floor and level back.

      - Releveling:  Provide smooth and accurate releveling required due to cable stretch.

    - Operating Qualities:  Architect and his Representative will judge riding qualities of cars and enforce the following requirements. Make all necessary adjustments.

      - Acceleration and Deceleration: Starting and stopping shall be smooth and comfortable, without obvious steps of acceleration. Slowdown, stopping and leveling shall be without jars or bumps.  Stopping upon operation of emergency stop switch shall be rapid but not violent.

        - Vertical Acceleration:  Maximum 4 ft. per second squared.  Maximum jerk 8 ft. per second cubed.

        - Horizontal Acceleration:  Maximum 10 mg peak-to-peak measured at full speed for full travel in both directions.

      - Full Speed Riding:  Free from vibration and sway.

    - Motor Control:

      - Equipment:  Capable of operating at plus or minus ten percent of normal feeder voltage and plus or minus three percent of feeder frequency without damage or interruption of elevator service.

      - Control System:  Closed loop feedback control incorporating positional and velocity selector system that is capable of operating continuously at contract speed and load for one hour without exceeding 50 degrees Centigrade from ambient machine room temperature.  Design system to not adversely affect stability of voltage and frequency controls of emergency generator set or loads connected to emergency power bus during standby power operation.

      - Car Load Sensing:

        - The control system shall sense the actual load condition of the elevator prior to any movement of the elevators.  The start/acceleration pattern shall be adjusted to reflect the car load to achieve a smooth start/acceleration under all load conditions and location in the hoistway.

        - Provide load sensing devices that utilize crosshead deflection or hoist rope pressure.  System shall be accurate within 100 pounds and stable over extended periods.

        - Systems using pre-torquing of the D.C. motor armature are acceptable; variable voltage control of the brake energization is not acceptable.

    - Sound Control:

      - Vibration:  Sound isolate machines and motor drives from beams and building structure to prevent objectionable noise and vibration transmission to occupied building spaces.

      - Airborne Noise:  Maximum acoustical output level of:

        - 65 dba measured in machine room.

        - 60 dba measured in elevator cars during all sequences of operation.

        - 50 dba measured in elevator lobbies.

  - Guide Rails:

    - Size:  Standard steel tees with backs machined for splice plates.  Extend rails full depth of pits and mounted to continuous pit channels with adjustment bolts to allow for building settlement.  Minimum weight in pounds per foot shall be            pounds for car and           pounds for counterweight.

      - Elevators Nos.  1&2 :   Car and Counterweight rails  = 15 #

    - Installation:  Drawings indicate basic hoistway framing and special supports for rail brackets.  All additional supports and/or rail backing required shall be provided by the Elevator Contractor.  Install plumb within 1/16 inch. File joints smooth.

  - Guide Shoes:

    - Roller Guides:  Roller type with neoprene tires, minimum 3/4 inch wide and fully adjustable spring loaded to provide continuous contact with rail surfaces.  Balance car to insure equal guide shoe pressure on all wheels and not exceed manufacturer's recommendations.

      - Size: Nominal roller diameters shall be six (6) inch for car and four (4) inch for counterweight.

  - Hoist and Governor Ropes:  Size and number to insure proper wearing qualities; minimum eight strands wound around hemp core.  Pre-formed cables will be permitted.  Minimum size:  Hoist ropes, 1/2 inch, governor ropes, 3/8 inch.

  - Buffers:  Mount on continuous pit channels with required blocking and supports.  For deep walk-in pits, provide platforms with access ladders for servicing car buffers as acceptable to Elevator Code authorities.

    - Oil Type:  Oil buffers, spring return type with switches.  Pistons shall be fully protected by bluing or canvas covers.

  - Counterweights:  Sectional metallic weights securely fastened in structural frame.  Frame to be designed to maintain structural integrity without bending upon activation of a seismic force of .5 g.  Weight shall occupy a minimum of two-thirds the height of the frame.

  - Safeties:  Flexible guide clamp type mounted on underside of car frame.

  - Governor:  Centrifugal speed type to be located over hoistway in machine room or in pit with protective covering over sheave, jaws and exposed gears.  Pit tail sheave frame shall be ratchet or tension type held under 200 pounds tension.

  - Car Frame and Platform:

    - Passenger Elevators:  Steel frame with steel or double wood floor; isolate platform from car frame by rubber pads and provided with jacking bolts for pad replacement.

  - Traction Machines:

    - General:  Provide machines with heavy structural steel bedplates and motors rated for 30 minute with maximum 50 degree Centigrade rise or better.

    - Gearless Traction: Provide manufacturer's standard double wrap or single wrap traction machines as approved with 1:1 or 2:1 roping.

    - Geared Traction: Provide manufacturer's standard single wrap traction worm-gear machines as approved with 1:1 roping and undercut sheave grooves.  Where machines are mounted adjacent to hoistways and where deflector sheaves are required for proper rope deflection, the deflector sheaves shall be an integral part of the machine bedplate.

  - Controller:  Provide the specified non proprietary manufactured controllers. As standard with approved manufacturer; overload relays in three legs of power circuit and in loop circuit; cabinets with NEMA-1 enclosures and doors arranged with locks or mechanical latches. Provide permanently marked symbols or letters identical to those on wiring diagrams adjacent to each component.

    - The controller wiring shall be carried out in a neat and workmanlike manner in accordance with relevant requirements of National Electric Code.

    - All external connections to the equipment on each controller shall be made by means of approved cable thimbles and/or solderless cable lugs, depending on the current to be carried.

    - Condenser activated or dash pot timers, motors or incandescent globes for dampening acceleration and deceleration steps are unacceptable.

    - Main contactors or starter switches shall be horsepower rated and are not to be mounted directly to the steel cabinets, to ensure quiet operation of controllers.

    - Where SCR drive control is provided, noise suppression chokes are to be connected in the A.C. feeders to the SCR drive and for the D.C. feeders to the hoist motor and located within the base of the controller. These chokes are to be mounted in an isolated manner to prevent electrical vibration noise to the steel cabinet.

    - The controllers must be properly shielded from line feeder pollution.

  - Power Conversion and Regulation Unit:

    - General:  Variable Voltage Variable Frequency (VVVF/AC) or Solid State (SCR/DC) control optional with manufacturer.

      - All circuitry shall be as approved by the enforcing code.  Operation shall be quiet and the performance standards herein specified shall be provided.

      - Design system to control starting and stopping and to prevent damage to motor from overload or excess current and to automatically disconnect power supply.  Apply brake and bring car to rest in event of power failure or safety device operation.

      - Controllers shall not have failure modes which results in full power being applied to drive machine operation in event of phase reversal, phase failure or low voltage which might result in elevator malfunction.

    - Solid State Control (SCR):

      - Provide smooth acceleration and deceleration by variable voltage applied to hoisting motor and by dynamic braking before brake application.

      - Failure of any static control device, speed measuring circuit or speed pattern generating circuit to operate as intended or occurrence of single accidental ground or short circuit shall not permit car to start or run if any hoistway door or gate is open or unlocked.

      - Provide coordinated fault protection which protects entire power circuit and power semi-conductors against short circuit conditions; protects against limited faults arising from partial grounds, partial shorts in motor armature, or in power unit itself; protects drive motor against sustained overloads; and provides semi-conductor transient and incoming line phase sequence protection.

      - Protects building system power line against line voltage transients by providing each elevator drive with isolation transformer and devices to limit distortion to not more than 4% RMS of base 60 Hz line voltage, with frequencies above 600 Hz attenuated at minimum of 12 db per octave.  Measure voltage distortion requirements at secondary of building system transformer used to provide power to elevator system.

    - Variable Voltage Variable Frequency (VVVF):

      - Provide system to convert 3 phase, 60 Hz, A.C. building power supply to a fixed D.C. voltage and then invert from D.C. voltage to a variable voltage, variable frequency, distortion-free, smooth A.C. current output to the A.C. hoist motor.

      - Motor speed shall be controlled by varying the frequency input to the motor; torque shall be controlled by varying the voltage to the motor.

      - System shall be provided with necessary devices to insure quiet operation not exceeding noise level specified in "Design Criteria" and to protect building system power line against line voltage transients.

  - Machine Beams and Sheaves:  Provide all structural steel machine and sheave beams with dead end hitch plates, bearing plates, anchors and blocking as required to support equipment.  Secondary, overhead and deflecting sheaves with roller bearings and means for lubricating bearings from machine rooms as required where secondary levels are not provided.

  - Selector:

    - The system shall utilize a device to establish incremental car position to an accuracy of .1875 inches or better using quadrature signal for the entire length of the hoistway.  Absolute floor number encoding with parity shall be provided at each floor in order to establish exact floor position to the computer.  The system shall not require movement to a terminal landing for the purpose of finding the correct car position.

    - The system shall utilize an automatic two-way leveling device to control the leveling of the car to within 1/4 inch above or below the landing sill.  Over travel, under travel, or rope stretch must be compensated and the car brought level to the landing sill.

    - The individual car controller shall be capable of learning the position of each floor in the building to an accuracy of .1875 inches.

    - The individual car controller shall have the software program that uses mathematical methods to create an idealized optimum velocity profile of the car travel from any floor to any other floor providing a smooth and stepless elevator ride.  All the system motion parameters (such as jerk, acceleration, deceleration rates etc.) shall be field programmable with parametric limitations for the system dynamics, and be stored on EPROM as non-volatile memory.

    - The drive control system shall utilize the optimized velocity profile in a dual-loop feedback system based on car position and speed.  A velocity feedback device shall permit continuous comparison of car speed with the calculated velocity profile to provide accurate control of the acceleration and deceleration, right to the final stop without discomfort, regardless of direction of travel or load in the car.

    - The individual car controller shall have an independent safety processor that monitors the speed of the car and creates a phantom speed contour near the terminal landing, so that the car would not be capable of traveling faster than the phantom speed contour.  This processor should work independently of any other logic or motion control processors in the system.

    - The controller shall utilize a solid state drive unit using solid state power devices to control the motor field and machine brake.

    - The controller shall provide the required electrical operation of the elevator control system including the automatic application of the brake, which shall bring the car to rest upon failure of power.

    - In addition, the power control shall be arranged to continuously monitor the actual elevator speed signal from the velocity transducer and to compare it with intended speed signal to verify proper and safe operation of the elevator.

    - During operation of the elevator with overhauling load (empty car up or loaded car down), precision speed control shall be obtained by the regulation system utilized in the power control.  The automatic leveling zone shall not extend more than 12 inches above or below the landing level nor shall the doors begin to open until the car is within 12 inches of the landing.  In addition, the inner leveling zone shall extend not more than 3 inches above or below the landing. The car shall not move if it stops outside the inner leveling zone unless the doors are fully closed.

    - All power feed lines to the brake shall be opened by an electro-mechanical switch.  A single ground, short circuit, or solid state control failure shall not prevent the application of the brake in the intended manner.  Systems that do not apply the brake when the car stops at a landing are not acceptable.

    - A motor field current sensing means shall be provided which shall cause electric power to be removed from the armature and brake unless the direct current flowing in the shunt field of the motor is sufficient to prevent over speeding of the motor.

  - Pit Ladders:

1.	Provide code complying safety ladders for access to elevator pit of each elevator, securely attached to concrete pit and wall between hoistways.

  - Compensation:

    - Chain Type: Provide encapsulated chain equal to Quiet Link, Whisperflex or equal with pivoted compensating sheave having a nominal diameter of 25 inches to maintain loop, limit horizontal movement and prevent rubbing of chain on elevator equipment or hoistway items.

# PART 3 - EXECUTION

- GENERAL:

  - Bidding Documents:  Bidders shall examine architectural, structural, electrical and mechanical plans and specifications.  Any discrepancies which affect the elevator work or conditions adverse to the bidder's equipment shall be brought to Architect's attention at least seven (7) days prior to the bid date.  If no discrepancies are presented, changes required to accommodate bidders equipment become the responsibility and cost of the Elevator Contractor.

- PREPARATION:

  - Field Measurements:  Field verify dimensions before proceeding with the work.  Coordinate related work by other trades. Verify the following to be acceptable for installation of elevators.

    - Hoistway has been correctly sized and otherwise properly prepared.

    - Equipment supports are satisfactory.

    - Electrical rough-ins are correct.

    - Do not begin installation until unsatisfactory conditions have been corrected.

- INSTALLATION:

  - General:  Install per manufacturer's requirements, those of regulatory agencies and as specified.

  - Welded Construction:  Provide welded connections for installation of elevator work where bolted connections are not required for subsequent removal or for normal operation, adjustments, inspection, maintenance and replacement of worn parts. Comply with AWS standards for workmanship and for qualifications of welding operators.

  - Sound Isolation: Mount rotating and vibrating elevator equipment and components on vibration-absorption mounts, designed to effectively prevent transmission of vibrations to structure and thereby, eliminate sources of structure-borne noise from elevator system.

  - Lubricate operating parts of systems, including ropes, as recommended by manufacturer.

  - Alignment:  Coordinate installation of hoistway entrances with installation of elevator guide rails, for accurate alignment of entrances with cars.  Where possible, delay final adjustment of sills and doors until car is operable in shaft.  Reduce clearances to minimum, safe workable dimensions at each landing.

  - Erect guide rails plumb and parallel with maximum deviation of 1/16 inch.  Anchorage of guide rails shall not compromise waterproofing.  Do not bottom rails on pit floor.

  - Grout sills with non-staining, non-shrink grout.  Set units accurately aligned with finished floor at landings.

  - Graphics:  Provide graphics visible to public as selected by Architect.

  - Manufacturer's Nameplates:  Manufacturer's nameplates, trademarks or logos not permitted on surfaces visible to public.

- TEMPORARY ELEVATOR USE DURING CONSTRUCTION:

  - General:  Should the General Contractor require the use of any elevator during construction, Contractor shall request approval of such use from Owner and if approved make arrangements directly with the Elevator Contractor, coordinate temporary facilities and pay all costs associated with the protection, operation and use of elevators.

  - Maintenance: Elevators shall be maintained on a regular basis during the temporary construction use.  A minimum of two hours per week per elevator shall be spent on examination, lubrication, adjusting and cleaning the elevator equipment.

  - Damage:  The Owner is entitled to receive new elevator equipment upon final acceptance of the entire project.  The Owner or Owner's designated representative will thoroughly examine all elevator equipment upon completion of temporary use and provide a punch-list outlining items that must be repaired or replaced to ensure the equipment is in new condition.  Final acceptance and payment will not be made until all items have been satisfactorily completed.

  - Schedule: Sufficient time must be allowed to prepare and adjust temporary elevators so that the entire elevator installation is ready for final acceptance.

- TEMPORARY ACCEPTANCE AND USE BY OWNER:

  - When an elevator is near completion and declared ready for service, before completion of other elevators, Owner agrees to accept elevator and place it into automatic service.

  - The elevator must be tested and inspected by regulatory agencies and a permit to operate issued.

  - A walk-through examination will be performed in the presence of Owner, Architect, General Contractor and Elevator Contractor to determine present condition of elevator.

  - The Owner agrees to sign or cause the General Contractor to sign a temporary acceptance form that is mutually agreeable to all parties.

  - During this temporary acceptance period, the Owner agrees to pay or cause the General Contractor to pay an agreed amount per day per elevator for regular maintenance.  The cost for this maintenance per elevator, per day, shall be stated in the Elevator Contractor's bid.

  - The guarantee and full maintenance period will be effective upon final acceptance of the entire installation.

- FIELD QUALITY CONTROL:

  - Regulatory Agencies Inspection:  Upon completion of each elevator, Contractor shall provide instruments, weights and personnel to conduct test required by regulatory agencies and the Owner’s Representative. The Contractor shall submit a complete report describing the results of the tests.

  - Examination and Testing:  When installation is ready for final acceptance, notify and assist Owner’s Representative witnessing the following tests and in making a walk-through review of entire installation to assure workmanship and equipment complies with contract documents.  Provide equipment to perform the following tests:

    - One hour heat and run test with full load in car.  Perform for one car of each duty.

      - Stop car at each floor in each direction for 30 minutes and then terminal stops for 30 minutes.

      - Provide well-shielded thermometers for motor and verify that temperatures do not exceed 50 degrees Centigrade above ambient.

      - Performance and leveling tests shall be made before and after heat and run test.

    - Check and verify operation of all safety features and special operations.

      - Measure horizontal acceleration.

      - Measure acoustical output levels in machine room, lobbies and cars.

      - Measure voltage transients and harmonics feedback into building electrical system.

  - Correction:  Make corrections to defects or discrepancies at no cost to Owner.  Should discrepancies be such that re-examination and retesting is required, all costs including those of Owner's representative fees shall be paid for by the Elevator Contractor.

  - Final Acceptance: Final acceptance of the  installation will be made only after all corrections are complete, final submittals and certificates received and the Owner is satisfied and the installation is complete in all respects. Final payment will not be made until the above is completed.

- INSTRUCTIONS:  Instruct Owner's personnel in proper use of each system.

- MAINTENANCE:

  - General:  Provide complete continuing maintenance on entire elevator equipment during regular working hours on regular working days for a period of 12 months after filing Notice of Completion.

  - Examination:  Include systematic examination, adjustment, and lubrication of elevator equipment whenever required and replacement of defective parts with parts of same manufacture as required for proper operation.  Contractor not responsible for repairs to car enclosures, door panels, frames, sills or platform flooring resulting from normal usage or misuse, accidents and negligence for which Contractor is not responsible.  Examinations shall be performed twice monthly expending a minimum of one and one-half hour per unit per visit performing adjustments and preventative maintenance service.

  - Performance Standards:

    - Maintain the performance standard set forth in this Specification and maintain correct operation of the dispatching system.

    - Maintain smooth starting and stopping, smooth riding qualities and accurate leveling at all times.

  - Call-Backs:  In event of failures, provide 24 hour call-back service at no additional cost to Owner.

  - Elevator Shutdowns:

    - Should any elevator become inoperative, repair within 24 hours of notification of such failure.  Breakdown of major components shall be completed and service restored within 72 hours.

    - Failure to comply with above, Owner may order the work done by other contractors at the Contractor's expense.

    - Devices repaired or replaced by others shall, nevertheless, be provided with maintenance by the Contractor who shall become completely responsible for correct operation of such devices for lifetime of this contract.

  - Follow-Up Tests:  Test all safety devices and emergency operations at six (6) month intervals or oftener and submit written report on each test.  Make tests at times which do not interfere with building operation.

  - Maintenance Materials:

    - Expendable Parts:  The Elevator Contractor shall provide a metal cabinet in machine room on project premises containing the following expendable parts required for prompt replacement. Parts used for routine maintenance shall be replenished and stored in machine room to ensure an adequate supply is available. Parts and cabinet shall become Owner's property and not removed upon expiration of maintenance period.

      - One set starter contacts and coils.

      - Two resistors of each type installed.

      - One set hanger sheaves for car and hoistway doors.

      - Two relays and relay bases of each type installed.

      - Twenty-four lamps of each type installed.

      - Car and hall buttons with identical graphics installed; six for manufacturer's standard buttons, one of each type for special buttons.

      - Twelve fuses of each type installed.

      - One set motor brushes of each type installed.

      - Any other parts required for prompt replacement.

      - Lubricants and cleaners of all types used for maintenance.

    - Replacement Parts:  Keep the following parts in a warehouse within 50 miles of the project premises.

      - One door operator motor of each type used.

      - Transformers of each type installed.

      - Two complete door interlocks.

      - Parts for motor drive units.

      - Parts for door protective devices.

      - Such other parts as are needed to insure prompt replacement in event of elevator shutdown such as spare control boards for computer operated systems.

  - Maintenance Data:  After completion and prior to final acceptance, submit three sets of complete and accurate maintenance data specific for each elevator.  Final payment will not be made until received.

    - Manuals:  Describe proper use and maintenance of equipment, lubrication points, types of lubricants used and frequency of lubricant application.

    - Parts Catalogs:  Complete listing of all parts of equipment and components used in the installation.

    - Wiring Diagrams:  One laminated set mounted in machine room, one reproducible mylar set and one blue line set delivered to Owner.  Wiring diagrams shall be as built, specific for this installation, and reference identification on drawings shall match points identified on terminals of controllers.

    - Maintenance Tool and Software Manuals:  Provide maintenance tools and supporting software documentation required for the complete maintenance of the entire system including diagnostics ad adjusting.  Maintenance tool may be hand held or built into control system and shall be of the type not requiring recharging or reprogramming nor of the automatic destruct type.  The tool and supporting software may be programmed to operate only with this project's identification serial numbering.

  - Final Service and Inspection:  Two weeks before expiration of the year's maintenance, the equipment shall be lubricated, fully serviced, adjusted to the standards designated and emergency service operation devices shall be checked.  A complete inspection will be made by a representative of the Owner.

  - Quotation:  Base bid shall include cost of maintenance and materials as described above.

# END OF SECTION