FIRE PROTECTION SYSTEM

GENERAL CONDITION & TECHNICAL SPECIFICATIONS

PROJECT	:	5-STOREY ACADEMIC BUILDING (PHASE 1)

FIRE PROTECTION SYSTEM

OWNER	:  	TARLAC STATE UNIVERSITY

LOCATION	: 	TSU LUCINDA CAMPUS, TARLAC CITY

==================================================================

PART 1:   GENERAL CONDITIONS

A.               The General Conditions form a part of these specifications and contract.

B.	The sub-contractor for the Fire Protection Works is designated as the Contractor in this Division.

PART 2:   SCOPE OF WORKS

A.	Furnishing of all materials, labor, tools, equipment and accessories for the complete installation, testing and adjustment, ready for use of the proposed automatic fire sprinkler system.

B.	The  works  essentially  shall  include,  but  shall  not  necessarily  be  limited  to  the following items:

1.	Supply  and  installation  of  the  automatic  fire  sprinkler  system  (AFSS) consisting of supply risers, feedmains, crossmains, branchlines, nipples, sprinkler heads, fittings, valves, hangers, trims and its accessories required to complete the system.

2.	Installation and supply of floor control valves, water flow switches & drain valves assembly including connections of electrical wiring up to the fire alarm box or electrical panel and its accessories required to complete the system.

3.	Supply & installation of 150 mm AFSS & 100 mm DSP Fire Department connection line complete with fittings, trims & its accessories to complete the system.

4.	Inspector test pipe, nozzle, valves and drain line on the farthest point of each system.

5.	Supply and installation of the wet standpipe consisting of fire hose cabinet housing, fire hoses and pressure reducing / restricting valves including connection to the Automatic Fire Sprinkler System, trims and its accessories required to complete the system

6.	Supply  and  installation  of  the  Dry  standpipe  system  to  consist  of  Fire Department connection inlet, Fire Department connection line, supply riser, fire hose valves, roof manifold outlet, trims and its accessories required to complete the system.

7.          Supply & installation of portable fire extinguishers.

8	All openings through which fire may spread from one floor to the other, such as  holes  through  floors  made  for  the  passage  of  plumbing  pipes  and electrical circuits shall be sealed with fire resistant materials.

9.          Tools and stock of sprinkler system required to complete the system.

10.	Furnishing and installation of instruction and identifications boards, charts, signs & markers.

11.	Priming and finish painting (red) of cladded and exposed piping and other part of sprinkler system except for sprinkler heads.

12.        Complete testing and commissioning, star-up of the entire Fire Protection

System in accordance with NFPA-13.

13.	Supply and installation of Fire pump and jockey pump including controllers, alarm check valve assembly, pressure relief valves, OS & Y valves, check valve flexible connector, suction strainer, trims and its accessories required to complete the system.

14.	Miscellaneous items and other related materials required for the satisfactory completion of the sprinkler system.

15.	Securing and payment of permits, licenses and bonds for the construction purposes, including approval from the Fire Department having jurisdictions.

16.	Contingency to include the furnishing of written one (1) year warranty upon completion works of sprinkler system.

17.	Preparation and submission  of  As-Built  drawings  in  reproducible  sheets including two (2) white prints copies at no cost to the Owner(s).

18.       Securing and payments of all Contractor’s taxes, VAT, etc.

PART 3:   WORK NOT INCLUDED

A.               The following items of works will be supplied and done by others.

1.	All cutting and patching shall be made by the General Contractor, except us a specifically modified herein.

2.	All electric power wiring, except that is furnished as an integral part of factory assembled equipment, except us otherwise specified herein by Electrical Contractor.

3.          Supply and installation of fire doors by General Contractor.

4.          Fire  alarm  bells  and  fire  station  for  the  alarm  system  by  Electrical

Contractor.

5.          Construction of the reinforced concrete fire storage reservoir by General

Contractor.

PART 4:   APPLICABLE      SPECIFICATIONS      CODES,      ORDINANCES, PERMITS AND FEES

A.	The work covered in this contract is to be installed according to the specifications, codes, ordinances and requirements of the following :

1.          Fire Code of the Philippines

| 2. | NFPA NO. | 13 | - latest edition |
| --- | --- | --- | --- |
|  | NFPA NO. | 80 | - latest edition |
|  | NFPA NO. | 75 | - latest edition |
|  | NFPA NO. | 18 | - latest edition (National Fire Code) |
|  | NFPA NO. | 20 - | latest edition |

NFPA NO. 101 -        latest edition

NFPA NO. 418 -        latest edition

3.          National Plumbing Code of the Philippines

4.          Fire Department Ordinances of concerned city and municipality.

B.	All construction permit and fees required for the work shall be obtained by & at the expense of the Contractor. The Contractor shall furnish the Architect, the Engineer

&  the  Owner  final  certificates  of  inspection  and  approval  from  the  proper government authorities after the completion of the work.

C.	The Contractor shall obtain all necessary allowances, pay royalties, etc. In connection with the use of any patented device or system & shall save the Owner harmless from any claim or lawsuit arising from such use.

PART 5:   SHOP DRAWINGS, SAMPLES AND OTHER SUBMITTALS

A.               The Contractor shall prepare and submit for approval the following :

1.	Dimensional layout of all pumping system, fire hose cabinet connections, etc.

2.	Manufacturer’s catalog, sheets, marked as necessary to indicate materials or equipment being furnished for the following items :

a.          Fire and Jockey Pumps

b.          Controls and pump controllers

c.	Pressure relief and reducing valves, alarm check valves, waste cone, O.S. & Y gate valve, drain valves, gate valves and water flow switches.

d.          Mechanical grooved couplings and flexible connectors.

e.	Fire department connections (inlet and outlet), siamese roof outlet, hose valves, hose headers and hose cabinets.

f.          Sprinkler heads, sprinkler wrench and spare cabinets g.          Riser supports and sleeves

3.	List of miscellaneous materials proposed, including pipe, fittings, valves, etc. and manhole accessories, identifying manufacturer and type.

4.          Field test reports

5.          Such other similar information the Engineer may require.

PART 6:   ACCEPTANCE TESTS

A.               Acceptance of the work shall be conditioned on successful tests of the entire system. B.               Test requirement laid out in the standards for the installation of sprinkler system

NFPA-13 shall be performed prior to the approval of the work.

C.	Isolated leak tests or partial tests of areas may be performed prior to installation of ceiling materials in the area to preclude any damage and during the total system final tests.

D.	The Contractor shall furnish the Owner a written statement to the effect that the work covered by the Contract has been completed and tested, before requesting for final approval of the installation from the Fire Department Authority.

PART 7:   WORKMANSHIP AND COORDINATION OF WORK WITH OTHERS

A.	The Contractor shall be held fully responsible for the work of any manufacturer or sub - contractor supplying materials to or performing work for; as it is intended that the entire Fire Protection System shall be ready in every respect for satisfactory and efficient operation when finally delivered to the Owners.

B.	The Contractor shall assume full responsibility and shall provide the services of a qualified  Engineer  to  supervise  the  complete  installation  of  equipment  and  to conduct the final acceptance tests.

C.	The work throughout shall be executed in the most thorough and satisfactory manner in accordance with the best practices of the trade.

PART 8:   SPRINKLER HEADS

A.               Type :

Automatic. Standard 15 mm  diameter orifice, solder fillet type, upright, pendent or sidewall heads. Pendent heads shall be provided with aluminum escutheon or approved equivalent to fit into ceiling boards or ceiling runners, flush or concealed type pendent units shall be accepted as substitute. Heads shall be UL Inc. approved, of  one  brand  all  throughout  and  shall  be  standard  product  of  a  reputable manufacturer.

B.               Head Rating and Type:

| Kitchen / Area | Standard,sidewall type sprinkler heads rating @ 1750 F to 2250 F | Chrome Plated Finish |
| --- | --- | --- |
| Office/Lobby/Common Hallway Areas | Standard, pendent/concealed type sprinkler heads rating @ 1750 F to 2250 F | Chrome Plated Finish |

C.               Pipe Thread and Valve Seat                    -           15       mm       diameter       nominal

(Conventional)

20 mm diameter nominal (extended) D.               Spare Sprinkler Heads:                                 (165 F)   (212 F)

3.1      Standard Type                 -           24 pcs. - pcs.

3.2      Extended Coverage Type-           24 pcs. - pcs.

4.          Flushed / Concealed Type          -           24 pcs. - pcs

E.                Sprinkler Tong                  -       3 pcs. required

F.                Sprinkler Wrench             -       3 pcs. required

G.	Furnished spare heads as required in the code and maintenance service part list for a period of at least one (1) year reckoned from the date after termination of warranty.

PART 9:      FIRE HOSE CABINETS

A.               Hose and valve assembly as manufactured by “POTTER-ROEMER” Manufacturing

Company or approved equal.

Hose                 -    40 mm diameter, 30.0 m Single Jacket, Rubberlined .

Nozzle              -     combination fog and solid stream, 40 mm diameter, chrome plated, Model; No. L-205

Rack                 -     semi-automatic, chrome plated, Model No. S-41

Angle  type,  Pressure  Reducing /or  restricting Valve  - 40 mm diameter, chrome plated polished trim, 110 m water pressure, provide with nipple and union patent, set at 70 m water pressure.

Hose Nipple-          for components, shall  be  chrome  plated.  Provide two (2)

universal spannel wrenches, Model 46-5.

B.	Cabinet             -     full flush mounting door with anodized cal - colored aluminum for all glass plate, frame and box shall be No18 gauge steel with white interior baked enamel finishes over primer. Cabinet size shall contain the above components.

PART 10:    FIRE DEPARTMENT CONNECTION (INLET)

A.	Shall be flushed wall mounted (sidewalk connection) similar to “Potter-Roemer” Model No. 5021 for Dry Standpipe and Model No. 5206 for Auto. Sprinkler Stand pipe or approved equal complete with cap/ plugs and chains, plates lettered with “Auto. Sprinkler Standpipe & “Dry Standpipe” to match Integrated Metropolitan Fire Department requirements.

B.	Type:         -     Two way outlet connections two (2) way 65 mm x 65 mm x 100 mm. For Dry Standpipe.

-	Two way outlet connections two (2) way 65 mm x 65 mm x 100 mm. For AFSS System.

C.               Finish:        -     Cast brass body with drop clappers

-     Polished brass rectangular identification plates

-     Polished brass, double female snoots, pin lugs, and chains

D.	Shall be female snoots and NPT x pin lug hose thread swivels & provided with pin lug plugs and chains connections.

PART 11:   TESTING HOSE HEADER (OUTLET)

A.	Shall be flushed wall mounted (sidewalk connection) similar to “Potter-Roemer” Model No. 5862, Model No. 4115 for valves, Model No. 4625 for caps and chains plates lettered with “Pump Test Connection” or approved equal to match Integrated Metropolitan Fire Department requirements.

way 65 mm x 65 mm x 100

D.               Shall be female NPT inlet x male hose thread outlet provided with caps & chains.

PART 12:   WALL HYDRANTS (FIRE HOSE VALVES)

A.	Shall be straight globe female x male assembly similar to “Potter-Roemer” Model No. 4115 for valves and Model No. 4625 for caps & chains or approved equal complete to match Integrated Metropolitan Fire Department requirements.

B.               Type :         -     Single outlet connection 65 mm x 100 mm. C.               Finish:        -     Cast brass valve with red handwheel

-     Polished brass caps and chains.

D.               Shall be female NPT inlet x male hose thread outlet provided with caps & chains.

PART 13:   ROOF MANIFOLDS (OUTLET)

A.               Shall be flushed wall mounted (sidewalk connection) similar to “Potter-Roemer”

Model No. 5871 for back inlet body,  Model No. 4115 for valves, Model No. 4625

for caps and chains and provided with round identification plates Model No. 5962 or approved equal to match Integrated Metropolitan Fire Department requirements

two (2) way 65 mm x 65 mm

E.                Shall be female NPT inlet and male NPT twin outlets for body and to match female

NPT inlet and male hose thread outlet for valves and provided with caps & chains.

PART 14:  PORTABLE FIRE EXTINGUISHERS

Furnish and install as indicated; on the drawings portable fire extinguisher, 10 lbs. dry chemical type and   halotron type capable for type ABC fire. Units shall be approved by the Fire Department having jurisdiction and UL listed. Mounting shall be inside fire hose cabinets and as shown on drawings.

PART 15:  PIPINGS - GENERAL

A.	Where American Standards are specified, other approved national or local standards may be acceptable, provided copies of these standard Specifications are forwarded to the Engineer for his written approval.

B.               Black iron, schedule 40 pipes, ASTM A-53 for pipe sizes 150 mm  and above only

(wet and dry).

C.	Black iron, schedule 40 pipes, ASTM A-120 for inside building installations (feed mains, cross mains and branch lines).

D.	All side piping shall be installed by means of screwed or flanged fittings. Flanged joint shall be used at all sprinkler risers and provided with 1.6 mm thick long fiber asbestos, cross laminated gasket “cranite”.

E.	Torch cutting shall not be permitted as means of modifying or repairing sprinkler system.

F.	All welding shall be “shop welding” only and shall be done by electric arc welding process.

PART 16:  FITTINGS GENERAL

A.	Sprinkler system fitting shall be extra heavy pattern. Whenever a change in pipe size is made, one piece of reducing fitting shall be used. Provide mechanical grooved couplings at riser pipes of every floor.

B.               All fittings shall be of malleable iron fittings.

C.	Steel pipe flangers mating with steel equipment flangers shall have the same facing as mating flange.

D.	Screwed union shall not be used on pipes larger than 50 mm (2”). Coupling and unions of pipes other than screwed type shall be of types approved specifically for sprinkler used.

PART 17:  VALVES - GENERAL

A.	All valves shall be of the same manufacture for each class of piping and as such as possible, for the entire project.  Valves shall permanently bear affixed stamp or tag indicating manufacturer, catalog number, pressure and temperature ratings of gate valve, angle valves, check valves, pressure relief with all cast iron body with bronze trim.

B.	Furnish  all  valves  and  accessories  material  necessary  for  piping  not  shown  on drawings as follows :

1.          Vents and drains for equipment to which piping connections are made.

2.	Connections to metering instruments and controls including pressure gauges, thermometer, controllers, traps and appurtenances required for proper functioning on instruments in controls.

3.	Temporary valves and accessories required for placing equipment    into initial service.

4.	Piping  50  mm (2”)  and  smaller  required  for  proper  operation  of  piping system and equipment, including drain valves required to drain all low points in piping.

C.               Valve seats shall be renewable except for forged steel and high pressure cast steel

valves where manufacturer’s standard is integral seats.

D.	All valves shall be approved by Factory Manual and Underwriters Laboratories, Inc. (UL listed).

E.	Where required and not noted, provided chain - wheel operators, extending chain for chain operated valves to which 1.2 meters of nearest floor or operating platform of valves.

F.	Provide floor stand with flanged faces for bolting to floor or platforms and other special devices where specified or noted on drawings.

G.	Provide extension stems, universal joints stem guide bearings and other accessories required to locate floor stands in convenient location with interference with other equipment, piping or building parts.

H.	Floor control valves within the building shall be approved indicating wedge gate with electrical contact and which will open when valve is partially or totally put in close position.

PART 18 :  SWAY   BRACES,   HANGERS,   SUPPORTS   AND   SEISMIC BRACINGS

A.	Sway Bracing   :   Steel flat bars, structural grade 7 mm minimum thickness, with corrosion protection; shape / type as shown on plans.

1.          Sway Bracings Installation

1.1	Adequate sway bracing shall be provided to oppose longitudinal or transverse pipe movements.

1.2	Lateral bracings shall withstand a force equal to 50% of the weight of the water contained in piping, valves and fittings. Spacing shall be

40 ft. (12m) maximum distances along main lines.

1.3	Longitudinal bracing shall with stand a force equal to 50% of the weight of crossmain and feedmain within the zone of water contained in piping, valves and fittings. Spacing shall be 80 ft. (24 m) maximum distances along main lines.

1.4	Piping anchorages shall not be scured on two (2) dissimilar parts of the building which will move differently.

B.	Pipe Hangers   :   Steel flat bars, structural grade, 7 mm minimum thickness, with corrosion protection, shape as shown on plans and 13 mm diameter bars with corrosion protection as shown on plans.

1.          Hangers Installation

1.1	Approved inserts may be used for the support of hangers, anchorage in concrete. Expansion shield should be used in a horizontal position on the sides of concrete beams and shall be above the bottom reinforcements.

1.2	Increase couplings shall be attached immediately adjacent to the expansion shields.

1.3	When  pipes  100  mm  diameter  and  larger  are  supported  in  the vertical position, the supports shall be at a minimum spacing of 3.0 meters (10’) on center. Holes in concrete for expansion shield shall be made of the proper size and depth, as specified for the type of

shield used, to provide a uniform contact with the shield over its entire length and circumference.

1.4	Maximum distance between hangers shall be 3.65 meters (12’) for size mm (1”). Provide at least one hanger for each length of branch line, one between each two cross main branches, one hanger for each

4.75 meters (15’) length of feed mains. The distance between the hanger and the center line of upright sprinkler shall be not less than

76 mm (3”).

C.               Support on Risers (Four Way Bracing)

Risers shall be adequately supported either by attachments directly to the riser or by hangers located on the horizontal connections close to the risers. Supports shall be provided at the ground level and at each every second floor level and at the top most level of the riser.

D.               Seismic Separation Bracing

Seismic separation assembly shall provided at every piping crosses at every construction joints of the building separation assembly shall composed of fittings, pipe and approved victaulic coupling that permits movement in all directions and sufficient to withstand differential motion during earthquake. For nominal 4” (100 mm) and above sizes of pipes the separation distances shall not exceed 8 inches (203  m)  maximum.  For other separation distances and pipe sizes, length and distances should be modified proportionally.

PART 19:  PIPES SLEEVES

A.               MATERIALS:

1.          Through fittings - cast iron

2.          Below Grade-cast iron or standard weight iron pipe

3.          Above Grade - steel pipe

B.               INSTALLATION:

1.	Minimum clearance between the pipe & sleeve shall not be less than 25 mm (1”) for pipes, 25 mm (1”) to 89 mm (3-½”) and 50 mm (2”) clearance between pipes 100 mm (4”) & larger. The clearance between pipes and sleeves shall be filled with non - combustible flexible materials such as asbestos rope & furnished with semi-hardening mastic flush.

2.          Floor sleeves shall extended at least 76 mm (3”) above the top of the wearing

surface.

3.	Drains, fire department  connections,  test  manifolds  and  other  auxiliary piping connected to risers shall not be cemented into walls or floors.

PART 20:  PIPE PAINTING

A.               Sprinkler heads, valve stems and the like shall not be painted.

B.	After installation and test and before the installation of ceiling fixtures or boards, all piping shall be prime painted and coated with two coats of gloss red quick drying enamel.

PART 21: ALARM CHECK VALVES

A.	The alarm assemblies shall be so constructed and installed, that any flow of water from the sprinkler system equal to or greater than from a single automatic sprinkler head, will result in an audible and visual alarm bells whether water or electrically actuated shall be capable of being actuated both automatically and annually.

B.	The  water  actuated  alarm check  valve  assembly  shall  be  complete  with  all  the necessary attachments required to give an alarm and ease in maintenance.

The gong shall be installed as indicated in the plans. The alarm check valve shall consist of but not limited to the following:

1.          Retard chamber

2.          Water motor

3.          Weatherproof gong, 300 mm diameter

4.          Strainer

5.          Pressure gages

6.          Drain and attachments

7.          Electrically supervised control valves

8.          Pressure switches

PART 22 :  FLOOR CONTROL VALVES AND WATER FLOW SWITCHES

A.               Flow alarm valves with sizes indicated on the plans shall be provided with two (2) N.

O. electrical contacts that will close instantaneously with steady flow of water in the pipe and shall be complete with tamperproof terminal chamber with minimum of

1/2” diameter conduit. False alarm shall be prevented by an adjustable pneumatic device to retard the flow of shall be actuated only by an undirectional flow of water. Electrical connections from these valves shall be done by the Electrical Contractors.

B.	The alarm apparatus shall be substantially supported, located and installed so that all parts shall be readily accessible for inspection, removal and repair.

C.	An actual water flow, through the use of the test connection, shall be employed to test the operation of the sprinkler alarm units in each floor or as a whole.

PART 23: 	ALARM AND SUPERVISORY SYSTEM

The supervisory and alarm system shall be integrated with the building Fire Alarm, System. The Fire Alarm System annunciator shall indicate the flow valves, and the valve supervisory switches.

PART 24: 	MARKERS, INSTRUCTION & IDENTIFICATION SIGNBOARD

These signboards shall be made of gauge No. 14 black iron sheet with baked enamel finish and letter instruction as shown on the plans. Additional signboards shall be mounted on the unobstructed for easy identification reading. Paints shall be basically gloss fire red and white.

PART 25: PUMPS

- GENERAL :

- Manufacturer’s installation drawings shall be submitted together with the proposal. After installation is completed as “as-installed” drawings showing all the field revisions and exact locations/dimensions on reproducible form plus two (2) white print copies shall be submitted to the Owners at the Contractor’s Expense.

- Pump performance curves shall be submitted together with the proposal. The pump efficiencies at various work loads shall be indicated thereon and properly marked.

- Test run shall be performed by the supplier after the installation is completed, to demonstrate conformity to the manufacturer’s specifications. A successful test shall be a condition to the Owner’s acceptance of the installed equipment and to final payment.

- A direct statement on the availability of spare parts and maintenance service from pump supplier, for a period of at least three (3) years reckoned from the date of acceptance test shall be submitted.

- FIRE PUMPS :

1. 	The pumps shall be Diesel engine drive, all control and necessary attachments specified herein shall be UL listed and FM engineering approved and shall be furnished under their Contract. The pump shall be capable of delivering not less than 150 percent of rated capacity at not less than 65 percent of total head. The shut-off head shall not exceed 120 percent of rated heads. The fire pump shall be horizontal centrifugal type with accessories to include, circuit breakers, starters & controllers.

- Up-feed System

Fire Pump @ Basement level (underground water tank level) volumetric capacity shall be 500 GPM vs. 231 FT. TDH (150 PSI), approx. 50 HP

Pump Unit Major Accessories:

- Circulation relief valve

- Hose valve manifold 105 dia, hose valve

- Flow measuring device

- Relief valve and discharge cone

- Suction strainer

- Primary connection

- Capacity plate

- Automatic air released valve fittings

- Water level testing device and piping

- Pressure gage, 80 mm dia.

- Pressure switches

2. 	Diesel Engine Drive:

HP		 -	 50 HP for fire pump (underground water tank level) or per Manufacturer’s recommendation.

Voltage 		- 	230/380 Volts (verify EE)

Phase		 - 	3

Frequency  	  -   	60 Hz

Temperature Rise -	 40 degree C

Service Factor	 - 	1.15 (min.)

3.          Motor Controller:

- Type-Combination Circuit Breaker and starter; UL listed and FM Engineering approved :

- Circuit Breaker-magnetic trip, 3 phase, 230 V (min) 300 times motor FLA continuous rating. Interrupting rating not less than 40,000 rms. amps. symmetrical at 230 VAC with external operating handle.

- Starter - magnetic, wye - delta reduced voltage type, close transition with 3 - O.L. relays and necessary auxiliary contracts.

3.   Enclosure-watertight type, NEMA 4 floor mounted.

4.    Flow Measuring Device

Fire pump shall be acquired also with “Flow Measuring Device” consisting of flow meter and flow indicator.

Flow element shall be similar to Universal Venture type and the flow indicator shall be similar to well type Mercury Manometer. Model shall be similar to Aurora Fire Pump Flow Metering Devices Model GB.

5.    Installation Drawings:

Manufacturer’s installation drawing shall be submitted as part of Shop Drawings, Section 500 of the Specifications.

6.    Performance Curves:

Performance curves shall be submitted together with the requirements of Section 500. The pump efficiencies at various work loads shall be indicated thereon and properly marked.

7.   Installation:

This Contractor shall assume unit responsibility and shall provide the services of a qualified Engineer to supervise the complete installation of equipment who shall be available conducting the final acceptance test as stated under Section 600 of the specifications.

C.         JOCKEY PUMPS:

1.	The  pumps  shall  be  electric  motor  drive,  all  control  and  necessary attachments  specified  herein  shall  be  UL  listed  and  FM  engineering approved and shall be furnished under their Contract. The pump shall be capable of delivering not less than 150 percent of rated capacity at not less than 65 percent of total head. The shut-off head shall not exceed 120 percent of rated heads. The fire pump shall be horizontal centrifugal type with accessories to include, circuit breakers, starters & controllers.

A.         Up-feed System

Jockey Pump volumetric capacity shall be    30 GPM (min.) vs. 115

FT. TDH (155 PSI), approx. 3.0 HP

Jockey  Pump  Control  Panels  :  Furnish  ready  for  wiring  jockey pump,  General  Electric  CRI 35  type  “F”  with  “  H-O-Automatic switch and timer run relays, with three overload relays, Clark Controller, Cutler Hammer, Inc. “Firetrol” or as approved.

B. 	PUMP SEQUENCE OPERATION

Adjust pressure switches to control the fire and jockey pump operation in the following sequence:

| Pump | Pump On | Pump Off |
| --- | --- | --- |
| 30gpm Jockey Pump 1.1 500gpm Fire Pump | __PSIG __PSIG | __PSIG MANUAL |

D. 	SPARE PARTS:

Furnish spare parts and maintenance service parts lists for a period of at least one (1) year reckoned form the date after termination of warranty as indicated in Section 2700 of these Specifications.

MOTORS:

1.	 General Requirements:

a. 	Motor types required for project: Refer to other parts of specifications.

b. 	Motors shall be furnished with driven equipment to assure proper coordination of motor and control characteristics with requirements of driven equipment. Contractor is responsible for proper correlation of horsepower, starting torque, other characteristics of electrical equipment, with requirements of driven equipment.

c.	 Horsepower: nameplate rating shall be at least as great as the brake horsepower required to drive the equipment under the maximum specified conditions without consideration of service factor.

d. 	Conform to NEMA Standard No. MGI entitled “Motor and Generator”, except where specifically noted otherwise.

e.	 Conform to ANSI Standard No. C50, 2-1955 Alternating - Current Induction Motors, Induction Machine is in General and Universal Motors.

f. 	Torque and speed characteristics; suited to requirements of driven equipment, including gear reducers if specified.

g.	 Maximum speed: 3,500 rpm unless specified otherwise.

h. 	Horsepower:

1.	Motor Hp rating specified shall be nameplate rating without consideration of motor service factor.

2.	Nameplate   Hp   not   less   than   Hp   required   by   driven equipment operated at maximum conditions specified.

i.          Duty:  continuous.

j.	Service   factor:   as specified herein, unless specifically stipulated otherwise in detailed equipment specifications.

k.	Bearings: ball, unless otherwise specified; provide for in - service lubrication of enclosed motors, unless specifically noted otherwise.

l.          Base:

1.	Provide cast iron or steel motor base with provision for motor alignment on direct - coupled drives.

2.	Provide sliding or hinge motor base with screw - type, automatic gravity - type, or other manufacturer’s standard means of adjustment for belt or chain drives.

m.         Accessories: lifting lugs as required.

n.	Motors specified as 230 - volts, three - phase may be designed for single or dual voltage in accordance with manufacturer’s standard for horsepower and speed required.

o.          Frequency:  60 hertz.

2.          Enclosures and Insulation:

a.	Suitable for 40 degree C ambient duty, with standard service factor, unless otherwise specified.

b.	Drip - proof encapsulated: encapsulated moisture sealed insulation system, with weather - resistant conduit box:  bearing shielded against entrance of moisture and dirt; and anti - corrosion treatment of exposed metal parts, 40 degree C ambient, continuous duty, with

1.15 (min.) service factor.

c.          Totally enclosed non - ventilated of fan-cooled; 40 degree C

ambient, continuous duty, with 1.15 (min.) service factor.

d.	If other types of insulation are proposed, operating temperature must be guaranteed satisfactory for proposed installation.

3.          Types:

Single   -  phase   induction;   method   of  starting  suited  to  driven  load requirement; constant or multi - speed, and method of starting as specified.

PART 26:   ACCEPTANCE TESTS

A.	The Contractor shall conduct tests in the presence of inspector or authority having jurisdiction (The Philippine Fire Protection Association of Fire Protection Associates).

B.	To remove foreign materials which may have entered the piping during installation of same, flushing or underground connection is required before sprinkler piping is connected.

C.               Hydrostatic Tests:

1.	Tests pressure not less than 200 psi on system pressure plus 50 psig for two hours.

2.	No visible leakage for inside sprinkler piping will be allowed. Fore underground mains and laid - ins, exceeding the permissible leakage or joints necessary repair shall be made.

3.	All control valve water pressure to insure proper operating tests. Use clean, non - corrosive water.

4.          Fire connection shall be tested.

D.	Testing of drainage facilities shall be made by opening the main drain valve while the control valve is wide open.

E.                Test  certificate  shall  be  filled  out  and  signed  by the  Owner’s  and  Contractor’s

Representative.

F.	System operations and maintenance chart shall be submitted to the Owners upon completion of the Contract. This shall include, among others, the locations of the control valves and care of the new equipment.

PART 27:  MINOR MODIFICATIONS AND TIME COMPLETION

A.	The plans as drawn should show conditions as accurately as it is possible to indicate them in scale. The plans are diagrammatical and do not necessarily show all fittings, etc. necessary to fit the building conditions. The locations of valves, fittings and the fixture shown on the plans are approximately. The Contractor shall be responsible for the proper location in order to make them for with architectural detains and instructions.

B.	The Contractor shall complete the work herein described in accordance with the specific schedules set by the Owners in accordance with General Contractor’s Schedule of Work.

PART 28:  GUARANTEE

The Contractor shall guarantee that the installed sprinkler system complies with the requirements  of  the  authorities  and  free  from  all  defective  workmanship  and materials and will remain so, for a period of one (1) year from the date to final inspection and acceptance of the work.  Any defect appearing within one year shall be corrected by the Contractor at no additional cost to the Owner.

PART 29:  CONTRACTOR’S RESPONSIBILITY

1.	The Contractor shall provide temporary fire protection system during the construction period. This shall be of sufficient capacity to put any fire that may break out at any floors due to construction operations.  This is in addition to temporary fire extinguisher required.

2.	The Contractor shall identify and save the Owner, the Architect and the Consulting Engineer Harmless from and against all liabilities for damage to property occasioned by any or omission of this Contractor on any of this Sub

- contractors, including any and all expenses, legal or otherwise which may be insured by the Owner, the Architect or the Consulting Engineer, in the defense of any claims, action or suits.

-  End of Specifications -

# Text boxes

| 1. | Upright Type | - 24 pcs. 3 pcs. |
| --- | --- | --- |
| 2. | Semi Recessed Pendent Type | - 12 pcs. 6 pcs. |
| 3. | Sidewall Type | - 40 pcs. |

| B. | Type : | - Two way outlet connections two (2) mm |
| --- | --- | --- |
| C. | Finish:- | Cast brass body with back inlet - Brass rectangular identification plates - Cast brass valves with red handwheel - Polished brass cap and chain |

| B. | Type : | - Double (twin) roof outlet manifolds, x 100 mm. |
| --- | --- | --- |
| C. | Finish: | - Cast brass body back inlet - Cast brass valve with red handwheel - Polished brass caps and chains. - Brass round identification plates |