Water-Cooled Screw Compressor Chillers

WGS 130AW To WGS 190AW, Packaged Water-Cooled Chiller

WGS 130AA To WGS 190AA, Chiller with Remote Condenser

120 to 200 Tons, 420 to 700 kW

R-134a, 60 Hz

Software Version WGSD30101E

Table of Contents

Introduction	3

General Description	3

Nomenclature	3

Definitions	4

Wiring Diagrams	8

Control Panel Layout	10

MicroTech II( Controller	13

System Architecture	13

General Description	14

Units of measure	14

Sequence of Operation	16

Start-Up and Shutdown	22

Pre Start-up	22

Start-up	22

Weekend or Temporary Shutdown	23

Start-up after Temporary Shutdown	23

Extended Shutdown	23

Start-up after Extended Shutdown	24

Unit Controller	27

Unit Inputs/Outputs	27

Unit Setpoints	27

Circuit Controller	30

Circuit Inputs and Outputs	30

Circuit Setpoint Table	31

Alarms and Events	33

Unit Stop Alarms	33

Unit Events	35

Circuit Stop Alarms	35

Clearing Alarms	37

Unit Controller Functions	37

Unit Enable	37

Unit Mode Selection	39

Unit States	40

Evaporator Pump Control	41

Leaving Water Temperature (LWT) Reset	42

Planned Unit Capacity Overrides	44

Condenser Pump and Tower Control	45

Cooling Tower Control	46

Evaporative Condenser Control	48

Circuit Controller Functions	51

Refrigerant Calculations	51

Compressor Control	52

Internal Capacity Overrides	55

Slide Positioning	56

Expansion Valve Control	58

Oil Heater Control	62

Starter Communications	62

Condenser Fan Control	64

Condenser Fan VFD	65

Digital Output Control	65

Using the Controller	66

Security	68

Entering Passwords	68

Editing Setpoints	68

Clearing Alarms	68

Menu Descriptions	69

Unit Controller	69

Circuit Controller	84

Editing Review	93

BAS Interface	94

Unit Troubleshooting Chart	95

(2007 McQuay International

Illustrations and data cover McQuay International products at the time of publication and we reserve the right to make changes in design and construction at anytime without notice.

(( The following are trademarks or registered trademarks of their respective companies: 
BACnet from ASHRAE; LONMARK and LONWORKS from Echelon Corporation; 
GeneSys, McQuay and MicroTech II from McQuay International.

# Introduction

## General Description

McQuay Model WGS water chillers are designed for indoor installations and are available with factory-mounted water-cooled condensers (Model WGS AW), or arranged for use with remote air-cooled or evaporative condensers (Model WGS AA).  Each water-cooled unit (WGS-AW) is completely assembled and factory wired before factory evacuation, charging and testing.  The units consist of two semi-hermetic rotary screw compressors, a two-circuit shell-and-tube evaporator, two shell-and-tube water-cooled condensers, and complete refrigerant piping.

Units manufactured for use with remote condensers (Models WGS-AA) have all refrigerant specialties factory-mounted and have two sets of connection points for refrigerant discharge and liquid lines to and from the remote condenser.  Discharge valves are included

Each circuit’s liquid line components are manual liquid line shutoff valve, charging valve, filter-drier, liquid line solenoid valve, sight glass/moisture indicator, and electronic expansion valve.

The electrical control center includes a MicroTech II( microprocessor control system and equipment protection and operating controls necessary for dependable, automatic operation.

The compressor circuits are equipped with individual circuit breakers and a unit disconnect switch is available as an option over the standard power block.

This software revision adds fixes several bugs in the IP/SI units logic, improves the operation of remote evaporator units in low ambient air temperatures, improves communications with the solid state starter and provides compressor electrical data at the supervisor port for building automation systems.

## Nomenclature

W G S  130    - A  W

# Definitions

### Active Setpoint

The active setpoint is the setting in effect at any given moment.  This variation occurs on setpoints that can be altered during normal operation.  Resetting the chilled water leaving temperature setpoint by one of several methods, such as return water temperature, is an example.

### Active Capacity Limit

The active setpoint is the setting in effect at any given moment.  Any one of several external inputs can limit a compressor’s capacity below its maximum value.

### Condenser Recirc Timer

A timing function, with a 30-second default, that holds off any reading of condenser water for the duration of the timing setting.  This delay allows the water sensors (especially water temperatures) to take a more accurate reading of the condenser water system conditions.

### Condenser Saturated Temperature Target

The saturated condenser temperature target is calculated by first using the following equation:

Sat condenser temp target raw = 0.833(evaporator sat temp) + 68.34

The “raw” value is the initial calculated value.  This value is then limited to a range defined by the Condenser Saturated Temperature Target minimum and maximum setpoints.  These setpoints simply cut off the value to a working range, and this range can be limited to a single value if the two setpoints are set to the same value.

### CPU Error

These are problems caused by a malfunction of the central processing unit.

### Dead Band

The dead band is a set of values associated with a setpoint such that a change in the variable occurring within the dead band causes no action from the controller.  For example, if a temperature setpoint is 44(F and it has a dead band of ( 2 degrees, nothing will happen until the measured temperature is less than 42(F or more than 46(F.

### DIN

Digital input, usually followed by a number designating the number of the input.

### Discharge Superheat

Discharge superheat shall be calculated for each circuit using the following equation:

Discharge Superheat = Discharge Temperature – Condenser Saturated Temperature

### Error

In the context of this manual, “Error” is the difference between the actual value of a variable and the target setting or setpoint.

### Evaporator Approach

The evaporator approach is calculated for each circuit.  The equation is as follows:

Evaporator Approach = LWT – Evaporator Saturated Temperature

### Evap Recirc Timer

A timing function, with a 30-second default, that holds off any reading of chilled water for the duration of the timing setting.  This delay allows the chilled water sensors (especially water temperatures) to take a more accurate reading of the chilled water system conditions.

### EXV

Electronic expansion valve, used to control the flow of refrigerant to the evaporator, controlled by the circuit microprocessor.

### High Saturated Condenser – Hold Value

High Cond Hold Value = Max Saturated Condenser Value – 5(F

This function prevents the compressor from loading whenever the pressures approach within 5 degrees of the maximum discharge pressure.  The purpose is to keep the compressor online during periods of possibly temporary elevated pressures.

### High Saturated Condenser – Unload Value

High Cond Unload Value = Max Saturated Condenser Value – 3(F

This function unloads the compressor whenever the pressures approach within 3 degrees of the maximum discharge pressure.  The purpose is to keep the compressor online during periods of possibly temporary elevated pressures.

### High Superheat Error

The degrees of temperature difference between 40(F and the actual discharge temperature.

### Light load Stg Dn Point

The percent load point at which one of two operating compressors will shut off, transferring the unit load to the remaining compressor.

### Load Limit

An external signal from the keypad, the BAS or a 4-20 ma signal that limits the compressor loading to a designated percent of full load.  Frequently used to limit unit power input.

### Load Balance

Load balance is a technique that equally distributes the total unit load among the running compressors.

### Low Ambient Lockout

Prevents the unit from operating (or starting) at ambient temperatures below the setpoint.

### Low Pressure Hold Setpoint

The psi evaporator pressure setting at which the controller will not allow further compressor loading.

### Low/High Superheat Error

The difference between actual evaporator superheat and the superheat target.

### LWT

Leaving water temperature.  The “water” is any fluid used in the chiller circuit.

### LWT Error

### Error in the controller context is the difference between the value of a variable and the setpoint.  For example, if the LWT setpoint is 44(F and the actual temperature of the water at a given moment is 46(F, the LWT error is +2 degrees.

### LWT Slope

The LWT slope is an indication of the trend of the water temperature.  It is calculated by taking readings of the temperature every few seconds and subtracting them from the previous value, over a rolling one-minute interval.

### ms

Milli-second

### Maximum Saturated Condenser Temperature

The maximum saturated condenser temperature allowed is calculated based on the compressor operational envelope.

### NC

Normally closed - usually refers to a contactor or valve.

### NO

Normally open - usually refers to a contactor. or valve.

### OAT

Outside ambient air temperature.

### Offset

Offset is the difference between the actual value of a variable (such as temperature or pressure) and the reading shown on the microprocessor as a result of the sensor signal.  See notes on page 32 for explanation of sensor off set.

### pLAN

Peco Local Area Network is the proprietary name of the network connecting the control elements.

### Rapid Stop

A compressor stop process that circumvents the normal pumpdown cycle.

### Refrigerant Saturated Temperature

Refrigerant saturated temperature is calculated from the pressure sensor readings for each circuit.  The pressure is fitted to an R-134a temperature/pressure curve to determine the saturated temperature.

### Soft Load

Soft Load is a control sub-routine that allows the chiller to load up gradually.  It requires setpoint inputs of selecting it by Yes or No inputs, by selecting the percent load to start ramping up, and by selecting the time to ramp up to full load (up to 60 minutes).

### SP

Setpoint

### SSS

Solid state starter as used on McQuay screw compressors.

### Suction Superheat

Suction superheat is calculated for each circuit using the following equation:

Suction Superheat = Suction Temperature – Evaporator Saturated Temperature

### Stage Up/Down Accumulator

The accumulator can be thought of as a bank storing occurrences that indicate the need for an additional fan.

### Stageup/Stagedown Delta-T

Staging is the act of starting or stopping a compressor or fan when another is still operating.  Startup and Stop is the act of starting the first compressor or fan and stopping the last compressor or fan.  The Delta-T is the “dead band” on either side the setpoint in which no action is taken.

### Stage Up Delay

The time delay from the start of the first compressor to the start of the second.

### Startup Delta-T

Number of degrees above the LWT setpoint required to start the first compressor.

### Stop Delta-T

Number of degrees below the LWT setpoint required for the last compressor to stop.

### VAC

Volts, Alternating current, sometimes noted as vac.

### VDC

Volts, Direct current, sometimes noted as vdc.

### VFD

Variable Frequency Drive, a device used to vary an electric motor’s speed.

# Wiring Diagrams

Figure 1, WGS 130AW – 190AW Field Wiring Diagram (Optional Single Point Connection)

Figure 2, WGS 130AA – 190AA Field Wiring Diagram (Remote Air-cooled Condenser)

# Control Panel Layout

Figure 3, Outer (Microprocessor) Panel

NOTES:

- Transformers T2 through T25 are class 100, 120V to 12V.

- Switches for MHPR 11 and 12 (Mechanical High Pressure Switches) are located on the compressors.

- Mechanical High Pressure Switches Open at 310 psi, Close at 250 psi.

Figure 4, Inner (Power) Panel (Optional Single-Point Power with Disconnect Switches Shown)

Figure 5, Circuit Breaker/Fuse Panel

# MicroTech II( Controller

Software Version:WGSD30101E

Bios: 3.62

BOOT: 3.0F

## System Architecture

The WGS MicroTech (( distributed control system consists of multiple microprocessor-based controllers that provide monitoring and control functions required for the controlled, efficient operation of the chiller.  The system consists of the following components:

- Unit Controller, one per chiller ( controls functions and settings that apply to the unit and communicates with the other controllers.  It is located in the control panel and is labeled “UNIT CONTROL”.

- Circuit Controllers for each compressor/circuit that control compressor functions and settings specific to the circuit.  The controllers are located in the control panel and are labeled “CIRCUIT CONROL”.

In addition to providing all normal operating controls, the MicroTech II control system monitors equipment protection devices on the unit and will take corrective action if the chiller is operating outside of its normal design envelope.  If an alarm condition develops, the controller will shut down the compressor, or entire unit, and activate an alarm output.  Important operating conditions at the time an alarm condition occurs are retained in the controller’s memory to aid in troubleshooting and fault analysis.

The system is protected by a password scheme that allows access only by authorized personnel.  The operator must enter the operator password into the controller’s keypad before any setpoints can be altered.

PLAN Addressing

The pLAN (proprietary local area network) addressing is based on a commonly used scheme among all applications using pLAN networked MicroTech II controllers.  Only three addresses are needed, and are designated as shown in the following table.

| Controller | Address | Dip Sw 1 Position | Dip Sw 2 Position | Dip Sw 3 Position |
| --- | --- | --- | --- | --- |
| Unit | 5 | Up | Down | Up |
| Circuit 1 | 1 | Up | Down | Down |
| Circuit 2 | 2 | Down | Up | Down |

The Dip switches are located on the upper front of the controller above the screen.

## General Description

The MicroTech II controller’s design permits the chiller to run more efficiently, and it simplifies troubleshooting if a system failure occurs.  Every MicroTech II controller is programmed and tested prior to shipment to assist in a trouble-free start-up.  The MicroTech II controller can be used to cycle fans on remote air-cooled condensers for head pressure control when the setpoint Water Cooled=N is selected in one of the setpoint menu screens.  Water Cooled=Y sets the chiller for operation with the water-cooled condenser and activates settings for cooling tower control.  Remote evaporative condensers will have to have self-contained, on-board, head pressure control systems.

## Units of measure

Version “C”, as described in this manual, supports metric (SI) units of measure.

| Inch-Pound | SI |
| --- | --- |
| (F to 0.1(F | (C to 0.1(C |
| psi to 0.1 psi | KPa to 1.0 kPa |

### Distributed Control

The WGS units have three MicroTech II microprocessors, a Unit Controller plus a Circuit Controller for each of the two circuits.  The Circuit Controllers are independent such that either one will operate its circuit if the other Circuit Controller is out of service.

### Operator-friendly

The MicroTech II controller menu structure is separated into three distinct categories, which provide the operator or service technician with a full description of the following:

- Current unit status

- Control parameters (setpoint settings and adjustment).  Security protection prevents unauthorized changing of the setpoints and control parameters.

- Alarm notification and clearing

The MicroTech II controller continuously performs self-diagnostic checks, monitoring system temperatures, pressures and protection devices, and will automatically shut down a refrigerant circuit or the entire unit if a fault occurs.  The cause of the shutdown and date stamp are retained in memory and can be easily displayed in plain English for operator review, which is an extremely useful feature for troubleshooting.  In addition to displaying alarm diagnostics, the MicroTech II controller also provides the operator with a warning of pre-alarm limit conditions.

### Staging

The two screw compressors are loaded and staged on and off as a function of leaving chilled water temperature, number of starts and run-hours.  See Sequence of Operation beginning on page 16.

### Equipment Protection

The unit is protected by alarms that shut it down and require manual reset, and also by limit alarms that limit unit operation in response to some out-of-ordinary condition.  Shutdown alarms activate an alarm signal that can be wired to a remote device.

### Unit Enable Selection

Enables unit operation from local keypad or digital input.

### Unit Mode Selection

Selects standard cooling, ice, glycol, or test operation mode.

### Keypad/Display

A 4-line by 20-character/line liquid crystal display and 6-key keypad is mounted on each controller.  Its layout is shown below.

Figure 6, Keypad and Display in MENU Mode

The four arrow keys (UP, DOWN, LEFT, RIGHT) have three modes of use.

- Scroll between data screens as indicated by the arrows (default mode).

- Select a specific data screen in a hierarchical fashion using dynamic labels on the right side of the display (this mode is entered by pressing the MENU key).

- Change field values in edit mode according to the following table:

LEFT	Default
	RIGHT	Cancel
	UP	Increment
	DOWN	Decrement
These four edit functions are indicated by one-character abbreviations on the right side of the display (this mode is entered by pressing the ENTER key).

# Sequence of Operation

### Compressor Heaters

With the control power on, 120V power is applied through the control circuit Fuse FU7 to the compressor oil separator heater (HTR-OIL SEP).

### Startup/Compressor Staging

During Cool Mode the following must be true to start a circuit operating.  The evaporator and condenser pump (WGS-AW only) outputs must be energized and flow must be established for a period of time defined by the evaporator recirculate setpoint.  Established flow will be detected by evaporator and condenser water flow switches.  The water temperature leaving the evaporator must be greater than the Active Leaving Water Temperature setpoint, plus the Startup Delta-T, before a circuit will start.  The first circuit to start is determined by sequence number.  The lowest sequence numbered circuit will start first.  If all sequence numbers are the same (default), then the circuit with the fewest number of starts will start first.

During operation, the slide valves for loading and unloading will be pulsed until the active leaving water temperature setpoint is maintained.  The second circuit start will occur once the first circuit has loaded to 75% slide capacity or is in Capacity Limit and the water temperature leaving the evaporator is greater than the active leaving water temperature Setpoint plus Stage Delta-T.  The circuits will load or unload simultaneously through a continuous capacity control to maintain the evaporator leaving water temperature.  If all sequence numbers are the same, the circuit with the most run hours will be shut down first.  The circuit with the most run hours will stop when the water temperature leaving the evaporator is less than the Active Leaving Water Temperature Setpoint minus Stage Delta-T.  The last remaining circuit will shut down when the water temperature leaving the evaporator is lower than the Active Leaving Water Temperature Setpoint minus the Stop Delta-T.

### Automatic Pumpdown

The Model WGS chiller has two separate refrigerant circuits so the refrigerant charge is stored in the condenser when the circuit is off.  Pumpdown to the condenser helps keep refrigerant from migrating to the compressor.  It also helps establish a pressure differential on start for oil flow.  In a normal shutdown, each circuit will close its expansion valve, causing the evaporator pressure to reach a low-pressure setpoint.  Once this setpoint is reached, or a specified amount of time has elapsed, the running circuit will be shut down.

### Chilled Water and Condenser Water Pumps

The chiller’s MicroTech II( controller has a total of four pump outputs, two for the evaporator and two for the condenser (WGS-AW only).  There is a manual setting in the software for the user to select either pump output 1 or 2.  It is recommended that the chiller’s outputs control the water pumps, as this will offer the most protection for the unit.

### Cooling Tower Control

The MicroTech II controller can control the cooling tower fans and/or a tower bypass valve.  This provides a simple and direct method to control the unit’s discharge pressure.  Programming directions and the sequence of operation can be found on page 44.  Some means of discharge pressure control is recommended and must be installed if the entering condenser water temperature to the condenser can fall below 60(F.

### Condenser Fan Control

The MicroTech II controller can be programmed to cycle air-cooled condenser fans on and off based on the discharge pressure.  Details are on page 61.

Unit Controller Sequence of Operation

### Circuit Controller Sequence of Operation

# Start-Up and Shutdown

## Pre Start-up

- Flush and clean the chilled-water system.  Proper water treatment is required to prevent corrosion and organic growth.  A 20-mesh strainer is required at the evaporator chilled-water inlet and should be cleaned after system flushing.

CAUTION

Failure to flush, clean and provide system water treatment can damage the unit.

- With the main disconnect open, check all electrical connections in control panel and starter to be sure they are tight and provide good electrical contact.  Connections are tightened at the factory, but can loosen enough in shipment to cause a malfunction.

CAUTION

Lock and tag out all power sources when checking connections. Electrical shock can cause severe personal injury or death..

- Check and inspect all water piping.  Make sure flow direction is correct and that piping is made to the correct connection on evaporator and condenser.

- Check that refrigerant piping on remote condensers is connected to the correct circuits and not crossed and has been properly leak tested and evacuated.

- Open all water flow valves to the condenser and evaporator.

- Flush the cooling tower and system piping to be sure the system is clean.  Start evaporator pump and manually start condenser pump and cooling tower.  Check all piping for leaks.  Vent the air from the evaporator and condenser water circuit, as well as from the entire water system.  The cooler circuit should contain clean, treated, non-corrosive water.

- Check to see that the evaporator water temperature sensor is securely installed.

- Make sure the unit control switch S1 is open OFF and the circuit switches CS1 and CS2 are open.  Place the main power disconnect switch to ON.  This will energize the compressor sump heaters.  Wait a minimum of 12 hours before starting the unit.

- Measure the water pressure drop across the evaporator and condenser, and check that water flow is correct (on pages 25 and 26) per the design flow rates.

- Check the actual line voltage to the unit to make sure it is the same as called for on the compressor nameplate, within + 10%, and that phase voltage unbalance does not exceed 2%. Verify that adequate power supply and capacity is available to handle load.

- Make sure all wiring and fuses are of the proper size.  Also make sure that all interlock wiring is completed per McQuay diagrams.

- Verify that all mechanical and electrical inspections by code authorities have been completed.

- Make sure all auxiliary load and control equipment is operative and that an adequate cooling load is available for initial start-up.

## Start-up

- Open the compressor discharge shutoff valves until backseated.  Replace valve seal caps.

- Open the two manual liquid line shutoff valves (king valves).

- Verify that the compressor sump heaters have operated for at least 12 hours prior to start-up.  Crankcase should be warm to the touch.

- Check that the MicroTech II controller is set to the desired chilled water temperature.

- Start the system auxiliary equipment for the installation by turning on the time clock, ambient thermostat and/or remote on/off switch and water pumps.

- Switch on the unit circuit breakers.

- Set circuit switches CS1 and CS2 to ON for normal operation.

- Start the system by setting the unit system switch S1 to ON.

- After running the unit for a short time, check the oil level in each compressor, rotation of condenser fans (if any), and check for flashing in the refrigerant sight glass.

## Weekend or Temporary Shutdown

Move circuit switches CS1 and CS2 to the OFF pumpdown position.  After the compressors have shut off, turn off the chilled water pump if not on automatic control from the chiller controller or building automation system (BAS).  With the unit in this condition, it will not restart until these switches are turned back on.

Leave on the power to the unit (disconnect closed) so that the sump heaters will remain energized.

## Start-up after Temporary Shutdown

- Start the water pumps.

- Check compressor sump heaters.  Compressors should be warm to the touch.

- With the unit switch S1 in the ON position, move the circuit switches CS1 and CS2 to the ON position.

- Observe the unit operation for a short time, noting unusual sounds or possible cycling of compressors.

## Extended Shutdown

- Close the manual liquid line shutoff valves.

- After the compressors have shut down, turn off the water pumps.

- Turn off all power to the unit.

- Move the unit control switch S1 to the OFF position.

- Close the discharge shutoff valves.

- Tag all opened disconnect switches to warn against start-up before opening the compressor suction and discharge valves.

- Drain all water from the unit evaporator, condenser and chilled water piping if the unit is to be shut down during the winter and exposed to below-freezing temperatures.  To help prevent excessive corrosion, do not leave the vessels or piping open to the atmosphere over the shutdown period.

## Start-up after Extended Shutdown

- Inspect all equipment to see that it is in satisfactory operating condition.

- Remove all debris that has collected on the surface of the condenser coils (remote condenser models) or check the cooling tower, if present.

- Open the compressor discharge valves until backseated.  Always replace valve seal caps.

- Open the manual liquid line shutoff valves.

- Check circuit breakers.  They must be in the OFF position.

- Check to see that the circuit switches CS1 and CS2 and the unit control switch S1 are in the OFF position.

- Close the main power disconnect switch.  The circuit disconnects switches should be off.

- Allow the sump heaters to operate for at least 12 hours prior to start-up.

- Start the chilled water pump and purge the water piping as well as the evaporator in the unit.

- Start the system auxiliary equipment for the installation by turning on the time clock, ambient thermostat and/or remote on/off switch.

- Check that the MicroTech II controller is set to the desired chilled water temperature.

- Switch the unit circuit breakers to ON.

- Start the system by setting the system switch S1 and the circuit switches to ON.

CAUTION

Most relays and terminals in the control center are powered when S1 is closed and the control circuit disconnect is on. Therefore, do not close S1 until ready for start-up or serious equipment damage can occur.

- After running the unit for a short time, check the oil level in the compressor oil sight glass and check the liquid line sight glass for bubbles.

Figure 7, Evaporator Pressure Drop WGS 130 – WGS 190

| WGS Model | Minimum Flow | Nominal Flow | Maximum Flow |
| --- | --- | --- | --- |
|  | Flow Rate | Pressure Drop | Flow Rate | Pressure Drop | Flow Rate | Pressure Drop |
|  | gpm | L/s | Ft. | kPa | gpm | L/s | Ft. | kPa | gpm | L/s | Ft. | kPa |
| 130AW/AA | 195 | 12.3 | 5.8 | 17.4 | 312 | 19.7 | 13.5 | 40.4 | 520 | 32.9 | 33.9 | 101.1 |
| 140AW/AA | 211 | 13.4 | 6.7 | 20.0 | 338 | 21.4 | 15.6 | 46.6 | 563 | 35.6 | 39.0 | 116.5 |
| 160AW/AA | 235 | 14.9 | 4.6 | 13.8 | 376 | 23.8 | 10.8 | 32.3 | 627 | 39.7 | 27.3 | 81.6 |
| 170AW/AA | 254 | 16.1 | 5.3 | 15.9 | 407 | 25.8 | 12.5 | 37.3 | 678 | 42.9 | 31.6 | 94.2 |
| 190AW/AA | 273 | 17.3 | 6.1 | 18.1 | 437 | 27.7 | 14.2 | 42.5 | 728 | 46.1 | 35.9 | 107.2 |

Note: Minimum, nominal, and maximum flows are at a 16F, 10F, and 6F chilled water temperature range respectively and at ARI tons.

Figure 8, Condenser Pressure Drop WGS 130 – WGS 190

| Pressure Drop Without Optional Condenser Manifold |
| --- |
| WGS Model | Minimum Flow | Nominal Flow | Maximum Flow |
|  | Flow Rate | Pressure Drop | Flow Rate | Pressure Drop | Flow Rate | Pressure Drop |
|  | gpm | L/s | Ft. | kPa | gpm | L/s | Ft. | kPa | gpm | L/s | Ft. | kPa |
| 130AW | 304 | 19.2 | 4.1 | 12.2 | 390 | 24.7 | 6.5 | 19.3 | 650 | 41.1 | 16.0 | 47.9 |
| 140AW | 304 | 19.2 | 4.1 | 12.2 | 422 | 26.7 | 7.4 | 22.2 | 704 | 44.5 | 18.5 | 55.1 |
| 160AW | 304 | 19.2 | 4.1 | 12.2 | 470 | 29.8 | 9.0 | 26.9 | 784 | 49.6 | 22.4 | 66.8 |
| 170AW | 372 | 23.5 | 4.3 | 12.8 | 509 | 32.2 | 7.9 | 23.7 | 848 | 53.7 | 19.8 | 59.1 |
| 190AW | 372 | 23.5 | 4.3 | 12.8 | 546 | 34.6 | 9.0 | 26.9 | 911 | 57.6 | 22.5 | 67.1 |
| Pressure Drop With Optional Condenser Manifold |
| WGS Model | Minimum Flow | Nominal Flow | Maximum Flow |
|  | Flow Rate | Pressure Drop | Flow Rate | Pressure Drop | Flow Rate | Pressure Drop |
|  | gpm | L/s | Ft. | kPa | gpm | L/s | Ft. | kPa | gpm | L/s | Ft. | kPa |
| 130AW | 304 | 19.2 | 4.7 | 14.0 | 390 | 24.7 | 7.4 | 22.0 | 650 | 41.1 | 18.5 | 55.1 |
| 140AW | 304 | 19.2 | 4.7 | 14.0 | 422 | 26.7 | 8.5 | 25.3 | 704 | 44.5 | 21.3 | 63.5 |
| 160AW | 304 | 19.2 | 4.7 | 14.0 | 470 | 29.8 | 10.3 | 30.7 | 784 | 49.6 | 25.8 | 77.1 |
| 170AW | 372 | 23.5 | 5.3 | 15.8 | 509 | 32.2 | 9.4 | 28.1 | 848 | 53.7 | 23.8 | 71.1 |
| 190AW | 372 | 23.5 | 5.3 | 15.8 | 546 | 34.6 | 10.7 | 32.0 | 911 | 57.6 | 27.1 | 80.9 |

# Unit Controller

## Unit Inputs/Outputs

Table 1, Analog Inputs

| # | Description | Signal Source | Range |
| --- | --- | --- | --- |
| 1 | Condenser EWT or Outdoor Ambient Temp. | Thermister (10k@25°C) | -58 to 212°F |
| 2 | Demand Limit | 4-20 mA Current | 0 to 100% limit |
| 3 | Chilled Water Reset | 4-20 mA Current | 0 to 10 degrees 60(F max. |
| 4 | Leaving Evaporator Water Temp. | Thermister (10k@25°C) | -58 to 212°F |
| 5 | Entering Evaporator Water Temp. | Thermister (10k@25°C) | -58 to 212°F |

C1 = Refrigerant Circuit #1,  C2 = Refrigerant Circuit #2,  UT = Unit

Table 2, Analog Outputs

| # | Description | Output Signal | Range |
| --- | --- | --- | --- |
| 1 | Cooling Tower Bypass Valve Position | 0 to 10 VDC | 0 to 100% |
| 2 | Cooling Tower VFD Speed | 0 to 10 VDC | 0 to 100% |
| 3 | Open |  |  |
| 4 | Open |  |  |

Table 3, Digital Inputs

| # | Description | Signal | Signal |
| --- | --- | --- | --- |
| 1 | Unit Switch | 0 VAC (Stop) | 24 VAC (On) |
| 2 | Remote Switch | 0 VAC (Stop) | 24 VAC (Start) |
| 3 | Evaporator Water Flow Switch | 0 VAC (No Flow) | 24 VAC (Flow) |
| 4 | Mode Switch | 0 VAC (Cool) | 24 VAC (Ice) |
| 5 | Condenser Water Flow Switch | 0 VAC (No Flow) | 24 VAC (Flow) |
| 6 | Open |  |  |
| 7 | Open |  |  |
| 8 | Open |  |  |

Table 4, Digital Outputs

| # | Description | Load | Output OFF | Output ON |
| --- | --- | --- | --- | --- |
| 1 | Evaporator Water Pump 1 | Pump Contactor | Pump OFF | Pump ON |
| 2 | Evaporator Water Pump 2 | Pump Contactor | Pump OFF | Pump ON |
| 3 | Condenser Water Pump 1 | Pump Contactor | Pump OFF | Pump ON |
| 4 | Condenser Water Pump 2 | Pump Contactor | Pump OFF | Pump ON |
| 5 | Tower Fan 1 | Fan Contactor | Fan OFF | Fan ON |
| 6 | Tower Fan 2 | Fan Contactor | Fan OFF | Fan ON |
| 7 | Remote Run Status |  | All Circuits Off | Any Circuit On |
| 8 | Alarm | Remote Alarm | No alarm | Stop alarm |

## Unit Setpoints

The following parameters are retained during power off, are factory set to the Default value, and can be adjusted to any value in the Range column.

The Type defines whether the setpoint is part of a coordinated set of duplicate setpoints in different controllers.  Types are as follows:

N = Normal setpoint – Not copied from, or copied to, any other controller

M = Master setpoint – Setpoint is copied to all controllers in the “Sent To” column

The PW (password) column indicates the password level that must be active in order to change the setpoint.  Passwords are as follows:

O = Operator [0100]	M = Manager (8745)

Toggle: Setpoints that have two choices, such as ON and OFF are toggled between the two settings using the Up or Down keys on the controller.

NOTE: in some software versions the terms “inhibit” and “hold” are used interchangeably.

Table 5, Unit Controller Setpoints

| Description | Default | Range | Type | PW |
| --- | --- | --- | --- | --- |
| Unit |
| Unit Enable | OFF | OFF, ON | N | O |
| Unit Mode | Cool | Cool, Ice, Test | M | O |
| Control source | Switches | Switches, Keypad, Network | N | O |
| Available Modes | Cool | Cool, Cool w/Glycol, Cool/Ice w/Glycol, ICE w/Glycol, TEST | N | T |
| Cool LWT | 44 (F | 30(40) to 60 (F | N | O |
| Ice LWT | 25 (F | 20 to 38(F | N | O |
| Start Delta T | 10 (F | 0 to 10 (F | M | O |
| Stop Delta T | 1.5 (F | 0 to 3 (F | M | O |
| Stage Up Delta T | 2 (F | 0 to 3 (F | M | O |
| Stage Down Delta T | 1 (F | 0 to 3 (F | M | O |
| Max Pulldown | 5 (F/min | 0.5-5.0 (F /min | M | M |
| Evap Recirc Timer | 30 | 0 to 300 seconds | N | M |
| Evap Pump Select | #1 Only | #1 Only, #2 Only, Auto | N | M |
| Water-cooled | Yes | No, Yes | N | M |
| Cond Recirc Timer (water-cooled only) | 30 | 0 to 300 seconds | N | M |
| Cond Pump Select (water-cooled only) | #1 Only | #1 Only, #2 Only, Auto | N | M |
| LWT Reset Type | NONE | NONE, RETURN, 4-20mA, OAT | N | M |
| Max Reset | 0 (F | 0 to 20 (F | N | M |
| Start Reset Delta T | 10 (F | 0 to 20 (F | N | M |
| Soft Load | Off | Off, On | N | M |
| Begin Capacity Limit | 40% | 20-100% | N | M |
| Soft Load Ramp | 20 min | 1-60 minutes | N | M |
| Demand Limit | Off | Off, On | N | M |
| Low OAT Operation (air-cooled only) | No | No, Yes | N | M |
| Low Ambient Lockout (air cooled only) | 55 (F | -10(35) to 70 (F | N | M |
| Ice Time Delay | 12 | 1-23 hours | N | M |
| Clear Ice Timer | No | No,Yes | N | M |
| Evap LWT sensor offset | 0 | -5.0 to 5.0 deg | N | M |
| Evap EWT sensor offset | 0 | -5.0 to 5.0 deg | N | M |
| Cond EWT/OAT sensor offset | 0 | -5.0 to 5.0 deg | N | M |
| Cond LWT sensor offset | 0 | -5.0 to 5.0 deg | N | M |
| Units | (F/psi | (F/psi, (C/kPa | N | M |
| BAS Protocol | Modbus | BACnet, LonWorks, Modbus | N | M |
| Ident number | 1 | 0-200 | N | M |
| Baud Rate | 19200 | 1200,2400,4800,9600,19200 | N | M |
| Compressors |
| Sequence # Cir 1 | 1 | 1-2 | M | M |
| Sequence # Cir 2 | 1 | 1-2 | M | M |
| Max Comps ON | 2 | 1-2 | N | M |
| Start-start timer | 20 min | 15-60 minutes | M | M |
| Stop-start timer | 5 min | 3-20 minutes | M | M |
| Pumpdown Pressure | 25 psi | 10 to 40 psi | M | M |
| Pumpdown Time Limit | 120 sec | 0 to 180 sec | M | M |
| Light Load Stg Dn Point | 25% | 20 to 50% | M | M |
| Stage Up Delay | 5 min | 0 to 60 min | M | M |
| Disc. Temp Sensor Type | PT1000 | NTC, PT1000 | M | M |
| Description | Default | Range | Type | PW |
| Alarms |
| Low Evap Pressure-Unload | 28 psi | [0,26] to 45 psi | M | M |
| Low Evap Pressure-Hold | 30 psi | [0,28] to 45 psi | M | M |
| Low Oil Level Delay | 120 sec | 10-180 sec | M | M |
| High Oil Press Diff Delay | 15 sec | 0-90 sec | M | M |
| High Discharge Temperature | 200 (F | 150 to 200 F | M | M |
| High Lift Pressure Delay | 5 sec | 0 to 30 sec | M | M |
| Evaporator Water Freeze | 36 (F | 15(36) to 42 (F | N | M |
| Evaporator Flow Proof | 3 sec | 3 to 10 sec | N | M |
| Recirculate timeout | 3 min | 1 to 10 min. | N | M |
| Low OAT Start Timer (air cooled only) | 60 sec | 20 to 180 sec | M | M |
| Condenser Water Freeze (water cooled only) | 38 (F | 34 to 42 (F | N | M |
| Condenser Flow Proof (water cooled only) | 3 sec | 3 to 10 sec | N | M |
| Cooling Tower(available for Water cooled only) |
| Tower Control | None | None, Temperature | N | M |
| Tower Stages | 2 | 0 to 2 | N | M |
| Stage #1 On | 70 (F | 40 to 120 (F | N | M |
| Stage #2 On | 75 (F | 40 to 120 (F | N | M |
| Stage Differential | 3.0 (F | 1.0 to 10.0 (F | N | M |
| Stage Up Time | 2 min | 1 to 60 min | N | M |
| Stage Down Time | 5 min | 1 to 60 min | N | M |
| Stage Fan Down @ | 20% | 0 to 100% | N | M |
| Stage Fan Up @ | 80% | 0 to 100% | N | M |
| Valve/VFD Control | None | None, Valve Setpoint, Valve Stage, VFD Stage, Valve SP/VFD Stage | N | M |
| Valve Type | NC to tower | NC, NO | N | M |
| Valve Setpoint | 65 (F | 60 to 120 (F | N | M |
| Valve Deadband | 2.0 (F | 1.0 to 10.0 (F | N | M |
| Minimum Start Position | 0% | 0 to 100% | N | M |
| Minimum Position @ | 60 (F | 0 to 100 (F | N | M |
| Maximum Start Position | 100% | 0 to 100% | N | M |
| Maximum Position @ | 90 (F | 0 to 100 (F | N | M |
| Valve Control Range (Min) | 10% | 0 to 100% | N | M |
| Valve Control Range(Max) | 90% | 0 to 100% | N | M |
| Error Gain | 25 | 10 to 99 | N | M |
| Slope Gain | 25 | 10 to 99 | N | M |

### Auto Adjusted Ranges

The following settings have different ranges of adjustment based on other settings.

Table 6, Cool LWT

| Mode | Range |
| --- | --- |
| Unit Mode = Cool | 40 to 60oF |
| Unit Mode = Cool w/Glycol, Ice w/ Glycol | 20 to 60oF |

Table 7, Evaporator Water Freeze

| Mode | Range |
| --- | --- |
| Unit Mode = Cool | 34 to 42oF |
| Unit Mode = Cool w/Glycol, Ice w/ Glycol | 15 to 42oF |

Table 8, Low Evaporator Pressure Inhibit

| Mode | Range |
| --- | --- |
| Unit Mode = Cool | 30 to 45 Psig |
| Unit Mode = Cool w/Glycol, Ice w/ Glycol | 15 to 45 Psig |

Table 9, Low Evaporator Pressure Unload

| Mode | Range |
| --- | --- |
| Unit Mode = Cool | 28 to 45 Psig |
| Unit Mode = Cool w/Glycol, Ice w/ Glycol | 15 to 45 Psig |

# Circuit Controller

## Circuit Inputs and Outputs

Table 10, Analog Inputs

| # | Description | Signal Source | Range |
| --- | --- | --- | --- |
| 1 | Evaporator Pressure | 0.1 to 0.9 VDC | 0 to 132 psi |
| 2 | Condenser Pressure | 0.1 to 0.9 VDC | 3.6to 410 psi |
| 3 | Open |  |  |
| 4 | Suction Temperature | NTC Thermister (10k@25°C) | -58 to 212°F |
| 5 | Discharge Temperature | NTC Thermister (10k@25°C) | -58 to 212°F |
| 6 | Open |  |  |
| 7 | Slide Load Indicator | 4 to 20 mA | 0 to 100% |
| 8 | Condenser LWT (circuit 1, water cooled only) | NTC Thermister (10k@25°C) | -58 to 212°F |

Table 11, Analog Outputs

| # | Description | Output Signal | Range |
| --- | --- | --- | --- |
| 1 | Fan VFD (air cooled only) | 0 to 10 VDC | 0 to 100% (1000 steps resolution) |
| 2 | Open |  |  |
| 3 | EXV Driver | 0 to 10 VDC | 0 to 6386 steps (1000 steps resolution) |
| 4 | Open |  |  |

Table 12, Digital Inputs

| # | Description | Signal | Signal |
| --- | --- | --- | --- |
| 1 | Circuit Switch | 0 VAC (Off) | 24 VAC (Auto) |
| 2 | Open |  |  |
| 3 | Open |  |  |
| 4 | VFD Fault | 0 VAC (Fault) | 24 VAC (No Fault) |
| 5 | Oil Differential Pressure Switch | 0 VAC (Fault) | 24 VAC (No Fault) |
| 6 | Mechanical High Pressure Switch | 0 VAC (Fault) | 24 VAC (No Fault) |
| 7 | Open |  |  |
| 8 | Open |  |  |
| 9 | Oil Level Sensor | 0 VAC (Fault) | 24 VAC (No Fault) |
| 10-14 | Open |  |  |

The status of digital inputs may be viewed on Circuit Status screen 5, on the circuit controllers only.

Table 13, Digital Outputs

| # | Description | Output OFF | Output ON |
| --- | --- | --- | --- |
| 1 | Fan 1 Contactor (air cooled only) | Fan off | Fan on |
| 2 | Fan 2 Contactor (air cooled only) | Fan off | Fan on |
| 3 | Fan 3 Contactor (air cooled only) | Fan off | Fan on |
| 4 | Fan 4 Contactor (air cooled only) | Fan off | Fan on |
| 5 | Fan 5 Contactor (air cooled only) | Fan off | Fan on |
| 6 | Fan 6 Contactor (air cooled only) | Fan off | Fan on |
| 7 | Load/Unload Pulse | Hold load slide | Move load slide |
| 8 | Load/Unload Select | Unload | Load |
| 9 | Compressor SSS Contact | Compressor off | Compressor on |
| 10 | Open |  |  |
| 11 | Oil Heater | Heater off | Heater on |
| 12 | Interstage Injection (future use) | Injection off | Injection on |
| 13 | EXV Close Signal | EXV follows 0 –10 VDC | EXV closed, ignores 0 – 10 VDC |

## Circuit Setpoint Table

The following parameters must be remembered during power off, are factory set to the Default value, and can be adjusted to any value in the Range column.

The PW (password) column indicates the password that must be active in order to change the setpoint.  Codes are as follows:

O = Operator (100)		M = Manager

Table 14, Circuit Setpoints

| Description | Default | Range | PW |
| --- | --- | --- | --- |
| Compressor |
| Circuit Mode | enable | Disable, enable, test | M |
| Slide Control | auto | Auto, manual | M |
| Slide target | 0 | 0-100 | M |
| Compressor Size | 167 | 167, 179, 197 | M |
| Clear Cycle Timers | No | No, Yes | M |
| Full Load Amps | 10 | 1 to 9999 amps | M |
| Rated load Amps | 10 | 1 to 9999 amps | M |
| Service Factor | 125% | 100 to 199% | M |
| Ground Fault Enable | Disable | Disable, enable | M |
| Ground Fault Trip Level | 1% | 1 to 100% | M |
| Overload Class | 10 | 0 to 40 | M |
| Initial Motor Current | 225% | 50 to 400% FLA | M |
| Maximum Motor Current | 300% | 100 to 800% | M |
| Ramp Time | 7 seconds | 0 to 300 seconds | M |
| Up to Speed Time (UTS) | 10 seconds | 1 to 900 seconds | M |
| Stop Mode | CoS | Coast(CoS), volt decel(dcL) | M |
| Rated RMS Voltage | 460 volts | 100 to 1000 volts | M |
| Over Voltage Trip Level | 10% | 1 to 40% rated volts | M |
| Under Voltage Trip Level | 10% | 1 to 40% rated volts | M |
| Ovr/Undr Volt Trip Delay | 1.0 seconds | 0.1 to 90.0 seconds | M |
| Current Unbalance Trip Level | 15% | 5 to 40% | M |
| Auto Fault Reset Time | 60 seconds | 0 to 120 seconds | M |
| CT Ratio | 864:1 | 72-8000:1 | M |
| Maximum Slide Target | 100.0 | 0-100.0% | M |

Continued next page

| Description | Default | Range | PW |
| --- | --- | --- | --- |
| EXV |
| EXV control | Auto | Auto, manual | M |
| Manual EXV position | 0 | 0-6386 | M |
| Service Pumpdown | No | No,Yes | M |
| Preopen Timer (water cooled only) | 20 | 20 to 120 seconds | M |
| Sensors (NOTE 1) |
| Evap pressure offset | 0 | -10.0 to 10.0 psi | M |
| Cond pressure offset | 0 | -10.0 to 10.0 psi | M |
| Suction temp offset | 0 | -5.0 to 5.0 deg | M |
| Discharge temp offset | 0 | -5.0 to 5.0 deg | M |
| Slide Minimum Position Offset | 0 | -15 to 15% | M |
| Slide Maximum Position Offset | 0 | -15 to 15% | M |
| Fans (available for air-cooled only) |
| Fan VFD enable | On | Off, On | M |
| Number of fans | 4 | 4 to 6 | M |
| Saturated Condenser Temp Target Min | 90.0 | 80.0-110.0 oF | M |
| Saturated Condenser Temp Target Max | 110.0 | 90.0-120.0 oF | M |
| Stage 1 On Deadband | 8.0 | 1.0-20.0 oF | M |
| Stage 2 On Deadband | 10.0 | 1.0-20.0 oF | M |
| Stage 3 On Deadband | 11.0 | 1.0-20.0 oF | M |
| Stage 4 On Deadband | 12.0 | 1.0-20.0 oF | M |
| Stage 2 Off Deadband | 20.0 | 1.0-25.0 oF | M |
| Stage 3 Off Deadband | 16.0 | 1.0-25.0 oF | M |
| Stage 4 Off Deadband | 11.0 | 1.0-25.0 oF | M |
| Stage 5 Off Deadband | 8.0 | 1.0-25.0 oF | M |
| VFD Max Speed | 100% | 90 to 110% | M |
| VFD Min Speed | 25% | 20 to 60% | M |
| Forced Fantrol 1 | 2 | 1 to 4 | M |
| Forced Fantrol 2 | 3 | 1 to 4 | M |
| Forced Fantrol 3 | 4 | 1 to 4 | M |

Notes:

- Offsets are used to fine-tune certain readings generated by sensors.  For example, if the controller was showing a 125 psi value and a calibrated pressure gauge at the same location showed 127 psi, an offset of +2 psi would be entered and the controller would then read the corrected value of 127 psi.

Table 15, RLA/FLA Values

| Compressor | 575V | 460V | 380V | 230V | 208V | 400V (50Hz) |
| --- | --- | --- | --- | --- | --- | --- |
| RLA |
| 197 | 113 | 141 | 178 | 282 | 312 | 141 |
| 179 | 94 | 122 | 145 | 240 | 267 | 122 |
| 167 | 85 | 112 | 128 | 210 | 232 | 112 |
| FLA |
| All | 113 | 141 | 178 | 282 | 312 | 141 |

NOTE: Table values used for circuit controller input.

# Alarms and Events

Situations may arise that require some action from the chiller or that should be logged for future reference.  A condition that  causes a shutdown and requires manual reset is known as a stop alarm.  Other conditions can trigger what is known as an event, which may or may not require an action in response.  All stop alarms and events are logged.

## Unit Stop Alarms

The alarm output and red button led shall be turned ON when any stop alarm occurs.  They shall be turned off when all alarms have been cleared.

### Evaporator Flow Loss

Alarm description (as shown on screen): Evap Water Flow Loss

Trigger:

1:  Evaporator Pump State = Run AND Evaporator Flow Digital Input = No Flow for time > Flow Proof Set Point AND at least one compressor running

2:  Evaporator Pump State = Start for time greater than Recirc Timeout Set Point and all pumps have been tried

Action Taken: Rapid stop all circuits

Reset:  This alarm can be cleared at any time manually via the keypad or via the BAS clear alarm signal.

If active via trigger condition 1:

When the alarm occurs due to this trigger, it can auto reset the first two times each day, with the third occurrence being manual reset.

For the auto reset occurrences, the alarm will reset automatically when the evaporator state is Run again.  This means the alarm stays active while the unit waits for flow, then it goes through the recirculation process after flow is detected.  Once the recirculation is complete, the evaporator goes to the Run state which will clear the alarm.  After three occurrences, the count of occurrences is reset and the cycle starts over if the manual reset flow loss alarm is cleared.

If active via trigger condition 2:

If the flow loss alarm has occurred due to this trigger, it is always a manual reset alarm.

### Condenser Flow Loss

Alarm description (as shown on screen): Cond Water Flow Loss

Trigger:

1:  Condenser Pump State = Run AND Condenser Flow Digital Input = No Flow for time > Flow Proof Set Point AND at least one compressor running

2:  Condenser Pump State = Start for time greater than Recirc Timeout Set Point and all pumps have been tried

Action Taken: Rapid stop all circuits

Reset:  This alarm can be cleared at any time manually via the keypad or via the BAS clear alarm signal.

If active via trigger condition 1:

The alarm will reset automatically when the condenser state is Run again.  This means the alarm stays active while the unit waits for flow, then it goes through the recirculation process after flow is detected.  Once the recirculation is complete, the condenser goes to the Run state which will clear the alarm.

If active via trigger condition 2:

If the flow loss alarm has occurred due to this trigger, it is always a manual reset alarm.

### Evaporator Water Freeze Protect

Alarm description (as shown on screen): Evap Water Freeze

Trigger: Evaporator LWT drops below evaporator freeze protect set point AND Unit State = Auto  AND Evaporator LWT Sensor Fault not active

Action Taken: Rapid stop all circuits

Reset:  This alarm can be cleared manually via the keypad or via the BAS clear alarm signal, but only if the alarm trigger conditions no longer exist.

### Leaving Evaporator Water Temperature Sensor Fault

Alarm description (as shown on screen): Evap LWT Sens Fault

Trigger: Sensor shorted or open

Action Taken: Rapid stop all circuits

Reset:  This alarm can be cleared manually via the keypad, but only if the sensor is back in range.

### Entering Condenser Water Temperature Sensor Fault

Alarm description (as shown on screen): Cond EWT Sens Fault

Trigger: Sensor shorted or open

Action Taken: Rapid stop all circuits

Reset:  This alarm can be cleared manually via the keypad, but only if the sensor is back in range.

### Outdoor Air Temperature Sensor Fault

Alarm description (as shown on screen): OAT Sensor Fault

Trigger: Sensor shorted or open AND unit is aircooled

Action Taken: Rapid stop all circuits

Reset:  This alarm can be cleared manually via the keypad, but only if the sensor is back in range.

### pLAN Failure

Alarm description (as shown on screen): pLAN Failure

Trigger: No circuit controllers found on pLAN for 60 seconds

Action Taken: Rapid stop all circuits

Reset:  This alarm can be cleared manually via the keypad, but only if at least one circuit is connected to pLAN.

## Unit Events

The following unit events are logged in the event log with a time stamp.

### Entering Evaporator Water Temperature Sensor Fault

Event description (as shown on screen): Evap EWT Sens Fault

Trigger: Sensor shorted or open

Action Taken: Return water reset cannot be used.

Reset:  Auto reset when sensor is back in range.

Leaving Condenser Water Temperature Sensor Fault

Event description (as shown on screen): Cond LWT Sens Fault

Trigger: Sensor shorted or open AND unit is watercooled

Action Taken: None

Reset:  Auto reset when sensor is back in range.

## Circuit Stop Alarms

All circuit stop alarms require shutdown of the circuit on which they occur.  Rapid stop alarms do not do a pumpdown before shutting off.  All other alarms will do a pumpdown.

The red button led on the circuit controller shall be turned on when any circuit stop alarm occurs.  It shall be turned off when all circuit alarms have been cleared.  In addition, the alarm status shall be sent to the unit control so the alarm output and the red button led on the unit controller can be energized while alarms are active.

Alarm descriptions apply to both circuits, the circuit number is represented by ‘N’ in the description.

### Low Evaporator Pressure

Alarm description (as shown on screen): Evap Press Low N

Trigger: [Freezestat trip AND Compressor State = Run AND Low OAT Start not active  AND Evap Pressure Sensor Fault not active] OR [Evaporator Press < -10 psi  AND startup timer complete AND Evap Pressure Sensor Fault not active]

Freezestat logic allows the circuit to run for varying times at low pressures.  The lower the pressure, the shorter the time the compressor can run.  This time is calculated as follows:

Freeze error = Low Evaporator Pressure Unload – Evaporator Pressure

Freeze time = 70 – 6.25 x freeze error, limited to a range of 20-70 seconds

When the evaporator pressure goes below the Low Evaporator Pressure Unload set point, a timer starts.  If this timer exceeds the freeze time, then a freezestat trip occurs.  If the evaporator pressure rises to the unload set point or higher, and the freeze time has not been exceeded, the timer will reset.

Action Taken: Rapid stop circuit

Reset: This alarm can be cleared manually via the Unit Controller keypad if the evaporator pressure is above –10 psi.

### High Lift Pressure

Alarm description (as shown on screen): Lift Pressure High N

Trigger: Condenser Saturated Temperature > Max Saturated Condenser Value for time > High Lift Delay set point

Action Taken: Rapid stop circuit

Reset: This alarm can be cleared manually via the Unit Controller keypad.

### Mechanical High Pressure

Alarm description (as shown on screen): Mech High Pressure N

Trigger:  Mechanical High Pressure switch input is low

Action Taken: Rapid stop circuit

Reset: This alarm can be cleared manually via the Unit Controller keypad if the MHP switch input is high.

### High Discharge Temperature

Alarm description (as shown on screen): Disc Temp High N

Trigger: Discharge Temperature > High Discharge Temperature set point AND compressor is running  AND Discharge Temperature Sensor Fault is not active

Action Taken: Rapid stop circuit

Reset:  This alarm can be cleared manually via the Unit Controller keypad.

### Low Oil Level

Alarm description (as shown on screen): Oil Level Low N

Trigger: Oil Level Switch input is open for time greater than Low Oil Level Delay while compressor is in the Run state AND the Low Oil Level Event has occurred in the past hour.

Action Taken: Rapid stop circuit

Reset:  This alarm can be cleared manually via the Unit Controller keypad.

### High Oil Pressure Difference

Alarm description (as shown on screen): Oil Pres Diff High N

Trigger: Oil DP switch input is low for time greater than High Oil Pressure Difference Delay set point AND compressor is running

Action Taken: Rapid stop circuit

Reset:  This alarm can be cleared manually via the Unit Controller keypad.

### Low OAT Restart Fault

Alarm description (as shown on screen): LowOATRestart Fail N

Trigger: Circuit has failed three low OAT start attempts

Action Taken: Rapid stop circuit

Reset:  This alarm can be cleared manually via the Unit Controller keypad.

### No Evaporator Pressure Drop After Start

Alarm description (as shown on screen): No Evap Press Drop N

Trigger: After start of compressor, at least a 1 psi drop in evaporator pressure has not occurred after 15 seconds

Action Taken: Rapid stop circuit

Reset:  This alarm can be cleared manually via the Unit Controller keypad.

### No Pressure At Startup

Alarm description (as shown on screen): No Press At Start N

Trigger: [Evap Pressure < 5 psi OR Cond Pressure < 5 psi] AND Compressor start requested AND VFD disabled

Action Taken: Rapid stop circuit

Reset:  This alarm can be cleared manually via the Unit Controller keypad.

## Clearing Alarms

Alarms may be cleared at the unit controller and no password is required.  The BAS can clear evaporator flow loss, evaporator water freeze and pLAN failure regardless of what other alarms are active.

# Unit Controller Functions

### Calculations

### LWT Slope

LWT slope is calculated such that the slope represents the change in LWT over a time frame of one minute.

Every 12 seconds, the current LWT is subtracted from the value 12 seconds back.  This value is added to a buffer containing values calculated at the last five intervals.  The final result is a slope value that is an average over the past 60 seconds.

### Pulldown Rate

The slope value calculated above will be a negative value as the water temperature is dropping.  For use in some control functions, the negative slope is converted to a positive value by multiplying by –1.

### Unit Capacity

Unit capacity is estimated based on the slide target of each running circuit.  The capacity of a running circuit is estimated with this equation:

Circuit capacity = 0.8(slide target) + 20

A circuit that is off is assumed to be at 0% capacity.  The unit capacity is then calculated by this equation:

Unit capacity = (Circuit 1 capacity + Circuit 2 capacity)/2

## Unit Enable

Enabling and disabling the chiller is controlled by the Unit Enable Setpoint with options of OFF and ON.  Enabling allows the unit to start if there is a call for cooling and also starts the evaporator pump.

This setpoint (in other words, enabling the unit to run) can be altered by the:

Unit OFF input (unit On/Off switch)

a field installed remote stop switch

a keypad entry

a BAS request

The Control Source Setpoint determines which sources can change the Unit Enable Setpoint with options of SWITCHES, KEYPAD or NETWORK.

Changing the Unit Enable Setpoint can be accomplished according to the following table.
NOTE: An “x” indicates that the entry is ignored.

Table 20, Unit Enable Combinations

| Unit On/Off Switch | Control Source Setpoint | Remote Stop Switch | Key-pad Entry | BAS Request | Resultant Unit Enable Status |
| --- | --- | --- | --- | --- | --- |
| OFF | x | x | x | x | OFF |
| ON/OFF | SWITCHES | OFF | x | x | OFF |
| ON | SWITCHES | ON | x | x | ON |
| ON | KEYPAD | x | OFF | x | OFF |
| ON | KEYPAD | x | ON | x | ON |
| ON | NETWORK | x | x | OFF | OFF |
| ON | NETWORK | OFF | x | x | OFF |
| ON | NETWORK | ON | x | ON | ON |

Example:

- If the Control Source is set to “Switches”, enabling is controlled by the field-installed remote stop switch.  If the unit-mounted On/Off switch is either On or Off, the unit will be disabled if the remote switch is Off.  If the unit-mounted On/Off switch is On, the unit will be enabled if the remote switch is On.

### Chiller Control Source Options:

Set Unit Setpoints Screen #1 (shown below) has three fields: “Enable”, “Mode” and “Source.”

#### Unit Setpoints

SET UNIT SPs (1)

Enable=On

Mode= COOL

Source = KEYPAD

The Enable field can only be used with Source = Keypad, to enable and disable the chiller through the key pad, any other control inputs including unit and pumpdown switches and BAS controls are ignored.  The Enable field toggles between On and Off using the Up or Down key on the controller.

- The Mode field is an informational display, showing the active control mode of the chiller. It is used as an input only when the source is set to keypad, only then can this field be changed manually.

- The Source field has three options, “SWITCHES”(default), “KEYPAD”, and “BAS NETWORK”.

- Switches source is used when there is no BAS interface used.  This allows the unit switches to function as pumpdown and shut down switches for the circuit.  This option is also used with applications using the remote start/stop input and not using a BAS interface.

- Keypad source is used to override BAS or remote start/stop commands.  This would be used for servicing only.

- BAS Network source would be used for those applications using “MODBUS”, “BACnet”, or “LON” communications through a building automation system.  BAS Protocol is set at Set Unit Setpoints item #14.

All methods of disabling the chiller, except for the unit switch, will cause a normal pumpdown shutoff of any running circuits.  Any time the unit switch is used to disable the chiller, all running circuits will shut down immediately, without pumping down.

Shutdown by the unit switch without going through the pumpdown cycle is undesirable and should only be used for an emergency shutdown or for manually and locally disabling the unit after both circuits have gone through a normal shutdown.

## Unit Mode Selection

The overall operating mode of the chiller is set by the Unit Mode setpoint with options of COOL, ICE and TEST.  This setpoint can be altered by the keypad, BAS, and Mode input.  Changes to the Unit Mode Setpoint are controlled by two additional setpoints.

- Available Modes setpoint:  usually set during initial setup and determines the operational modes available at any time with options of:

COOL, cooling only operation, with setpoints available for normal chilled water temperatures

COOL w/Glycol, cooling only operation, allows lower setpoints than COOL

COOL/ICE w/Glycol, allows both cooling and ice mode operation, switchable by a field-installed remote ICE mode switch, by the BAS or through the keypad.

ICE w/Glycol, ice mode only, i.e., full load operation until LWT setpoint is reached

TEST

- Control Source Setpoint: The setting determines the source that can change the Unit Mode Setpoint with options of KEYPAD, NETWORK, or SWITCHES.

When the Control source is set to KEYPAD, the Unit Mode stays at its previous setting until changed by the operator.  When the Control source is set to BAS, the most recent BAS mode request goes into effect, even if it changed while the Control source was set to KEYPAD or DIGITAL INPUTS.

Changing the Unit Mode Setpoint can be accomplished according to the following table.

NOTE: An “x” indicates that the value is ignored.

Table 21, Unit Mode Setpoint Sources

| Control Source Setpoint | Remote ICE Mode Switch | Keypad Entry | BAS Request | Available Modes Setpoint | Resultant Unit Mode |
| --- | --- | --- | --- | --- | --- |
| x | x | x | x | COOL | COOL |
| x | x | x | x | COOL w/Glycol | COOL w/Glycol |
| SWITCHES | OFF | x | x | COOL/ICE w/Glycol | COOL w/Glycol |
| SWITCHES | ON | x | x | COOL/ICE w/Glycol | ICE w/Glycol |
| KEYPAD | x | COOL w/Glycol | x | COOL/ICE w/Glycol | COOL w/Glycol |
| KEYPAD | x | ICE w/Glycol | x | COOL/ICE w/Glycol | ICE w/Glycol |
| NETWORK | x | x | COOL | COOL/ICE w/Glycol | COOL w/Glycol |
| NETWORK | x | x | ICE | COOL/ICE w/Glycol | ICE w/Glycol |
| x | x | x | x | ICE w/Glycol | ICE w/Glycol |
| x | x | x | x | TEST | TEST |

The Remote ICE Mode Switch (usually a time clock) is a field installed option and is used to switch from ice mode operation at night to cooling mode operation during the day.  This requires that the Control Source be set to SWITCHES, which in this case refers to the Remote ICE Mode Switch.

There are really only three operational modes for the unit, although they can be used in combination:

- COOL, the unit unloading and compressor staging is controlled by the Active LWT Setpoint.  COOL w/ Glycol is a special case, providing for lower setpoint ranges.

- ICE, the unit runs with all compressors fully loaded until the LWT (set for making ice) is reached, and the unit shuts off.  The Ice Delay Timer can be set to prevent restarting until the next ice making cycle.

- TEST, manually energize controller outputs to test functionality.

### Unit Test Mode

The unit test mode allows manual testing of controller outputs.  Entering this mode shall require the following conditions.

Unit OFF input = OFF (i.e. entire chiller is shut down).

Technician password active.

Available Circuit Mode setpoint = TEST

A test menu can then be selected to allow activation of the outputs.  It shall be possible to switch each digital output ON or OFF and set the analog outputs to any value.

## Unit States

The unit will always be in one of three states.

#### Transitions:

#### T1 – Transition from Off to Auto

Requires all of the following

- Unit enabled based on settings and switches

- If unit mode is ice, the ice timer has expired

- No unit alarms exist

- At least one circuit is enabled and available to start

#### T2 – Transition from Auto to Pumpdown

Requires any of the following

- Control source is keypad and the unit enable keypad setting is “off”

- Control source is BAS and either the remote switch is “off” or the BAS command is “off”

- Control source is switches and the remote switch is “off”

#### T3 – Transition from Pumpdown to Off

Requires any of the following

- All circuits have finished pumpdown and are off

- A unit alarm is active

- Unit switch is “off”

#### T4 – Transition from Auto to Off

Requires any of the following

- Unit switch is “off”

- A unit alarm is active

- All circuits are unavailable to start (cannot start even after any cycle timers have expired)

- The unit mode is ice, all circuits are off, and the ice mode delay is active

### Ice Mode Start Delay

An adjustable start to start ice delay timer will limit the frequency with which the chiller may start in Ice mode.  The timer starts when the first compressor starts while the unit is in ice mode.  While this timer is active, the chiller cannot restart in Ice mode.  The time delay is user adjustable.

The ice delay timer may be manually cleared to force a restart in ice mode. A setpoint specifically for clearing the ice mode delay is available.  In addition, cycling the power to the controller will clear the ice delay timer.

## Evaporator Pump Control

The state-transition diagram shown below controls operation of the evaporator pump.

#### Transitions:

T1 – Transition from Off to Start

Requires any of the following

- Unit state = Auto AND  [If Low OAT Lockout active then LWT <=40]

- LWT < Freeze setpoint - 1

T2 – Transition from Start to Run

- Flow ok for time > evaporator recirculate time

T3 – Transition from Run to Off

Requires any of the following

- Unit state = Off AND LWT > Freeze setpoint

- Low OAT Lockout is active AND No compressors running AND LWT > 70°F

T4 – Transition from Start to Off

Requires any of the following

- Unit state = Off AND LWT > Freeze setpoint

- Low OAT Lockout is active AND No compressors running AND LWT > 70°F

T5 – Transition from Run to Start

Requires all of the following

- Evaporator water flow loss for time > flow proof

### Pump Selection

The pump output used will be determined by the Evap Pump Control set point.  This setting allows the following configurations:

#1 only – Pump 1 will always be used

#2 only – Pump 2 will always be used

Auto – The primary pump is the one with the least run hours, the other is used as a backup

#1 Primary – Pump 1 is used normally, with pump 2 as a backup

#2 Primary – Pump 2 is used normally, with pump 1 as a backup

#### Primary/Standby Pump Staging

The pump designated as primary will start first.  If the evaporator state is start for a time greater than the recirculate timeout set point and there is no flow, then the primary pump will shut off and the standby pump will start.  When the evaporator is in the run state, if flow is lost for more than half of the flow proof set point, the primary pump will shut off and the standby pump will start.  Once the standby pump is started, the flow loss alarm logic will apply if flow cannot be established in the evaporator start state, or if flow is lost in the evaporator run state.

#### Auto Control

If auto pump control is selected, the primary/standby logic above is still used.  When the evaporator is not in the run state, the run hours of the pumps will be compared.  The pump with the least hours will be designated as the primary at this time.

## Leaving Water Temperature (LWT) Reset

The Active Leaving Water variable shall be set to the current Leaving Water Temperature (LWT) setpoint unless the unit is in COOL mode and any of the reset methods below are selected.  The type of reset in effect is determined by the LWT Reset Type setpoint.  The Active Leaving Water variable is sent from the unit controller to all circuits for capacity control after the applicable reset is applied.

### Reset Type – NONE

The Active Leaving Water variable is set equal to the current LWT setpoint.

### Reset Type – RETURN

The Active Leaving Water variable is adjusted by the return water temperature.

The active setpoint is reset using the following parameters:

- Cool LWT setpoint

- Max Reset setpoint

- Start Reset Delta T setpoint

- Evap Delta T

Reset is accomplished by changing the Active Leaving Water variable from the Cool LWT setpoint to the Cool LWT set-point + Max Reset setpoint as the Evaporator EWT – LWT (Evap Delta T) varies from the Start Reset Delta T setpoint to 0.

Referring to the above figure as an example, the LWT is 44(F and a 10-degree maximum reset value was selected.  The Active LWT setpoint would range from the normal 44(F setting up to 54(F depending on the Evap Delta-T.  The amount of reset would be at the maximum value (10 degrees) when the Evap Delta-T is zero and at the minimum value when the Evap Delta-T is at the Start Reset Delta T value and is proportional in between.  The Start Reset Delta T function is available so that the start of reset can be adjusted.  For example, on a system with a 10-degree Delta-T, it may be desirable to not start the resetting until the evaporator Delta-T goes down to eight degrees (80% load), or some other value.

### Reset Type – 4-20 mA

The Active Leaving Water setpoint is adjusted by the 4 to 20 mA reset analog input, using:

- Cool LWT setpoint

- Max Reset setpoint

- LWT Reset signal

Reset is 0 if the reset signal is less than or equal to 4 mA.  Reset is equal to the Max Reset Delta T setpoint if the reset signal equals or exceeds 20 mA.  The amount of reset will vary linearly between these extremes if the reset signal is between 4 mA and 20 mA.   An example of the operation of 4-20 reset in Cool mode is shown below.

Reset Type – OAT

This reset can only be used if the unit is configured as air-cooled.

The Active Leaving Water variable is reset based on the outdoor ambient temperature. Parameters used:

- Cool LWT setpoint

- Max Reset setpoint

- OAT

Reset is 0 if the outdoor ambient temperature is greater than 75 F.  From 75 down to 60 F the reset varies linearly from no reset to the max reset at 60 F.  At ambient temperatures less than 60 F, reset is equal to the Max Reset setpoint.

## Planned Unit Capacity Overrides

Unit capacity limits can be used to limit total unit capacity in COOL mode only. Multiple limits may be active at any time, and the lowest limit is always used in the compressor capacity control.

The estimated unit capacity and the active capacity limit are sent to all circuits for use in compressor capacity control.

### Soft Load

Soft Loading is a configurable function used to slowly ramp up the unit capacity over a given time. The setpoints that control this function are:

- Soft Load – (ON/OFF)

- Begin Capacity Limit – (Unit %)

- Soft Load Ramp – (seconds)

The Soft Load Unit Limit increases linearly from the Begin Capacity Limit setpoint to 100% over the amount of time specified by the Soft Load Ramp setpoint.  If the option is turned off, the soft load limit is set to 100%.

### Demand Limit

The maximum unit capacity can be limited by a 4 to 20 mA signal on the Demand Limit analog input at the unit controller.  This function is only enabled if the Demand Limit setpoint is set to ON.

As the signal varies from 4 mA up to 20 mA, the maximum unit capacity changes linearly from 100% to 0%.  Although the demand limit can call for 0% capacity, this signal will never cause a running compressor to shut down.  Rather, all running compressors will be held at minimum load, and this may occur at a demand limit value that is actually less than 20mA.

### Network Limit

The maximum unit capacity can be limited by a network signal.  This function is only enabled if the unit control source is set to network.  The signal will be received through the BAS interface on the unit controller.

As the signal varies from 0% up to 100%, the maximum unit capacity changes linearly from 0% to 100%.  Although the network limit can call for 0% capacity, this signal will never cause a running compressor to shut down.  Rather, all running compressors will be held at minimum load, and this may occur at a network limit value that is actually less than more than 0%.

## Condenser Pump and Tower Control

Condenser pump and cooling tower control logic requires that the unit be configured as water-cooled in order to be active.  The unit controller controls water-cooled components such as condenser pumps and tower controls, since there is usually one tower per unit.  Air-cooled equipment, associated with the remote condenser option, is controlled by the circuit controllers.  Remote evaporative condensers require a self-contained, on-board, discharge pressure control system.

### Condenser Water Pump State Control

If the unit is configured as water-cooled, then the condenser pump is controlled by the state-transition diagram shown below.

Transitions:

T1 – Transition from Off to Start

Requires any of the following

- Unit state = Auto AND any circuit available AND LWT error  > Startup Delta

- Cond Water Freeze Alarm

T2 – Transition from Start to Run

- Flow ok for time > cond recirculation timer setpoint

T3 – Transition from Run to Off

Requires all of the following

- Unit state = Off OR No circuit available OR LWT error < Start Delta

- Cond Water Freeze Alarm not active

- No compressors running

T4 – Transition from Start to Off

Requires all of the following

- Unit state = Off OR No circuit available OR LWT error < Start Delta

- Cond Water Freeze Alarm not active

- No compressors running

T5 – Transition from Run to Start

Requires all of the following

- Condenser water flow loss for time > flow proof

- All circuits in Off state

### Pump Selection

The pump output used will be determined by the Condenser Pump Control setpoint.  This setting allows the operator to select pump #1, pump #2, or auto.   The first two selections will use a single pump output all the time.  The auto selection will start the pump with the least run hours.

The selected output will be ON if the Evap State is set to START or RUN.  Both outputs will be OFF if the Evap State is set to OFF.

## Cooling Tower Control

### Tower Fans

Tower fan control is active when the unit is set up as water-cooled, Tower Control is set to Temperature, and the condenser pump is in the RUN state.  Staging is based on Condenser Entering Water Temperature.  Operation depends on the following parameters.

- Condenser pump state

- Condenser EWT

- Stage up and stage down timer values

- Tower setpoints (Tower Control, Tower Stages, Stage Up Time, Stage Down Time, Stage Differential, Stage #1 ON, Stage #2 ON, Stage Down @, Stage Up @)

When the condenser pump starts, the stage up timer shall start.  The first stage shall turn ON when the following conditions are met:

- The stage up timer completes

- The Condenser EWT is > Stage #1 ON setpoint

- Bypass valve position is > the Stage Up @ setpoint (only if Valve/VFD Control setpoint = Valve Stage)

- VFD Speed is > the Stage Up @ setpoint (only if Valve/VFD Control setpoint = VFD Stage OR Valve SP/VFD Stage)

Additional stages can turn on (up to the number specified by the Tower Stages setpoint) when above conditions are met for the next stage.

Down staging shall occur when the following conditions are met:

- The stage down timer completes

- The Condenser EWT is < Stage #X ON (Temp) setpoint – Stage Differential (Temp) setpoint

- Bypass valve position is < the Stage Down @ setpoint (only if Valve/VFD Control setpoint = Valve Stage)

- VFD Speed is < the Stage Down @ setpoint (only if Valve/VFD Control setpoint = VFD Stage OR Valve SP/VFD Stage)

Each stage up or stage down event shall restart both the stage up and stage down timers.  Only one fan output shall be switched at a time (except that all outputs switch OFF when the condenser pump state equals OFF).

### Cooling Tower Bypass Valve

When the Valve/VFD Control setpoint is set to None OR VFD Stage, this output shall be set to 0.  Otherwise, it shall be controlled as described below.

#### Initial Valve Position

When the condenser pump is not in the RUN state, the valve output shall be set as a function of entering condenser water temperature (ECWT)) per the following graph.

#### Operation After Start

When the condenser pump is in the RUN state, the valve output shall be controlled in one of two modes as specified by the Valve/VFD Control setpoint.  The controlled parameter shall be the condenser entering water temperature.  When the desired output signal varies from 0 to 100%, the output voltage shall vary as shown below.

0 to 10 VDC (Valve Type = NC to tower)

10 to 0 VDC (Valve Type = NO to tower)

#### Valve Setpoint Mode

This mode is operational when the Valve/VFD Control setpoint is set to Valve setpoint OR Valve SP/VFD Stage.  In this mode the valve output is varied with a proportional-derivative (PD) algorithm (with deadband) in order to maintain the controlled parameter (CP) at the desired value.  The output is always limited between the Valve Control Range (Min) setpoint and the Valve Control Range (Max) setpoint.  A valve increment shall be computed once every 5 seconds according to the following equation.

- Increment = [(Error) * (Error Gain setpoint)] + [(Slope) * (Slope Gain setpoint)] Where:	Error = ECWT – Valve Setpoint Slope = (Present CP) – (Previous CP)

When the Error is > the Valve Deadband setpoint, the valve position analog output (% of full scale) is updated according to the following equation.

- New %Position = Old %Position + Increment/10.

#### Valve Stage Mode

This mode is only operational when the Valve/VFD Control setpoint is set to Valve Stage.  In this mode the valve output is controlled as for Valve setpoint mode (above) except that the active setpoint for the controlled parameter is selected according to the following table.

| # of Fans ON | Active Setpoint |
| --- | --- |
| 0 | Valve Setpoint |
| 1 | Stage #1 ON |
| 2 | Stage #2 ON |

### Cooling Tower Fan VFD

When the Valve/VFD Control setpoint is set to None, Valve Setpoint, OR Valve Stage, this output shall be set to 0.  Otherwise, it shall be controlled in a manner identical to Valve Stage Mode (above) except that (1) it shall be kept at zero until the first fan stage is ON and (2) the following setpoints do not apply.

Valve Control Range (Min)

Valve Control Range (Max)

Valve Type

## Evaporative Condenser Control

It is acceptable to use WGS-A chillers (less condenser) with evaporative condensers.  It is the installer's responsibility to provide the evaporative condenser control because this condenser type is not available from McQuay.  The WGS-A software does not directly support evaporative-cooled applications since there is a variety of fan configurations and pumps available from the manufacturers of evaporative condensers.  In addition, the WGS software does not support the auxiliary functions of the evaporative condenser such as make up water valves, sump drain valves, electronic make up water valves, water freeze protection, variable frequency drives, damper controls or water treatment options.  The WGS software will provide equipment protection and operational limits as if it were a remote air-cooled condenser application.   See other sections of this manual for complete descriptions.

The system must be comprised of two controls systems that operate together to make a complete system.  First, the WGS-A software provided with the unit will control the indoor chiller section of the unit including compressor loading/unloading, equipment protection, BAS interface  (when applicable), and other functions as described in this manual without the condenser control.  The WGS software setup shall be treated as a remote air-cooled application.  The second control system is required to control the condenser and auxiliary functions.  The best method for interfacing the two systems is through the "first on, last off" fan contacts as if the application was a remote air-cooled condenser.  At start up of the compressors, the Fan 1 Contactor fan contacts will close and activate the condenser control system provided by others.  At shut down, the reverse occurs where the condenser control will be deactivated when the compressor stops as the Fan 1 fan contacts open.

Special considerations must be given to the condenser control including (but not limited to) the following items.

- All WGS-A chillers have two refrigerant circuits and an evaporative condenser with two refrigerant circuits is also required.

- A control system for each refrigerant circuit is required.  It is best to have separate fans and pumps for each refrigerant circuit to prevent "fighting" of control signals between the two refrigerant circuits.

- The control system shall maintain a minimum condenser pressure at all times.

- The normal control philosophy is to maintain the lowest possible condensing pressure above the minimum allowable to provide the best operating efficiency throughout the chiller's entire operating range.

- For a normal starting sequence, it is best to start the fans first with minimum airflow.  As the condenser pressure rises, increase the airflow by increasing the fan RPM, opening inlet vanes, opening outlet dampers, or other meaning of increasing airflow.  If condensing pressure continues to rise after maximum airflow is reached, start the circulating pump (s).  Reverse the sequence for the shut down procedure.

- Provide the maximum number of condenser staging steps as possible to provide as stable operation as possible.

- Recognize that condenser pressure will change drastically and rapidly, when the water pump starts and stops.  This is the reason for starting the fan first in an increasing capacity situation and stopping the fan operation last with a shutdown procedure.

- It is important for the control pressure settings for the fans and pumps to have a large control band so that condenser component cycling does not occur.  It is also good practice for the fan and pump control to "overlap".  Overlap means that the control bands must be determined so that there is a pressure range between when a pump starts/ stops with fan operation.  Use caution to be certain that fan & pump cycling does not occur which causes rapid changes in condensing pressure which causes instability in the refrigeration system.

- Refer to the installation, operation and maintenance manuals of the manufacturer of the evaporative condenser for their guidelines and recommendations.  Give special consideration to preventing freezing conditions, make up water, and other functions common to evaporative condensers that should be described in those brochures.

CAUTION

Use water treatment with evaporative condensers. Failure to prevent microbiology growth, scaling and corrosion can damage the unit.

- Damage caused or contributed by improper water treatment may not be covered by McQuay’s warranty.

- For recommendations and answers to system questions, contact the McQuay Applications Group in Staunton, Virginia.

Building Automation System (BAS) interface and monitoring is an optional accessory required for many systems.  The WGS-A interface options are communication cards supporting LONWORKS, BACnet or Modbus.  Refer to the other McQuay brochures listed in this manual for a complete description of capabilities.  As a general statement, the McQuay communication cards do NOT support the evaporative condenser.  The desired interface points for the condenser must be provided by others and through the control system provided with the evaporative condenser.  Use caution in the ability to change condenser setpoints through the BAS system as such changes can impact chiller operation.

# Circuit Controller Functions

## Refrigerant Calculations

### Refrigerant Saturated Temperature

Refrigerant saturated temperature is calculated from the pressure sensor readings for each circuit.  The pressure will be fitted to a curve made up of 12 straight line segments.  The points used to define these segments are shown in the following tables.

Table 22, Evaporator Pressure Conversion:

| Pressure (PSI) | Temperature (oF) |
| --- | --- |
| 0 | -15.0 |
| 7.1 | 0 |
| 19.0 | 20.0 |
| 34.7 | 39.0 |
| 50.7 | 54.0 |
| 70.4 | 69.0 |
| 99.6 | 87.0 |
| 129.2 | 102.0 |
| 166.8 | 118.0 |
| 205.4 | 132.0 |
| 246.5 | 145.0 |
| 320.0 | 165.0 |
| 428.5 | 188.1 |

Table 23, Condenser Pressure Conversion:

| Pressure (PSI) | Temperature (oF) |
| --- | --- |
| 0 | 0.6 |
| 17.5 | 18.5 |
| 31.5 | 35.9 |
| 50.0 | 53.7 |
| 76.0 | 73.4 |
| 115.0 | 95.6 |
| 161.5 | 116.2 |
| 185.0 | 125.2 |
| 260.0 | 149.2 |
| 284.5 | 155.9 |
| 349.5 | 172.0 |
| 365.5 | 175.5 |
| 428.5 | 188.1 |

### Circuit Operating Mode

The circuits on the chiller can each be individually enabled or disabled.  Test mode on each circuit can also be entered independent of all other circuits.  With the circuit switch on, the circuit mode setpoint offers settings of either enable or disable.  This simply allows the circuit to be disabled through a keypad setting.

### Circuit Test Mode

The circuit test mode allows manual testing of all controller outputs.  Entering this mode requires the following conditions.

Circuit Switch = OFF

Technician password active

Circuit Mode setpoint = TEST

A test menu can then be selected to allow activation of the outputs.  It is possible to switch each digital output ON or OFF and set the analog outputs to any value.  Upon entering test mode, all outputs will always default to the off state.  Upon leaving test mode, all outputs will automatically reset to the off state.

Compressors cannot be started in TEST mode.

## Compressor Control

### Multiple Compressor Staging

This section defines which compressor is the next one to start or stop.   Compressors with fewer starts will normally start first, and compressors with more run hours will normally stop first.

#### Functions

Can start/stop compressors according to an operator defined sequence.

Can start compressors based on number of starts (run hours if starts are equal) and stop on run hours.

The above two modes can be combined, so that there are two or more groups, where all compressors in the first group are started (based on number of starts/hours) before any in the second group, etc.  Conversely, all compressors in a group are stopped (based on run hours) before any in the preceding group, etc.

#### Multiple Compressor Start/Stop Timing – Cool Mode

This section defines when a compressor is to start or stop when the chiller is operating in cool mode.

Required Parameters

Startup Delta T setpoint.

Stage Up Delta T setpoint

Stage Down Delta T setpoint

Stop Delta T setpoint

LWT error (See definition under Compressor Capacity Control section.)

Full load indicator for each compressor

#### Full Load Indicator

A circuit is considered to be at full load in the compressor staging logic when any of the following occur:

Slide control = manual

A low or high pressure limit event has been active for 10 seconds

Slide target >= 75% AND max slide target  > 75%

Slide target >= max slide target AND max slide target <= 75%

#### Starting

A compressor will start (stage up):

IF LWT is above the Active LWT Setpoint plus the  Startup Delta-T SP AND no compressors are running OR all running compressors are at full load

Stopping

A compressor will stop (stage down);

IF LWT is below the Active LWT Setpoint minus the Stop Delta-T SP AND other compressors are running or not;

OR IF LWT is below the Active LWT Setpoint minus the Stop Delta-T SP AND all other running compressor’s slide position is less than the light load stagedown setpoint.

### Multiple Compressor Start/Stop Timing – Ice Mode

This section defines when a compressor is to start or stop when the chiller is operating in ice mode.

#### Required Parameters

Startup Delta T setpoint.

Stage Up Delta T setpoint

LWT error (See definition under Compressor Capacity Control section.)

#### Starting

A compressor will start (stage up):

IF  LWT is above the Active LWT Setpoint plus the  Startup Delta-T SP AND no compressors are running OR all running compressors are at full load.

#### Stopping

The compressor will stop.

IF LWT reaches the ICE LWT Setpoint

### Compressor Capacity Control

Compressor capacity is determined by calculating a slide position target. Adjustment to the slide target for normal running conditions occurs every 5 seconds.  For loading a maximum change of 1% is allowed, and for unloading a maximum change of 2% is allowed.

#### Required parameters

Count In Load Balance status for each compressor

Slide targets of all compressors

LWT error

LWT slope

#### LWT Error

LWT error compares the actual LWT to the active LWT setpoint.  The equation is:

LWT error = LWT – active LWT setpoint

#### LWT Slope

LWT slope is calculated in the unit controller and sent to circuits via pLAN.

In the unit controller, this value is calculated such that the slope represents a time frame of one minute.

Every 12 seconds, the current LWT is subtracted from the value 12 seconds back.  This value is added to a buffer containing values calculated at the last five intervals.  The final result is a slope value that is an average over the past 60 seconds.

#### Count In Load Balance Flag

A circuit will be counted for load balancing only if all of the following are true:

- Compressor state is run

- Compressor is able to load up (no limits in effect due to pressure or superheat)

- Slide control is auto

- Slide position target is less than the max slide target setpoint

#### Cool Mode

When the chiller is in COOL mode, capacity of the compressor is adjusted to maintain leaving water temperature at the Active LWT setpoint while balancing the load between running circuits.  Load balance offset, LWT error, and LWT slope are used to calculate a change in slide position as described below.

Load balance offset:
IF other compressor is flagged to be counted in load balance

THEN Load Balance Offset = slide target - (cir 1 target + cir 2 target)/2

ELSE Load Balance Offset = 0

LWT Error:

LWT Error = (Leaving Evaporator Water Temp) – (Active LWT setpoint).

LWT slope:

Slope (deg/minute)  = sum of last five LWT changes as calculated every 12 seconds

# Slide target adjustment = [LWT Error + (LWT Slope x 4) – Load Balance Offset] / # Compressors Running

### Ice Mode

In ICE mode, the compressor capacity is increased at the maximum rate continuously until reaching the maximum slide position.  Load balancing, LWT error, and LWT slope are ignored.

### Low OAT Start Logic

In order to avoid low pressure alarms at the start of a circuit, low OAT start logic allows for running at low pressures for a longer time than normal, as well as multiple start attempts.  This logic is only used for air-cooled operation.

A low OAT start is initiated if the condenser saturated temperature is less than 60(F when the compressor starts.  Once this happens, the circuit is in the low OAT start state for a time equal to the low OAT start timer setpoint.  During this time, the freezestat logic and the low pressure events are disabled.  The absolute limit of –10 psi is still enforced.

At the end of the low OAT start, the evaporator pressure is checked.  If the pressure is greater than, or equal to, the low evaporator pressure unload setpoint, the start is considered successful.   If the pressure is less than the unload setpoint, the start is not successful and the compressor will stop.  Three start attempts are allowed before tripping on the restart alarm; so if on the third attempt the start is not successful, the restart alarm is triggered.

The restart counter will be reset when either a start is successful or the circuit is off on an alarm.

## Internal Capacity Overrides

The following conditions override the automatic slide control when the chiller is in COOL mode or ICE mode.  These overrides keep the circuit from entering a condition in which it is not designed to run.  Any compressor running with capacity limits because of these conditions is considered to be at full load in the compressor staging logic.

#### Low Evaporator Pressure

If the evaporator pressure drops below the Low Evaporator Pressure Hold setpoint while the compressor is running, the Low Evaporator Pressure Inhibit (Hold) event is triggered.  When triggered, the compressor will not be allowed to increase in capacity.

If the evaporator pressure drops below the Low Evaporator Pressure Unload setpoint while the compressor is running, the Low Evaporator Pressure Unload event is triggered. When triggered, the compressor will begin reducing capacity.  The maximum allowed slide target will be adjusted down 5% every 5 seconds until the evaporator pressure rises above the Low Evaporator Pressure-Unload setpoint.

These events are logged to an event log when they occur.  Both remain active until the evaporator pressure rises above the hold setpoint plus 2 psi, or the circuit goes to a state other than Run.

#### High Lift Pressure

If the compressor is running and the condenser pressure rises above the High Lift Pressure Hold setpoint, the High Lift Pressure Inhibit event is triggered.  When this happens, the compressor will not be allowed to increase capacity. This event is active until the condenser pressure drops 10 psi below the hold setpoint.

If the compressor is running above minimum load capacity and the condenser pressure rises above the High Lift Pressure Unload setpoint, the High Lift Pressure Unload event is triggered.  When this happens, the compressor will begin reducing capacity.  The maximum allowed slide target will be adjusted down 5% every 5 seconds until the condenser pressure drops below the High Condenser Pressure Unload setpoint.  The compressor will not be allowed to increase in capacity until the condenser pressure drops to 10 psi below the unload setpoint.

### Maximum LWT Pulldown Rate

The maximum rate at which the leaving water temperature can drop is limited by the Maximum Rate setpoint, only when the LWT is less than 60oF and the unit mode is Cool.  A slope unload factor is used to reduce the slide target if the pulldown rate exceeds the Maximum Rate setpoint.

Slope Unload Factor: Maximum Rate + LWT slope

If the pulldown rate is too fast, then the slide adjustment made will be equal to the slope unload factor.

### High Water Temperature Capacity Limit

If the evaporator LWT exceeds 55(F, compressor slide position will be limited to a maximum of 75%.  Compressors shall unload to 75% or less if running at greater than 75% slide position when the LWT exceeds the limit.  This feature is to keep the circuit running within the capacity of the condenser coil.

### Unit Capacity Overrides

Unit capacity limits override the automatic slide control when the chiller is in COOL mode only. The active capacity limit as well as the estimated unit capacity will be calculated in the unit controller and sent to all circuits.

If the unit capacity is greater than the active capacity limit, then no circuit will increase slide position.  If the unit capacity is greater than the active limit plus 1%, the circuits will unload until the unit capacity is less than 1% greater than the active limit.

### Pumpdown

When a circuit reaches a condition where the compressor needs to shut down normally, a pumpdown will be performed.  The slide target will automatically go to 0 while pumping down, and the compressor will run until the pumpdown pressure has been reached, or the pumpdown time has been exceeded.

#### Service Pumpdown

If the option for a service pumpdown is enabled, then on the next pumpdown the pressure setpoint will be 5 psi.  The circuit will pumpdown to this pressure and shut off.  When the compressor has completed the service pumpdown, the setpoint is reset to No.

## Slide Positioning

### Slide Position Indicator

Each compressor estimates its slide load percentage from the present value of the slide position indicator.  The percentage is based on the 4-20mA signal from the slide load indicator.  A percentage value of 0 corresponds to approximately a 4mA signal, a percentage value of 100 corresponds to approximately a 20mA signal.

### Slide Calibration Procedure

Slide Position is a relative capacity adjustment from 0.0%(Min load) to 100.0%(Max Load).  There are two MicroTech readings that apply to the indicator, Slide Target and Slide Position.  It is important to understand the difference between these.  The Slide Target is the value in which the controller uses to display the calculated prediction of slide position, this value represents the destination or goal of pulsing the load and unload solenoid coils. The slide target is used for direction of control for all load and unload operations, including alarm limit events.  When putting a circuit in Manual mode, the slide target is the value that you will be adjusting.   The controller will load or unload the chiller to match, with in about 3%, the target entered with the current slide position value.  The second value is the Slide Position (Pos) this is the slide position value which is the 4-20mA reading received from the position indicator.  These values can be viewed at the circuit controller on screen “VIEW CIR STATUS (1)”.

A slide target of 0.0% is fully unloaded and the unload solenoid will be constantly energized. A slide target of 100.0% means that the chiller is at full load and the load solenoid is continually energized.  The chiller will regulate the slide position to infinite steps between 0% and 100% by pulsing the appropriate solenoid.  Facing the discharge end of the compressor, looking along the left side, the solenoid coil on the top is for load (oil vent) and the solenoid coil on the side is for unload (oil feed).  During normal operation, the controller makes decisions to move the Slide target, the calculated value, and pulses the proper solenoid in order to keep the actual and the target position with in a few percent.

### Calibration Procedure:

- The circuit to be calibrated should be near normal operating temperatures.  Note that the compressor requires sufficient oil pressure to unload the compressor while it is running, and may load up due to lack of oil feed pressure.

- On the Circuit controller, first verify what your current slide target is at screen “View Circ Status (1)” and then go to screen “SET COMP SPs (2)” to switch circuit into manual slide control.  Note:  Some hold limits will be ignored but all alarm limits are still active while in manual slide control.

- Slowly take the circuit to 0% slide position.  When the slide target is at 0%, verify that the unload coil is energized.

- Find the slide indicator device located on the left side of the compressor facing the discharge end.  Unscrew the metal cap and press the calibrate button beside the LED.  The red LED will come on for about 30 seconds and then start to blink.  The indicator is now calibrated at 0%.

- Now, slowly take the circuit to 100% slide position, watching that the suction pressure and other unit readings are OK.  Always keep discharge superheat above 22°F.  When the slide target is at 100%, verify that the load coil is energized.  Press the calibrate button.  The red LED will come on for about 30 seconds and then the green LED will come on.   The indicator is now calibrated at 100%.

- The mechanical calibration is now complete for the compressor you are working with. Replace the calibration cap.

- Once you have the mechanical slide calibration complete you may fine tune the calibration from the circuit controller, if necessary.  On the circuit controller scroll all the way to the right, this is the calibration and offsets menu.  Scroll down until you see “SET SENSOR OFFSET(3)”.  You will see an adjustment for Min Load and Max Load and on the bottom line you will see the value of actual slide position indicator.  Add offset until value is within +/-.5% of the corresponding full load or minimum load position.

- Repeat calibration procedure until all circuits have min and max positions calibrated.

Note: The Slide Indicator Transducers may vary a considerable amount with temperature change, and therefore they need to be calibrated at typical running temperatures.

### Manual Slide Control Mode

The slide position on each circuit can be controlled manually.  A setting on the compressor setpoints screen in each circuit controller allows the operator to select manual slide control.  On the same screen, a slide target can be selected, from 0% to 100%.

Anytime a circuit is in manual slide control, it is considered to be at full load in the staging logic.  It also will not be considered in load balancing calculations.  None of the capacity limits outlined above will apply in manual slide control, but all stop alarms are still applicable.

Slide control will revert back to automatic control if a stop alarm occurs on the circuit or unit, or the slide control has been manual for four hours.

### Slide Pulse

The slide pulse output moves the compressor slide in order to reach the capacity requested by the slide position target.  The output will pulse for 200 ms every 6 seconds while the Slide Pulse flag is true, that is, whenever there is a difference between the actual slide position and the requested position.

## Expansion Valve Control

The electronic expansion valve (EXV) can be in one of four control states.  Each state is described below.

### Preopen

The preopen state occurs before the compressor starts. This mode is used only in water-cooled operation, and helps prime the evaporator prior to starting as well as getting the EXV in a better starting position.  During preopen, the EXV signal is held at 3000 steps.

### Pressure Control

In pressure control, the evaporator pressure is controlled by the EXV position.  The pressure target varies based on evaporator LWT and discharge superheat values.  A PID logic will be used to control the pressure to the target value.

The base pressure target is calculated using the following formula:

Base target = 0.6(LWT) – 2

The base target is limited to a range from the low pressure inhibit setpoint plus 2 psi, up to 52 psi.

The pressure control target may be adjusted if the discharge superheat is not within an acceptable range.  If the superheat is less than 22 degrees F, the base pressure target will be reduced by a value equal to the low superheat error.  If the superheat is more than 40 degrees F, the base pressure target will be increased by a value equal to the high superheat error.  At any time, the adjusted target pressure cannot go below the low pressure inhibit setpoint or above 52 psi.

When the EXV transitions to the pressure control state, the target will start at the current evaporator pressure value.  The pressure target will then decrement 0.2 psi every second until reaching the normal calculated target.  If the pressure at transition is less than the calculated target, then pressure control will start immediately with the calculated target.

### Superheat Control

In superheat control, suction superheat is controlled directly by the EXV.  The superheat target varies linearly from 6 to 10 degrees F as discharge superheat changes from 30 degrees F to 22 degrees F.  A PID logic will be used to control the superheat to the target value.

When the EXV transitions to the superheat control state, the target will start at the current suction superheat value.  This target will then decrement 0.1F every second until reaching the normal target.

### Closed

Any time the EXV is not in pressure control or superheat control, it will be in a closed state.  At this time, the EXV position is 0 steps and the EXV close signal (digital output) is active.

### EXV State Transitions – Water-cooled

Any time the EXV is not in pressure control or superheat control, it will be in a closed state.  At this time, the EXV position is 0 steps and the EXV close signal (digital output) is active.

Transitions:

T1 – Transition from Closed to Preopen, Requires all of the following:

- Unit State = Auto

- Evap State = Run

- Compressor is available

- Compressor is next on

- Stage up now flag is set

- Compressor State = Off

T2 – Transition from Preopen to Pressure Control, Requires the following:

- EXV State has been Preopen for a time greater than the preopen timer setpoint

T3 – Transition from Pressure Control to Superheat Control, Requires all of the following:

- Suction Superheat > Superheat target

- Evap LWT <= 60°F

- EXV State = Pressure AND Discharge Superheat >= 22°F for at least 3 minutes

T4 – Transition from Superheat Control to Pressure Control, Requires any of the following

- Evap LWT > 63°F

- Low Evap Pressure Unload event active

- Discharge Superheat < 22°F or > 40°F

T5, T6, T7 – Transition from any state to Closed state, Requires the following

Compressor State not Run

### EXV State Transitions – Air-cooled

The following state diagram shows the transitions between EXV control states for air-cooled operation only.

Transitions:

T1 – Transition from Closed to Pressure Control, Requires all of the following:

- Unit State = Auto

- Evap State = Run

- Compressor is available

- Compressor is next on

- Stage up now flag is set

- Compressor State = Off

T2 – Transition from Pressure Control to Superheat Control, Requires all of the following:

- Suction Superheat >= Superheat target

- Evap LWT <= 60°F

- EXV State = Pressure AND Discharge Superheat >= 22°F for at least 3 minutes

- Discharge Temperature <= 180°F

T3 – Transition from Superheat Control to Pressure Control, Requires any of the following:

- Evap LWT > 63°F

- Low Evap Pressure Unload event active

- Discharge Superheat < 22°F

- Discharge Temperature > 185°F

T4, T5 – Transition from any state to Closed state, Requires the following:

- Compressor State not Run

### EXV Control Range

The table below shows the EXV range of steps (positions) for each size compressor, at minimum and maximum capacity, as determined by the slide position.  The minimum and maximum values vary linearly with slide position, defining a new EXV control range for every change in slide position.  Thus, the range of EXV steps allowed (minimum and maximum step) increases as the load increases and more refrigerant flow is required.  The minimum and maximum opening also increases as the compressor size, and its capacity and motor cooling requirement, increases.

| EXV | UnloaderSlide % | Compressor Size |
| --- | --- | --- |
|  |  | 167 | 179 | 197 |
| Min | 0 | 250 | 250 | 250 |
| Max | 0 | 3000 | 3000 | 3000 |
| Min | 100 | 870 | 1080 | 1300 |
| Max | 100 | 3400 | 4200 | 5000 |

Based on the values in the above table, the EXV control range varies as shown in the table below.  The shaded area the control range.  The control range considers factors such as providing sufficient refrigerant flow for motor cooling and preventing liquid flood-back.

Manual EXV Control

The EXV position can be set manually.  Manual control can only be selected when the compressor is in the run state.  At any other time, the EXV control setpoint is forced to auto.

When EXV control is set to manual, the EXV position is equal to the manual EXV position setting.  If set to manual when the compressor state transitions from run to another state, the control setting is automatically set back to auto.

## Oil Heater Control

The oil heater shall be on when the compressor is not running AND the oil level input is closed for 15 seconds.  This output will turn off immediately when either the oil level switch opens or the compressor state is no longer off.

## Starter Communications

The Modbus protocol is used to establish communications between the compressor starter and the circuit controller on the supervisor port, with the circuit controller acting as the master and the starter as the slave.

Table 24, Parameters to be Read/Written:

| Register | Description | R/W | Range | Units |
| --- | --- | --- | --- | --- |
| 1020 | Starter Control | R/W | Bit Mask 0: Run/Stop 1: Fault Reset | - |
| 1021 | Starter Status | R | Bit Mask 0: Ready 1: Running 2: UTS 3: Alarm 4: Fault 5: Lockout | - |
| 1026 | Avg Current | R |  | Amps |
| 1027 | L1 Current | R |  | Amps |
| 1028 | L2 Current | R |  | Amps |
| 1029 | L3 Current | R |  | Amps |
| 1032 | Avg Voltage | R |  | Volts |
| 1033 | L1-L2 Voltage | R |  | Volts |
| 1034 | L2-L3 Voltage | R |  | Volts |
| 1035 | L3-L1 Voltage | R |  | Volts |
| 1037 | PF | R | -99 to 100 (in 16 bit two’s compliment signed format) | 0.01 |
| 1038 | KW | R |  | KW |
| 1039 | KVA | R |  | KVA |
| 1045 | Motor FLA | R/W | 1-9999 | Amps |
| 1046 | Motor RLA | R/W | 1-9999 | Amps |
| 1057 | Ground Fault Trip Enable | R/W | 0: Disabled 1: Enabled | - |
| 1058 | Ground Fault Trip Level | R/W | 1-100 | % RLA |
| 1078 | Fault Code – Most Recent Fault Log Entry | R |  | - |

Read-only parameters are displayed at the circuit controller, and sent over pLAN to the unit controller where they will also be displayed.  Read/write parameters are accessible at the circuit controller only.  These read/write parameters are changeable when the starter communication is working and the proper password is active.

### Starter Faults

Starter faults can be viewed from the unit controller.  Some starter faults will be implemented as unique alarms, and others are grouped into a generic starter fault alarm.  The most recent fault code shall be stored in the alarm log parameter list.  The fault reset signal is sent to the starter when the operator clears the active alarm on the unit controller.

The starter fault codes and their corresponding alarms are shown in the table below:

Table 25, Starter Fault Codes

| Fault Code | Starter Fault Description | Alarm Triggered |
| --- | --- | --- |
| 00 | No Fault | N/a |
| 01 | UTS Time Limit Expired | No Starter Transition |
| 02 | Motor Thermal Overload Trip | Compressor Current Overload Trip |
| 10 | Phase Rotation Error, not ABC | Phase Reversal |
| 12 | Low Line Frequency | Starter Fault |
| 13 | High Line Frequency | Starter Fault |
| 15 | Input power not three phase | Phase Loss |
| 21 | Low Line L1-L2 Voltage | Undervoltage |
| 22 | Low Line L2-L3 Voltage | Undervoltage |
| 23 | Low Line L3-L1 Voltage | Undervoltage |
| 24 | High Line L1-L2 Voltage | Overvoltage |
| 25 | High Line L2-L3 Voltage | Overvoltage |
| 26 | High Line L3-L1 Voltage | Overvoltage |
| 27 | Phase Loss | Phase Loss |
| 28 | No Line Voltage | Undervoltage |
| 30 | Instantaneous Overcurrent | Compressor Current Overload Trip |
| 31 | Overcurrent | Compressor Current Overload Trip |
| 37 | Current Imbalance | Motor Current Imbalance |
| 38 | Ground Fault | Ground Fault Protection |
| 39 | No Current at Run | Low Motor Current |
| 40 | Shorted/Open SCR | Starter Fault |
| 47 | Stack Protection Fault | Starter Fault |
| 48 | Bypass Contactor Fault (on Stop Input) | No Starter Transition |
| 50 | Control Power Low | Starter Fault |
| 51 | Current Sensor Offset Error | Starter Fault |
| 52 | Burden Switch Error | Starter Fault |
| 60 | Thermistor Trip (on DIN#1) | High Motor Temperature |
| 61 | Stack OT Switch Trip (on DIN#2) | Starter Fault |
| 71 | Analog Input Trip | Starter Fault |
| 82 | Modbus Timeout | Starter Fault (detected by circuit controller) |
| 94 | CPU Error – Software Fault | Starter Fault |
| 95 | CPU Error – Parameter Storage Fault | Starter Fault |
| 96 | CPU Error – Illegal Instruction Trap | Starter Fault |
| 97 | CPU Error – Software Watchdog Fault | Starter Fault |
| 98 | CPU Error – Spurious Attempt | Starter Fault |
| 99 | CPU Error – Program Storage Fault | Starter Fault |

If a starter fault is active and the active alarms are cleared at the unit controller, the clear alarm signal will also be sent to the starter to clear the alarm status in the starter.

#### Loss of Starter Comm

If starter communication is lost for 10 seconds while the circuit is in a state other than Off or there is a start request, then the Starter Fault alarm will be triggered.  Without communication, the fault code cannot be read from the starter so the code 82 will be automatically logged with the alarm.

## Condenser Fan Control

Condenser fan control from the MicroTech II controller is used only for air-cooled condenser operation.  Head pressure control, as part of the condenser, can be used instead.

Remote evaporative condensers require their own self-contained, on-board, head pressure controls.  See page 46.

### Fan Stages

There are up to 6 stages of Fantrol available. See the table below:

Table 26, Fantrol Staging

| Fantrol Stage | Fans On |
| --- | --- |
| 1 | 1 |
| 2 | 1,2 |
| 3 | 1,2,3 |
| 4 | 1,2,3,4 |
| 5 | 1,2,4,5,6 |
| 6 | 1,2,3,4,5,6 |

### Staging Up

The controller looks at high the discharge pressure is and how quickly it is rising by accumulating “points” in a collection bin called the “Stage Up Accumulator”.

There are four Stage Up deadbands that apply to the Fantrol stages. Stages one through three use their respective deadbands.  Stage four to six share the fourth Stage Up dead band.

When the saturated condenser temperature is above the Target + the active deadband, a Stage Up Error is accumulated.

Stage Up Error Step  = Saturated Condenser Refrigerant temperature – (Target + Stage Up dead band).  If the condensing temperature is high (rising quickly) relative to the Target plus the dead band, multiple Stage Up Error Steps will be accumulated.  This will start a fan sooner than if the temperature is rising slowly.

The Stage Up Error Step is added to Stage Up Accumulator once every Stage Up Error Delay seconds. When the Stage Up Error Accumulator is greater than the Stage Up Error Setpoint, another stage is added.

When a stage up occurs or the saturated condenser temperature falls back within the Stage Up deadband, the Stage Up Accumulator is reset to zero.

### Forced Fan Stage At Start

Fans may be started simultaneously with the compressor based on outdoor ambient temperature.  When the compressor starts, a Fantrol stage is forced based on the following table.  Since this logic applies only to Fantrol fans, the VFD fan is not affected.

Table 27, Forced Fan Staging

| OAT | Fantrol Stage At Start |
| --- | --- |
| > 75 oF | Forced Fantrol 1 SP |
| > 90 oF | Forced Fantrol 2 SP |
| > 105 oF | Forced Fantrol 3 SP |

### Staging Down

There are four Stage Down dead bands.   Stages one through three use their respective deadbands.  Stages four to eight share the fourth Stage Down deadband.

The Stage Down process is similar to the Stage Up except in reverse.

When the saturated condenser refrigerant temperature is below the Target – the active deadband, a Stage Down error is accumulated.

Stage Down Error Step  = (Target - Stage Down dead band) - Saturated Condenser Refrigerant temperature.

The Stage Down Error Step is added to Stage Down Accumulator once every Stage Down Error Delay seconds. When the Stage Down Error Accumulator is greater than the Stage Down Error Setpoint, another stage of condenser fans turned off.

When a stage down occurs or the saturated temperature rises back within the Stage Down deadband, the Stage Down Error Accumulator is reset to zero.  The accumulator is also held at zero after startup until either the outside ambient temperature is less than or equal to 75(F, or the saturated condenser temperature is greater than the condenser target less the active stage down deadband.

## Condenser Fan VFD

Fan VFD operation is available for use with remote condenser units.

For units configured with remote condensers, there is an option to enable fan VFD operation.

- Fan VFD speed and target are displayed.

- Fan VFD minimum speed and maximum speed set points are available.

- An input for fan VFD fault was added at digital input 4 on each circuit controller.  VFD faults are logged in the event log, and notification sent on BAS interface.

- Fan VFD speed is sent on BAS interface.

## Digital Output Control

Each digital output is controlled according to the following rules.  All outputs are initialized to OFF at power on.

### Alarm – (Terminals J12 – NO1)

This output is turned ON when any Equipment Protection ALARM occurs.  It is turned OFF when all alarms have been cleared.

### Evaporator Pump – (Terminals J12 – NO2)

An Evaporator Water Pump output is ON if the Evap State is set to START or RUN.

### Fan #1 to #8 (Air-Cooled Condensers)

[Water Cooled = N] - Condenser Fans Staging is based on condenser pressure as selected by Fan Stage On & Off setpoints.  Fans 1, 3, 5 and 7 are for circuit 1, and fans 2, 4, 6, and 8 are for circuit 2. Fans 1 and 2 start with the first compressor on the respective circuit when the ambient temperature is greater than 75(F.  Below 75(F, these fans start when the condenser pressure gets up to the stage on setpoint.

## Using the Controller

### 4x20 Display & Keypad

#### Layout

The 4-line by 20-character/line, liquid crystal display and 6-key keypad for both of the circuit controller and the unit controller is shown below.

Figure 10, Display (in MENU mode) and Keypad Layout

Note that each ARROW key has a pathway to a line in the display.  Pressing an ARROW key will activate the associated line when in the MENU mode.  There is no display line associated with the Down Arrow.

### Arrow Keys

The four arrow keys (UP, DOWN, LEFT, RIGHT) have three modes of use.

- Scroll between data screens as indicated by the arrows (default mode).

- Select a specific data screen in a hierarchical fashion using dynamic labels on the right side of the display (this mode is entered by pressing the MENU key).

- Change field values in edit mode according to the following table:

LEFT	  Default (D)

RIGHT	  Cancel (C)

UP	  Increment (+)

DOWN	  Decrement (-)

These four edit functions are indicated by one-character abbreviations on the right side of the display (this mode is entered by pressing the ENTER key).

### Getting Started, Navigating - Press the MENU key to get started.  The navigating procedures are the same for both the unit controller and the circuit controller.

#### MENU Key

The MENU key is used to switch between the MENU mode as shown in Figure 10 and the SCROLL mode as shown in Figure 11.  The MENU mode is basically a shortcut to specific groups of menus used for checking ALARMS, for VIEWING information, or to SET setpoint values.  The SCROLL mode allows the user to move about the matrix (from one menu to another, one at a time) by using the four ARROW keys.

When in the MENU mode (as shown in Figure 10), pressing the LEFT ARROW key will select the ALARM menus, the RIGHT ARROW key will select the VIEW menus and the UP key the SET menus.  The controller will go the next lower menu in the hierarchy, and then other menus can be accessed by using the ARROW keys.  Pressing the MENU key from any menu screen will automatically return to the MENU mode as shown in Figure 10.

Another way to navigate through the menus is to press the MENU key when in the MENU mode (as above).  This will switch the controller to the SCROLL mode.  The controller will automatically go to the first screen as shown below (the upper-left menu on the menu matrix shown on pages 66 and 82.  From there, the four ARROW keys can be used to scroll up, down, or across to any other menu.

Figure 11, Display in the Shortcut (SCROLL) Mode and Keypad Layout

#### ENTER Key

Pressing the ENTER key changes the function of the ARROW keys to the editing function as shown below:

LEFT key	Default, changes a value to the factory-set default value.

RIGHT key	Cancel, cancels any change made to a value and returns to the original setting.

UP key	Increment, increases the value of the setting

DOWN key	Decrement decreases the value of a setting.

These four edit functions are indicated by one-character abbreviation on the right side of the display (this mode is entered by pressing the ENTER key).

#### Changing Setpoints

Most menus containing setpoint values have several different setpoints shown on one menu.  When in a setpoint menu, the ENTER key is used to proceed from the top line to the second line and on downward.  The cursor will blink at the entry point for making a change.  The ARROW keys (now in the edit mode) are used to change the setpoint as described above.  When the change has been made, press the ENTER key to enter it.  Nothing is changed until the ENTER key is pressed.

For example, to change the chilled water setpoint:

- Press MENU key to go to the MENU mode.

- Press SET (the UP Key) to go to the setpoint menus.

- Press UNIT SPs (the Right key) to go to setpoints associated with unit operation.

- Press the DOWN key to scroll down through the setpoint menus to the third menu which contains Evap LWT=XX.XF.

- Press the ENTER key to move the cursor down from the top line to the second line in order to make the change.

- Use the ARROW keys (now in the edit mode as shown above) to change the setting.

- When the desired value is achieved, press ENTER to enter it and also move the cursor down.

At this point, the following actions can be taken:

- Change another setpoint in this menu by scrolling to it with the ENTER key.

- Using the ENTER key, scroll to the first line in the menu.  From there, the ARROW keys can be used to scroll to different menus.

## Security

All setpoints on the unit controller, as well as the circuit controllers, are protected using passwords.  Two four-digit passwords provide OPERATOR and MANAGER levels of access to changeable parameters.

## Entering Passwords

Passwords can be entered using the ENTER PASSWORD screen on the unit controller, which is the last screen in the Unit SPs column.  The password is entered by pressing the ENTER key, scrolling to the correct value with the UP and DOWN arrow keys, and pressing ENTER again.  The longer a key is held down, the faster it will increment.  The entered password is not shown after the enter key is pressed.  The operator password is 100.

Once the correct password has been entered, the ENTER PASSWORD screen indicates which password is active (none, operator, technician, or manager).  If the wrong password is entered, a temporary message will appear so stating.  If no valid password is active, the active password level displays “none”.

Entering an incorrect password while a password is active will render that password inactive. Entering a valid password that is not the same as the active password will result in the active password level being changed to reflect the new password level.

## Editing Setpoints

After a valid password has been entered at the unit controller, setpoints on the circuit controllers and the unit controller can be changed.  If the operator attempts to edit a setpoint for which the necessary password level is not active, no action will be taken.

Once a password has been entered, it remains valid for 60 minutes after the last key-press on the unit controller.

## Clearing Alarms

Alarms are only shown on the unit controller and are cleared at the unit controller.  No password is required.

To clear an alarm, go to the unit controller Alarm Log.  Scroll down to the last alarm listed.  The screen will note “No More Alarms”.  Press and hold ENTER for several seconds until the circuit controllers get a clear signal.  If there are no active alarms, the red Alarm light will be off and alarms status will clear from the unit and circuit controllers.

# Menu Descriptions

## Unit Controller

Various menus are shown in the controller display.  Each menu screen shows specific information.  In some cases menus are used only to view the status of the unit, in some cases they are used for checking and clearing alarms, and in some case they are used to set the setpoint values that can be changed.

The menus are arranged in a matrix of screens across a top horizontal row.  Some of these top-level screens have sub-screens located under them.  The content of each screen and its location in the matrix are shown in Unit Controller Menu Matrix.  Each menu screen’s detailed description begins on page 67.

The ARROW keys on the controller are used to navigate through the menus.  The keys are also used to change numerical setpoint values contained in certain menus.

As an alternate to selecting screens with the menu function, it is possible to scroll through all of them with the 4 arrow keys.  For this use, the screens are arranged logically in a matrix as shown below.

### Shortcut Menus

These menus are accessed by pressing the Menu button at any time.  The hierarchical structure of the shortcut menus is shown below.

Table 28, Unit Controller Shortcut Menus

| LEVEL 1 | LEVEL 2 | LEVEL 3 |  |
| --- | --- | --- | --- |
| VIEW | UNIT | STATUS | VIEW UNIT STATUS (1-4) |
|  |  | TEMP | VIEW UNIT TEMP (1-3) |
|  | CIR STATUS | CIR 1 | VIEW CIR 1 STATUS (1-5) |
|  |  | CIR 2 | VIEW CIR 2 STATUS (1-5) |
|  | REFRIGERANT | CIR 1 | VIEW REFR CIR 1 (1-5) |
|  |  | CIR 2 | VIEW REFR CIR 2 (1-5) |
|  | FANS | VIEW FANS |  |
|  | TOWER | VIEW TOWER (1-2)/ |  |
| ALARM | LOG | EVENT/ALARM LOG |  |
|  | ACTIVE | ALARM ACTIVE |  |
| SET | UNIT SPs | SET UNIT SPs (1-15) |  |
|  | COMPRESSOR SPs | SET COMP SPs (1-4) |  |
|  | ALARM LIMITS | SET ALARM LIMITS (1-4) |  |
|  | TOWER SPs | SET TOWER SPs (1-8) |  |

### Unit Controller Menu Matrix

When scrolling through the screens, the following matrix is used:

| “VIEW” SCREENS |  |
| --- | --- |
| VIEW UNIT STATUS (1) | VIEW UNIT TEMP (1) | VIEW CIR 1 (1) | VIEW CIR 2 (1) | VIEW REFRG CIR 1 (1) | VIEW REFRG CIR 2 (1) | VIEW FANS | VIEW TOWER (1) | EVENT LOG (1) | CONTINUED BELOW |
| VIEW UNIT STATUS (2) | VIEW UNIT TEMP (2) | VIEW CIR 1 (2) | VIEW CIR 2 (2) | VIEW REFRG CIR 1 (2) | VIEW REFRG CIR 2 (2) |  | VIEW TOWER (2) | . . . . |  |
| VIEW UNIT STATUS (3) | VIEW UNIT TEMP (3) | VIEW CIR 1 (3) | VIEW CIR 2 (3) | VIEW REFRG CIR 1 (3) | VIEW REFRG CIR 2 (3) |  |  | . . . . |  |
| VIEW UNIT STATUS (4) |  | VIEW CIR 1 (4) | VIEW CIR 2 (4) | VIEW REFRG CIR 1 (4) | VIEW REFRG CIR 2 (4) |  |  | EVENT LOG (25) |  |
|  |  | VIEW CIR 1 (5) | VIEW CIR 2 (5) | VIEW REFRG CIR 1 (5) | VIEW REFRG CIR 2 (5) |  |  |  |  |

|  | “ALARM” SCREENS | “SET SCREENS” | TEST |
| --- | --- | --- | --- |
| CONTINUATION FROM ABOVE | ALARM LOG (1) | ALARM ACTIVE (1) | SET UNIT SPs (1) | SET COMP SPs (1) | SET ALARM LMTS (1) | SET TOWER SPs (1) | TEST UNIT |
|  | . . . . | . . . . | . . . . | SET COMP SPs (2) | SET ALARM LMTS (2) | . . . . |  |
|  | . . . . | . . . . | . . . . | SET COMP SPs (3) | SET ALARM LMTS (3) | . . . . |  |
|  | ALARM LOG (25) | ALARM ACTIVE (n) | SET UNIT SPs (15) | SET COMP SPs (4) | SET ALARM LMTS (4) | SET TOWER SPs (8) |  |

Selection can be made within the matrix by using the LEFT/RIGHT keys to move between columns and the UP/DOWN keys to move between rows.

### Unit Controller Menu Descriptions

This section contains information on each screen of the unit controller.  The menu screens are in order of the matrix above, going from left to right and also down when there are sub-menus.  Many menus are self-explanatory.  A Setpoint menu allows selection of whether the unit has a water-cooled condenser, Water-Cooled = Y (Yes) or a remote condenser, Water-Cooled = N (No).  This selection will alter some menus as appropriate to the type of condenser.

### Screen Definitions – MENU

Top level menu:

< ALARM

< VIEW

< SET

<

ALARM menu:

ALARM < ACTIVE

< LOG

<

<

VIEW menu:

Water-cooled			  Air-cooled

| VIEW < UNIT | VIEW < UNIT |
| --- | --- |
| < CIR STATUS | < CIR STATUS |
| <REFRIGERANT | <REFRIGERANT |
| < TOWER | < FANS |

VIEW UNIT menu:

VIEW < STATUS

UNIT < TEMP

<

<

VIEW CIRCUIT STATUS menu:

VIEW CIR < CIR 1

STATUS < CIR 2

<

<

VIEW REFRIGERANT menu:

VIEW REFR < CIR 1

< CIR 2

<

<

SET menu:

Water-cooled			   Air-cooled

| SET < ALARM LIMITS | SET < ALARM LIMITS |
| --- | --- |
| < UNIT SPs | < UNIT SPs |
| < COMPRESSOR SPs | < COMPRESSOR SPs |
| < TOWER SPs |  |

### Screen Definitions – VIEW

#### View Unit Status

Water-cooled:			   Air-cooled:

| VIEW UNIT STATUS (1) | VIEW UNIT STATUS (1) |
| --- | --- |
| {Unit Status} | {Unit Status} |
| Evap Pump= {state} | Evap Pump= {state} |
| Cond Pump= {state} |  |

Unit Status will display one of the following:

Auto				Off:Ice Mode Timer		Off:All Cir Disabled

Off:Unit Alarm			Off:Keypad Disable		Off:Remote Switch

Off:BAS Disable		Off:Unit Switch			Off:Test Mode

Auto:Wait for load		Auto:Cond Recirc		Auto:Evap Recirc

Auto:Wait Cond Flow		Auto:Wait Evap Flow		Auto:Pumpdown

Pump states include Off, Start, and Run.  The condenser pump state is visible only for water-cooled operation.

VIEW UNIT STATUS (2)

Softload Limit=XXX.X

Demand Limit= XXX.X

Network Limit= XXX.X

VIEW UNIT STATUS (3)

Unit Capacity=XXX.X%

Ice Delay= XXh XXm

Ice Delay will be visible only when unit mode is ice.  It prevents the unit from undesirable starts before the next day’s ice-making cycle.

VIEW UNIT STATUS (4)

1 2 3 4 5 6 8

D.O. X X X X X X X

D.I. X X X X X

The digital input and output status will show either a “0” or a “1” designating Off and On states respectively.

#### View Unit Temperature

VIEW UNIT TEMP (1)

Evap LWT= XXX.X oF

Evap EWT= XXX.X oF

Active SP= XXX.X oF

VIEW UNIT TEMP (2)

LWT Pulldn= 0.0 oF/m

Evap Delta T= XX.X

Water-cooled:			   Air-cooled:

| VIEW UNIT TEMP (3) | VIEW UNIT TEMP (3) |
| --- | --- |
| Cond EWT= XXX.X oF | OAT= XXX.X oF |
| Cond LWT= XXX.X oF |  |

#### View Circuit Status

In the following VIEW CIR screens, the N field indicates which circuit (#1, #2) is being viewed.  Certain screens located in the circuit controller are also displayed here on the unit controller for convenience.

VIEW CIR N STATUS(1)

{Circuit Status}

Slide Pos= 000.0%

Slide Target=000.0%

Circuit Status will display one of the following:

Off:Ready			Off:Cycle Timer		Off:Low OAT Lock

Off:Keypad Disable		Off:Pumpdown Switch		Off:Alarm

Off:Test Mode			EXV Preopen			Run:Pumpdown

Run:Normal			Run:LWT PullDn Limit		Run:Unit Cap Limit

Run:High LWT Limit		Run:Evap Press Low		Run:Lift Press High

Off:pLAN failure

VIEW CIR N STATUS(2)

Hours = XXXXX

Starts = XXXXX

VIEW CIR STATUS (3)

Current (amps)

L1 L2 L3 Avg

XXX XXX XXX XXX

VIEW CIR STATUS (4)

Voltage

L1-2 L2-3 L3-1 Avg

XXX XXX XXX XXX

VIEW CIR STATUS (5)

PF= 0.XX %RLA=XXX.X

KW= XXX

KVA= XXX

#### View Refrigerant

In the following VIEW REFR screens, the N field indicates which circuit (#1, #2) is being viewed.

VIEW REFR CIR N (1)

Evap Press=XXX.X psi

Cond Press=XXX.X psi

VIEW REFRG CIR N (2)

Sat Evap= XXX.X(F

Sat Cond= XXX.X(F

VIEW REFRG CIR N (3)

Suct Temp = XXX.X (F

Disc Temp = XXX.X (F

VIEW REFRG CIR N (4)

Suct SH= XXX.X (F

Disc SH= XXX.X (F

VIEW REFRG CIR N (5)

Evap Approach=XX.X(F

Cond Approach=XX.X(F

EXV position = XXXX

#### View Fans

This screen is only viewable when unit is configured for air-cooled.

VIEW FANS

Fans On, Cir 1= X

Fans On, Cir 2= X

#### View Tower

These screens is only viewable when unit is configured for water-cooled.

VIEW TOWER (1)

Fans On= X of X

Cond EWT= XXX.X (F

Set Point=XXX (F

VIEW TOWER (2)

Bypass Valve=XXX.X%

VFD Speed= XXX.X%

### Screen Definitions – ALARM

ALARM LOG: XX

{Alarm Description}

hh:mm mm/dd/yy

{Parameters}

The most recent 25 alarms, either shutdown or limit, are shown in this menu and subsequent menus located under it.  The last alarm is shown first.  ARROW DOWN from this menu will go to the next-to-last alarm, ARROW DOWN again will go to the second from last, and so on through the last 25 occurrences.  The screens are numbered (1), (2), (3), etc.

Alarm Description will indicate which alarm occurred.  If the alarm is a circuit alarm, then the circuit for which the alarm occurred will also be indicated.

Parameters at the time of the alarm are shown on the bottom line of the screen one at a time.  These are scrolled through by pressing the edit key and using the up and down arrows to scroll through the list.  Parameters include:

Unit State			Evap LWT			Evap EWT

Cond EWT/OAT		Circuit State			Evaporator Pressure

Condenser Pressure		Suction Temperature		Discharge Temperature

Discharge Superheat		EXV Position			EXV State

Slide Position			Fans On

Starter Fault Code (will show “00” when the alarm logged is not a starter fault)

EVENT LOG: XX

{Event Description}

hh:mm mm/dd/yy

*** ALARM ***

hh:mm mm/dd

{Alarm Description}

NO MORE ALARMS

Press ENTER to clear

If the unit is off on a shutdown alarm or running, but in a limit alarm condition, the cause and date will appear in the above screen.  If there is a simultaneous occurrence of more than one alarm, the others will appear in additional screens below the first one, accessed by the DOWN ARROW.  Either type alarm will light a red light in back of the LEFT-ARROW KEY.  The light will go out when the fault is cleared.  To clear the fault, scroll down to the last screen and press ENTER.  If other faults have appeared, they will all be cleared at the same time.

### Screen Definitions – SET

#### Unit Set Points

SET UNIT SPs (1)

Enable=On

Mode= COOL

Source = KEYPAD

Unit Enable settings can be OFF and ON as determined from the Unit Enable setpoint.

Unit Enable is an external signal or a keypad setting that keeps the unit off when the setting is OFF and allows it to run if there is a call for cooling when the setting is ON.  The source for the signal is selected in the 4th line and can be:

- KEYPAD, in which case the selection is made in line 2 and would be normally selected as ON.  This is the normal setting when no external signals are controlling the unit.

- SWITCHES, in which an external switch is wired across terminals #60 and #66. (See wiring diagram page 8 or 9.)

- NETWORK, used with BAS signal, which is wired to the three communication ports.

Unit Mode settings can be

- COOL, normal setting used with chilled water air-condition applications.

- COOL w/GLYCOL, used with low temperature, glycol applications.  It allows a lower LWT setpoint to be used.

- ICE w/GLYCOL, used with ice storage systems, allows changing from chilled glycol operation to lower temperature ICE operation.  In ICE, the unit runs at full load until the ICE setpoint is reached, at which time the unit shuts off.  A three-position switch wired to terminals #60 and #68 initiates the change from glycol cooling to making ice.  (See wiring diagrams on page 8 or 9.)

Unit Mode settings can be COOL COOLw/Glycol, or ICEw/Glycol, as determined from the Unit Mode setpoint.

Source settings can be KEYPAD, SWITCHES, or NETWORK as determined from the Mode Source setpoint.

SET UNIT SPs (2)

Available Modes

= COOL

Select w/Unit Off

SET UNIT SPs (3)

Cool LWT = XX.X(F

Ice LWT = XX.X(F

StartDelta=XX.X(F

SET UNIT SPs (4)

StopDelta= X.X(F

Stg Up Delta= X.X(F

Stg Down Delta=X.X(F

SET UNIT SPs (5)

Max Pulldn=X.X(F/min

EvapRecTimer=XXX sec

Evap Pump= #1 Only

Water-cooled:			   Air-cooled:

| SET UNIT SPs (6) | SET UNIT SPs (6) |
| --- | --- |
| Watercooled= Yes | Watercooled= No |
| CondRecTimer=XXX sec |  |
| Cond Pump= #1 Only |  |

SET UNIT SPs (7)

Reset Type= none

Max Reset = XX.X(F

StrtResetDT= XX.X(F

SET UNIT SPs (8)

Soft Load= Off

Begin Capacity= XXX%

SoftLoadRamp= XXmin

Water-cooled:		   Air-cooled:

| SET UNIT SPs (9) | SET UNIT SPs (9) |
| --- | --- |
| Demand limit= Off | Demand limit= Off |
|  | LowOAT Operation=No |
|  | Low Amb Lock= XX.X(F |

SET UNIT SPs (10)

Ice Time Delay=XXhrs

Clear Ice Timer=No

SET UNIT SPs (11)

Sensor Offset

Evap LWT= XX.X(F

Evap EWT= XX.X(F

Water-cooled:		  Air-cooled:

| SET UNIT SPs (12) | SET UNIT SPs (12) |
| --- | --- |
| Sensor Offset | Sensor Offset |
| Cond EWT= XX.X(F | OAT= XX.X(F |
| Cond LWT= XX.X(F |  |

SET UNIT SPs (13)

CLOCK

mm/dd/yyyy

hh:mm day

SET UNIT SPs (14)

Units = (F/psi

Lang = ENGLISH

After entering a valid manager password, selecting (F/psi will provide IP units; selecting (C/kPa will provide SI units.

SET UNIT SPs (15)

Protocol=

Ident Number=

Baud Rate=

SET UNIT SPs (16)

Enter Password:0000

Active Password

Level:none

#### Compressor Set Points

SET COMP SPs (1)

Seq # Comp 1= X

Seq # Comp 2= X

SET COMP SPs (2)

Max Comps On = x

Start-Start =XX min

Stop-Start =XX min

This menu sets the anti-recycle timers.  Stop-Start is the time required before starting a compressor after it has stopped.  Start-Start is the time required before starting a compressor after the last time it has started.  It is recommended that the default values of 5 minutes and 15 minutes not be changed.  Max Comps On can be 1 or 2 with 2 being the default.

SET COMP SPs (3)

Pumpdown

Pressure= XX.X psi

Time Limit= XXX sec

SET COMP SPs (4)

Light Load Stage

Down Point=XX% slide

Stg Up Delay= XX min

SET COMP SPs (5)

Discharge Temp

Sensor Type=PT1000

#### Alarm Set Points

SET ALARM LIMITS (1)

Low Evap Pressure

Hold=XX.Xpsi

Unload=XX.Xpsi

The LowEvPrHold (Low Evaporator Pressure Hold) and LowEvPrUnld (Low Evaporator Pressure Unload) have the same default value of 59 psi.  If two compressors are running, the LowEvPrUnld is in effect and the lag compressor will be shut off to unload the unit.  If one compressor is running, the LowEvPrHold is in effect and the lag compressor is prevented from starting, thereby holding the unit capacity.

The last action to take place is the shutoff of all compressors running when the LowEvPrStop setting is reached (default is 58 psi).  Reducing these time intervals will increase detrimental compressor cycling.  It is recommended that these settings not be changed.

SET ALARM LIMITS (2)

LowOilDelay= XXX sec

HighOilDpDel=XXX sec

Water-cooled:		   Air-cooled

| SET ALARM LIMITS (3) | SET ALARM LIMITS (3 |
| --- | --- |
| High Disc Temp=XXX(F | High Disc Temp=XXX(F |
| HighLift Delay=XXsec | HighLift Delay=XXsec |
|  | LowOATStartTmr=XXsec |

:

SET ALARM LIMITS (4)

Evap Freeze= XX.X(F

Evap Flow Proof=XXXs

Recirc Timeout=xxmin

Evap Freeze (the unit freeze protection shutdown) is actually a stop alarm and shuts off the unit when the LWT reaches 36F.  It is cleared by going to the CLEAR ALARM menu in the ACTIVE ALARM hierarchy.

Evap/Cond FlowProof is the flow switch interlock.  Closing the flow switch, and therefore proving the existence of chilled water flow, resets this trip.  It is recommended that these settings not be changed.

SET ALARM LIMITS (5)

Cond Freeze= XX.X(F

Cond Flow Proof=XXXs

Set Alarm Limits (5) is accessible only if unit is configured as water-cooled.

#### Tower Setpoints

Tower set points are only available when the unit is configured as water-cooled.

The MicroTech II controller is capable of controlling cooling tower water temperature on chillers using water-cooled condensers.  Output wiring connection points are shown on the field wiring diagrams beginning on page 8.

[Water Cooled = Y] - Condenser Pump on with first Compressor on. Tower fan control is active when the Tower Control setpoint is set to Temperature and the condenser pump is in the RUN state.  Staging is based on Entering Condenser Water Temperature (ECWT).  Operation depends on the following parameters.

- Condenser pump state

- ECWT OR Lift pressure

- Stage up and stage down timer values

- Tower setpoints (Tower Control, Tower Stages, Stage Up Time, Stage Down Time, Stage Differential, Stage #1 ON, Stage #2 ON, Stage Down @, Stage Up @)

When the condenser pump starts, the stage up timer shall start.  The first stage shall turn ON when the following conditions are met:

- The stage up timer completes

- The ECWT is > Stage #1 ON setpoint

- Bypass valve position is > the Stage Up @ setpoint (only if Valve/VFD Control setpoint = Valve Stage)

Additional stages can turn on (up to the number specified by the Tower Stages setpoint) when above conditions are met for the next stage plus the following condition:

- VFD Speed is > the Stage Up @ setpoint (only if Valve/VFD Control setpoint = VFD Stage OR Valve SP/VFD Stage)

Down staging shall occur when the following conditions are met:

- The stage down timer completes

- The ECWT is < Stage #X ON (Temp) setpoint – Stage Differential (Temp) setpoint point

- Bypass valve position is < the Stage Down @ setpoint (only if Valve/VFD Control setpoint = Valve Stage)

- VFD Speed is < the Stage Down @ setpoint (only if Valve/VFD Control setpoint = VFD Stage OR Valve SP/VFD Stage)

Each stage-up or stage-down event shall restart both the stage-up and stage-down timers.  Only one fan output shall be switched at a time (except that all outputs switch OFF when the condenser pump state equals OFF).

SET TOWER SPs (1)

Tower Control=None

Tower Stages= 2

When Tower Control is None, the control of condenser water temperature is not by the MicroTech II controller and assumed to be furnished elsewhere.

Tower Stages is the number of tower fans to be staged by the controller, choices are 0, 1, or 2.  "0" indicates control will be by a bypass valve or variable speed pump controlled by the MicroTech II controller.

StageUP/DN imposes a time delay between fan stages when turning on or turning off.

SET TOWER SPs (2)

Stage 1 On =XXX

Stage 2 On =XXX

StageDiff = XX.X

SET TOWER SPs (3)

Stage Up Tmr= XX min

Stage Dn Tmr= XX min

Stage Up/Dn=XXX/XXX%

StageDiff is the number of degrees below the Stage ON that will turn off the tower fans.  For example, if Stage ON #1 is 70F and StageDiff is 5F, tower fan #1 will stage off when the ECWT drops to 65F and stage the fan on when the ECWT rises to 70F.  The same is true for fan #2.

Stage Up timer is the number of minutes that must elapse between the condenser pump starting (it starts with the unit) and fan #1 starting or the time between fan #1 starting and fan #2 starting.

StageDown is the elapsed time between staging down the fan motors.

SET TOWER SPs (4)

Valve/VFD Control=

None

Valve Type=NC to twr

Valve/VFD Control settings are None, Valve Setpoint, Valve Stage, VFD Stage, or ValveSP/VFDStage.  Default is None which results in no control of the tower from the MicroTech II controller.

- Valve Setpoint, the valve will control (bypass tower) to hold the minimum temperature as established by the Set Tower SPs in screen number 5 shown on the following page.

This mode is operational when the Valve/VFD Control setpoint is set to Valve Setpoint OR Valve SP/VFD Stage.  In this mode the valve output is varied with a proportional-derivative (PD) algorithm (with deadband) in order to maintain the controlled parameter (CP) at the desired value.  The output is always limited between the Valve Control Range (Min) setpoint and the Valve Control Range (Max) setpoint.  A valve increment shall be computed once every 5 seconds according to the following equation. (Error Gain and Slope Gain are set in menu screen #8.)

Increment = [(Error) * (Error Gain setpoint)] + [(Slope) * (Slope Gain setpoint)]
	Where:	Error = ECWT – Valve Setpoint
		Slope = (Present CP) – (Previous CP)

When the Error is > the Valve Deadband setpoint, the valve position analog output (% of full scale) is updated according to the following equation.

New %Position = Old %Position + Increment/10

- Valve Stage, controls from the fan stage setpoint in use.  It is recommended that the Valve Setpoint method explained above be used rather than this mode.

This mode is only operational when the Valve/VFD Control setpoint is set to Valve Stage.  In this mode the valve output is controlled as for Valve Setpoint mode (above), except that the active setpoint for the controlled parameter is selected according to the following table.

| # Of Fans ON | Active Setpoint |
| --- | --- |
| 0 | Valve Setpoint |
| 1 | Stage #1 ON |
| 2 | Stage #2 ON |
| 3 | Stage #3 ON |
| 4 | Stage #4 ON |

- VFD Stage, ValveSP/VFDStage, When the Valve/VFD Control setpoint is set to None, Valve Setpoint, OR Valve Stage, this output is set to 0.  Otherwise, it will be controlled in a manner identical to Valve Stage Mode (above) except that (1) it shall be kept at zero until the first fan stage is ON, and (2) the following setpoints do not apply.

Valve Control Range (Min)

Valve Control Range (Max)

Valve Type

Valve Type settings are NC (normally closed to tower) or NO (normally open).
These settings establish the operation of a tower bypass valve (must be a 3-way valve).

#### Initial Valve Position

When the condenser pump is not in the RUN state, the valve output shall be set as a function of entering condenser water temperature (ECWT) per the following graph.

Figure 12, Initial Valve Position

#### Operation After Start

When the condenser pump is in the RUN state, the valve output shall be controlled in one of two modes as specified by the Valve/VFD Control setpoint.  The controlled parameter shall be the condenser entering water temperature.  When the desired output signal varies from 0 to 100%, the output voltage shall vary as shown below.

0 to 10 VDC (Valve Type = NC)

10 to 0 VDC (Valve Type = NO)

SET TOWER SPs (5)

Valve SP=XXX

Valve DB=XX.X

Valve SP is the minimum tower water temperature acceptable, default is 65F.

Valve DB is the dead-band in degrees, default is 2.0F.

SET TOWER SPs (6)

Valve Start Position

Min= XXX% @XXX

Max= XXX% @XXX

The ValveStart position is the position of the valve when the unit starts.  Default for minimum start position is 0%, and 100% for maximum position.

SET TOWER SPs (7)

Valve Control Range

Min= XXX%

Max= XXX%

Defaults are 10% minimum and 90% maximum.

SET TOWER SPs (8)

PD Control Loop

Error Gain=XX

Slope Gain=XX

Defaults are 25 for both error and slope.

### Screen Definitions – TEST

TEST UNIT (1)

Alarm Out=Off

Evap Pump 1= Off

Evap Pump 2= Off

TEST UNIT (2)

Cond Pump 1= Off

Cond Pump 1= Off

TEST UNIT (3)

Tower Fan 1= Off

Tower Fan 2= Off

TEST UNIT (4)

Tower Bypass= XXX.X

Tower VFD Spd= XXX.X

## Circuit Controller

The display on the circuit controller displays information about the circuit that it is controlling.  Setpoint availability will be limited to setpoints that are unique to that circuit. Other set points are changed at the Unit Controller.

### Shortcut Menus

Pressing the Menu button at any time accesses these menus.  The hierarchical structure of the shortcut menus is shown below.

| LEVEL 1 | LEVEL 2 | LEVEL 3 (No. of Screens) |
| --- | --- | --- |
| VIEW | UNIT | VIEW UNIT (1-2) |
|  | CIR STATUS | VIEW CIR STATUS (1-9) |
|  | REFRIGERANT | VIEW REFRIGERANT (1-7) |
|  | FANS | VIEW FANS (1-2) |
| SET | COMPRESSOR SPs | SET COMP SPs (1-4) |
|  | EXV SPs | SET EXV SPs (1-2) |
|  | FAN SPs | SET FANS (1-6) |
|  | SENSOR OFFSETS | SET SENSOR OFFSET (1-3) |

### Menu Matrix

When scrolling through the screens, the following matrix is used:

| VIEW UNIT (1) | VIEW CIR STATUS (1) | VIEW REFRG (1) | VIEW FANS (1) | SET COMP SPs (1) | SET EXV SPs (1) | SET FANS (1) | SET SENSOR OFFSETS (1) | TEST CIRCUIT (1) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| VIEW UNIT (2) | VIEW CIR STATUS (2) | VIEW REFRG (2) | VIEW FANS (2) | SET COMP SPs (2) | SET EXV SPs (2) | SET FANS (2) | SET SENSOR OFFSETS (2) | TEST CIRCUIT (2) |
|  | VIEW CIR STATUS (3) | VIEW REFRG (3) |  | SET COMP SPs (3) |  | SET FANS (3) | SET SENSOR OFFSETS (3) | TEST CIRCUIT (3) |
|  | - - - - | - - - - |  | SET COMP SPs (4) |  | - - - - |  | TEST CIRCUIT (4) |
|  | VIEW CIR STATUS (9) | VIEW REFRG (7) |  | SET STARTER SPs (3-8) |  | SET FANS (5) |  |  |

### Screen Definitions – MENU

Top level menu:

< VIEW

< SET

<

<

View menu:

VIEW < UNIT

< CIR STATUS

<REFRIGERANT

< FANS

Fan data is available only when unit is configured as air-cooled.

Set menu:

SET <COMPRESSOR SPs

< EXV SPs

< FAN SPs

<SENSOR OFFSETS

Fan setpoints are available only when unit is configured as air-cooled.

### Screen Definitions – VIEW

#### View Unit Status

Water cooled:			   Air cooled:

| VIEW UNIT (1) | VIEW UNIT (1) |
| --- | --- |
| {Unit status} | {Unit status} |
| Evap pump = {State} | Evap pump = {State} |
| Cond pump = {State} |  |

Unit Status will display one of the following:

Auto				Off:Ice Mode Timer		Off:All Cir Disabled

Off:Unit Alarm			Off:Keypad Disable		Off:Remote Switch

Off:BAS Disable		Off:Unit Switch			Off:Test Mode

Auto:Wait for load		Auto:Cond Recirc		Auto:Evap Recirc

Auto:Wait Cond Flow		Auto:Wait Evap Flow		Auto:Pumpdown

Pump states include Off, Start, and Run.  The condenser pump state is visible only for water-cooled operation.

VIEW UNIT (2)

Evap LWT= XXX.X(F

Active SP= XX.X(F

LWT pulldn= XX.X(F/m

#### View Circuit Status

VIEW CIR STATUS (1)

{Circuit Status}

Slide Pos= XXX.X%

Slide Target= XXX.X%

Circuit Status will display one of the following:

Off:Ready			Off:Cycle Timer		Off:Low OAT Lock

Off:Keypad Disable		Off:Pumpdown Switch		Off:Alarm

Off:Test Mode			EXV Preopen			Run:Pumpdown

Run:Normal			Run:LWT PullDn Limit		Run:Unit Cap Limit

Run:High LWT Limit		Run:Evap Press Low		Run:Lift Press High

Off:pLAN failure 		Off:Stage Up Delay

VIEW CIR STATUS (2)

Hours = XXXXX

Starts = XXXXX

KW Hours= XXXXXXX

A KW hours counter has been added to the Circuit control Circuit Status Screen. The KW Hours field will display up to 9,999,999 kW-Hours.

VIEW CIR STATUS (3)

Current (amps)

L1 L2 L3 Avg

XXX XXX XXX XXX

VIEW CIR STATUS (4)

Voltage

L1-2 L2-3 L3-1 Avg

XXX XXX XXX XXX

VIEW CIR STATUS (5)

PF= 0.XX %RLA=XXX.X

KW= XXX

KVA= XXX

VIEW CIR STATUS (6)

Digital Outputs

1 2 3 4 5 6 7 8 9 10

X X X X X X X X X X

Status will be “0” for OFF and “!” for ON.

VIEW CIR STATUS (7)

Digital Outputs

11 12 13

X X X

VIEW CIR STATUS (8)

Analog Outputs

(volts X 100)

1=XXXX 3=XXXX

VIEW CIR STATUS (9)

Digital Inputs

1 3 4 5 6 9

X X X X X X

#### View Refrigerant

VIEW REFRIGERANT (1)

Evap Press=XXX.X psi

Cond Press=XXX.X psi

VIEW REFRIGERANT (2)

Sat Evap = XXX.X (F

Sat Cond = XXX.X (F

VIEW REFRIGERANT (3)

Suct Temp = XXX.X (F

Disc Temp = XXX.X (F

VIEW REFRIGERANT (4)

Suct SH= XXX.X (F

Disc SH= XXX.X (F

VIEW REFRIGERANT (5)

Evap Approach=XX.X(F

Cond Approach=XX.X(F

VIEW REFRIGERANT (6)

MaxCondSatT= XXX.X(F

EXV Ctrl=Superheat

SH target= XX.X(F

VIEW REFRIGERANT (7)

EXV Steps= XXXX

EXV ctrl range:

XXXX – XXXX steps

#### View Fans

View Fans screens are only available when the unit is configured as air-cooled.

VIEW FANS (1)

Fans Running= X

Stage Up Err= XXX

Stage Dn Err= XXX

VIEW FANS (2)

Target Sat T=XXX.X(F

VFD Speed=XXX.X%

VFD Target=XX.X(F

### Screen Definitions – SET

#### Compressor Set Points

SET COMP SPs (1)

Clear Cycle Tmr= no

Comp Size= XXX

Max Slide= XXX.X %

SET COMP SPs (2)

Circuit Mode=Enable

Slide Target= XXX.X%

Slide Control=auto

SET STARTER SPs (3)

Motor FLA= XXX amps

Motor RLA= XXX amps

The starter set points are stored in permanent memory on the starter and the Circuit control set points will be reset to the values stored on starter when the Circuit control is powered up.

When the Circuit control is powered up the starter set points MUST be adjusted from the Circuit control.

Ground Fault Enable, Ground Fault Trip Level, Rated RMS Voltage and CT Ratio set points are NOT adjustable while the compressor is running.

SET STARTER SPs (4)

Ground Fault=No

GF Trip Level= XXX%

#### EXV Set Points

SET EXV SPs (1)

Manual EXV Pos= XXXX

EXV Control=auto

Service Pumpdown=No

SET EXV SPs (2)

Preopen Timer=XXXsec

#### Sensor Offsets

SET SENSOR OFFSET(1)

Evap Press= XX.X psi

Cond Press= XX.X psi

SET SENSOR OFFSET(2)

Suct Temp= X.X (F

Disch Temp= X.X (F

SET SENSOR OFFSET(3)

Slide min pos= XX%

Slide max pos= XX%

Slide Pos= XXX.X%

#### Fan Set Points

SET FAN SPs (1)

Number of fans = X

Fan VFD = Enable

SET FAN SPs (2)

Stg On Deadband((F)

Stg1=XX.X Stg2=XX.X

Stg3=XX.X Stg4=XX.X

SET FAN SPs (3)

Stg Off Deadband((F)

Stg2=XX.X Stg3=XX.X

Stg4=XX.X Stg5=XX.X

SET FAN SPs (4)

VFD Min Speed= XX%

VFD Min Speed= XXX%

SET FAN SPs (5)

Cond Sat Temp Target

Max= XXX.X (F

Min= XXX.X (F

SET FAN SPs (6)

# Fans On At Startup

>75(F >90(F >105(F

X X X

### Screen Definitions – TEST

TEST CIRCUIT (1)

Slide

Direction = Unload

Pulse = Off

TEST CIRCUIT (2)

Oil Heater= Off

EXV Closed= Off

TEST CIRCUIT (3)

EXV Position=XXXX

TEST CIRCUIT (4)

Condenser Fans:

1=Off 2=Off 3=Off

4=Off 5=Off 6=Off

## Editing Review

Editing is be accomplished by pressing the ENTER key until the desired field is selected.  This field shall be indicated by a blinking cursor under it.  The arrow keys shall then operate as defined below.

CANCEL (Right)	Reset the current field to the value it had when editing began.

DEFAULT (Left)	Set value to original factory setting.

INCREMENT (Up)	Increase the value or select the next item in a list.

DECREMENT (Down)	Decrease the value or select the previous item in a list.

During edit mode, the display shows a two-character wide menu pane on the right as shown below.

SET UNIT SPs (X) <D

(data) <C

(data) <+

(data) <-

Additional fields can be edited by pressing the ENTER key until the desired field is selected.  When the last field is selected, pressing the ENTER key switches the display out of “edit” mode and returns the arrow keys to “scroll” mode.

### Alarms

When an alarm occurs, the alarm type, limit value (if any), date, and time are stored in the active alarm buffer corresponding to that alarm (viewed on the Alarm Active screens) and also in the alarm history buffer (viewed on the Alarm Log screens).  The active alarm buffers hold a record of the last occurrence of each alarm and whether or not it has been cleared.  The alarm can be cleared by pressing the Edit key.  A separate buffer is available for each alarm (High Cond Pressure, Evaporator Freeze Protect, etc.).  The alarm history buffer holds a chronological account of the last 25 alarms of any type.

### Security

Two four-digit passwords provide OPERATOR and MANAGER levels of access to changeable parameters.  Either password can be entered using the ENTER PASSWORD screen which can be accessed either through the SET OTHER menu or by simply pressing the ENTER key while on one of the SET screens.  The password can then be entered by pressing the ENTER key, scrolling to the correct value with the UP and DOWN arrow keys, and pressing ENTER again.  Once the correct password has been entered, the previously selected screen will reappear.  Once a password has been entered, it will remain valid for 15 minutes after the last key-press.

# BAS Interface

The MicroTech II controller is equipped with the Protocol Selectability( feature, an exclusive McQuay feature that provides easy unit interface with a building automation system (BAS).  If the unit will be tied into a BAS, the controller should have been purchased with the correct factory-installed interface module.  The modules can also be added in the field during or after installation.

If an interface module was ordered, one of the following BAS interface installation manuals was shipped with the unit.  Contact your local McQuay sales office for a replacement, if necessary or download from www.mcquay.com.

- IM 735, LONWORKS( Communication Module Installation

- IM 736, BACnet( Communication Module Installation

- IM 743, Modbus( Communication Module Installation

- ED 15062-0, MicroTech II Chiller Protocol Information – BACnet( and LONWORKS(

- ED 15063-0, MicroTech II Chiller Unit Controller Protocol Information – Modbus(

### Unit Controller Setting

Settings are made in the unit controller.  Set Unit Setpoints, Menu 1 is set to Source = Network.  The specific protocol being used is set in Set Unit Setpoints, menu 15.

### Connection to Chiller

Connection to the chiller for all BAS protocols will be at the unit controller.  An interface card will have to be installed in the unit controller depending on the protocol being used.

NOTE:

In this revision (D), the starter electric data in the table below is now available to the Building Automation System at the unit control supervisor port:

Starter Parameter 			Supervisor Type  		Index Number

Compressor Average Amps  		Analog Output  			26

Compressor Kilowatts  			Analog Output  			27

Compressor Average Volts  		Analog Output  			29

# Unit Troubleshooting Chart

WARNING

Troubleshooting can cause severe personal injury or death. Troubleshooting must be performed by trained, experienced technicians only.

| PROBLEM | POSSIBLE CAUSES | POSSIBLE CORRECTIVE STEPS |
| --- | --- | --- |
| Compressor Will Not Run | Main switch, circuit breakers open. Fuse blown. Thermal overloads tripped or fuses blown. Defective contactor or coil. System shut down by equipment protection devices. No cooling required. Liquid line solenoid will not open. Motor electrical trouble. Loose wiring. | Close switch Check electrical circuits and motor winding for shorts or grounds. Investigate for possible overloading. Replace fuse or reset breakers after fault is corrected. Overloads are auto reset. Check unit closely when unit comes back on line. Repair or replace. Determine type and cause of shutdown and correct it before resetting protection switch. None. Wait until unit calls for cooling. Repair or replace coil. Check motor for opens, short circuit, or burnout. Check all wire junctions. Tighten all terminal screws. |
| Compressor Noisy or Vibrating | Flooding of refrigerant into compressor. Improper piping support on suction or liquid line. Worn compressor. | Check superheat setting of expansion valve. Relocate, add or remove hangers. Replace. |
| High Discharge Pressure | Condenser water insufficient or temperature too high. Fouled condenser tubes (water-cooled condenser). Clogged spray nozzles (evaporative condenser). Dirty tube and fin surface (air cooled condenser). Noncondensables in system. System overcharge with refrigerant. Discharge shutoff valve partially closed. Condenser undersized (air-cooled). High ambient conditions. | Readjust temperature control or water regulating valve. Investigate ways to increase water supply. Clean. EPA purge the noncondensables. Remove excess refrigerant. Open valve. Check condenser rating tables against the operation. Check condenser rating tables against the operation. |
| Low Discharge Pressure | Faulty condenser temp. regulation. Insufficient refrigerant in system. Low suction pressure. Condenser too large. Low ambient conditions. | Check condenser control operation. Check for leaks. Repair and add charge. See corrective steps for low suction pressure below. Check condenser rating table against the operation. Check condenser rating tables against the operation. |
| High Suction Pressure | Excessive load. Expansion valve overfeeding. | Reduce load or add additional equipment. Check remote bulb. Regulate superheat. |

Continued on next page.

| PROBLEM | POSSIBLE CAUSES | POSSIBLE CORRECTIVE STEPS |
| --- | --- | --- |
| Low Suction Pressure | Lack of refrigerant. Evaporator dirty. Clogged liquid line filter-drier. Expansion valve malfunctioning. Condensing temperature too low. Compressor will not unload. Insufficient water flow. | Check for leaks. Repair and add charge. Clean chemically. Replace cartridge(s). Check and reset for proper superheat. Replace if necessary. Check means for regulating condensing temperature. See corrective steps for failure of compressor to unload. Adjust flow. |
| Little or No Oil Pressure | Clogged suction oil strainer. Excessive liquid in crankcase. Low oil level. Flooding of refrigerant into crankcase. | Clean. Check sump heater. Reset expansion valve for higher superheat. Check liquid line solenoid valve operation. Add oil. Adjust expansion valve. |
| Compressor Loses Oil | Lack of refrigerant. Velocity in risers too low (A-C only). Oil trapped in line. | Check for leaks and repair. Add refrigerant. Check riser sizes. Check pitch of lines and refrigerant velocities. |
| Motor Overload Relays or Circuit Breakers Open | Low voltage during high load conditions. Defective or grounded wiring in motor or power circuits. Loose power wiring. High condensing temperature. Power line fault causing unbalanced voltage. High ambient temperature around the overload relay | Check supply voltage for excessive line drop. Replace compressor-motor. Check all connections and tighten. See corrective steps for high discharge pressure. Check Supply voltage. Notify power company. Do not start until fault is corrected. Provide ventilation to reduce heat. |
| Compressor Thermal Switch Open | Operating beyond design conditions. Discharge valve partially shut. | Add facilities so that conditions are within allowable limits. Open valve. |
| Freeze Protection Opens | Thermostat set too low. Low water flow. Low suction pressure. | Reset to 42°F (6°C) or above. Adjust flow. See “Low Suction Pressure.” |

All McQuay equipment is sold pursuant to McQuay’s Standard Terms and Conditions of Sale and Limited Product Warranty.

This document contains the most current product information as of this printing.  For the most up-to-date product information on this unit and others, please go to www.mcquay.com.

# Text boxes

Manufactured in an ISO Certified Facility

Design Vintage

W = Water-Cooled Condenser

A = Unit Less Condenser

Nominal Capacity (Tons)

Rotary Screw Compressor

Global

Water-Cooled Condensing

Figure 9, Slide Indicator and Coils Locations

ENTER Key and Green Compressor Run Light

Key-to-Screen Pathway

T13, Circ#1 Controller

ARROW Keys (4)

Circ#1 Controller

T2, Unit Controller

MENU Key

T14, Circ#1 Load Solenoid

Unit Controller

T25, Circ#2 EXV Power

T24, Circ#2 Load Solenoid

T23, Circ#2 Controller

MHPR11 &12, Mechanical High Pressure Relay

T15, Circ#1 EXV Power

(4) Arrow Keys

"Enter" Key and Green Comp. Run Light

Key to Screen Pathway

Menu Key

MENU Key

Circuit Breaker & Switch Panel

Red Alarm Light

Slide Indicator

ENTER Key + Green light for comp. On

Red light for fault indication

Circ#1 & 2 EXV Drivers

External Disconnect Handle

Circ#2 Controller

TB3, Circ#2 Controller Terminal Board

TB2, Circ#1 Controller Terminal Board

TB1 Unit Controller Terminal Board

Circ#1 Solid State Starter

Circ#2 Solid State Starter

SSS1 Bypass Contactor

SSS2 Bypass Contactor

Secondary Fuses

Circ#1 Circuit Breaker

Circ#2 Circuit Breaker

Unit Disconnect Switch

W/ External Handle

External Disconnect Handle

T1, Supply Voltage to 120V Transformer

Primary Fuses

Outside (Microprocessor) Panel

S1  Main Unit On-Off Switch

Open Location

CS1, Circuit#1 On-Off Switch

CS2, Circuit#2 On-Off Switch

CB11 Circ#1 Circuit Breaker

CB12, Circ#1 Sump Heater

Open Location

CB21, Circ#2 Circuit Breaker

CB22, Circ#2 Sump Heater

Open Locations

Location for Optional 115V Receptacle

Left Arrow Key and Red Alarm Light

Conform to the BACnet protocol (ANSI/ASHRAE 135-2001).

Load Coil

Unit controllers are LONMARK certified with an optional LONWORKS communications module.

ARROW Keys (4)

Unload Coil