DEPARTMENT OF TRANSPORTATION

FEDERAL AVIATION ADMINISTRATION

PCT/ATCSCC

3699/3701 MACINTOSH DRIVE

WARRENTON, VIRGINIA 20187

REQUEST FOR OFFER NO:  DTFAEN-12-RFQ-PCTFIRE

ANNUAL TESTING, INSPECTION & SERVICE OF THE FIRE ALARM & DETECTION SYSTEM

Coordinate on-site visit with:

Brian McPhillips

Phone:  540-349-7405

Fax:   540-349-7602

Email:  brian.mcphillips@faa.gov

#### SCOPE OF WORK

PROJECT:  Perform annual testing, inspection and service of various elements of the fire alarm and detection systems at Potomac TRACON and the Air Traffic Control System Command Center, Warrenton, VA.

DESCRIPTION OF WORK:  The contractor shall perform annual tests, inspections and services on various fire alarm and detection systems in accordance with National Fire Protection Association recommendations, local codes, and manufacturer’s recommended procedures. The contractor shall deliver a written report that describes the test and inspection results and services performed.  A list of system components is attached to this document. Only technicians authorized by SimplexGrinnell shall perform work on this system. The contractor shall provide all transportation, shipping, labor, tools, equipment and material to accomplish the following: All fire alarm and detection systems will be inspected and functionally tested in accordance with National Fire Protection Association recommendations, manufacturer’s specifications, and local codes.

1. FIRE ALARM AND DETECTION SYSTEMS:

  - Inspect the system to determine whether it is in service and in satisfactory condition with NFPA standards.

  - Identify potentially detrimental site conditions that could compromise the performance of mechanical and/or electronic components of the system.

  - Inquire about any changes or modifications of the fire detection and alarm system.

  - Inquire about any changes in the general occupancy environment, operations and conditions relating to the fire detection and alarm system in accordance with NFPA standards.

  - Inquire about the customer’s general storage and stock arrangements for combustibles in relation to fire alarm and suppression systems.

  - Check the general condition of the fire alarm panel and related equipment.

  - Test all smoke and heat detectors in accordance with their manufacturer’s specifications.

  - Inspect all fire alarm control panels and remote fire alarm panels.

  - Inspect and test all annunciators and zones both visually and by tripping a detector.

  - Inspect and meter all batteries.

  - Inspect and exercise all flow switches, tamper switches and low pressure alarms.

  - Inspect all output relays and test their activation.

  - Verify that all signals are received by the central monitoring station.

  - Inspect the smoke detectors for cleanliness.  Clean the detectors that require cleaning in accordance with their manufacturer’s guidelines.

  - Test non-storable heat detector circuits by simulating electrical operation at the wiring connection.

  - Function test all accessible heat actuating devices, both electrically and pneumatically in accordance with the manufacturer’s specifications.  When explosive conditions are present, hot water will be used to heat test all accessible heat actuating devices.

  - Inspect and exercise all supervised control valves and switches.

  - During testing of the fire detection system, activate outputs for the purpose of equipment shutdown, start-up and HVAC/smoke control.

  - Tag devices as required and perform all required record keeping.

  - Compile a complete report of the inspection, explaining and deficiencies and recommending corrective action to be taken in accordance with recognized codes for care and maintenance.

  - Familiarize the customer with the proper operation of the equipment.

  - Test to confirm that all alarm, trouble, and supervisory signals are properly being sent to the local fire alarm panel, and if applicable, being sent and received at the supervising central alarm station.

  - Test and verify each fire alarm circuit including signaling, notification appliance, and indicating device circuits for ground faults and open circuits.

  - Test all manual fire alarm pull boxes.

  - Test all audible devices such as horns and bells to ensure that each device is functioning.  Record the sound pressure level during testing.

  - Test all visual devices such as strobes.  Check to ensure that occupancy changes within the facility have not obstructed the ability for occupants to see the visual devices.

  - Test all interlocked devices to the fire alarm system such as door closures, fan shut-off or start-ups, elevator recall, power shutdown, etc., for proper activation following alarm system activation.  Test to ensure that proper sequence of events occur following receipt of an alarm at the local fire alarm control panel.

  - Test the Digital Alarm Communicator Transmitter (DACT) by testing the line seizure while initiating an alarm signal while using the primary line for a telephone call.  Transmission to the central station via the DACT shall be within 90 seconds.  The primary and secondary lines from the DACT shall also be tested for proper supervision by disconnecting each line and ensuring that trouble transmission to the supervising station occurs within 4 minutes.

# Special Provisions

Test and Inspection Overview:

Under this Special Provisions, SimplexGrinnell trained technicians will perform inspections and diagnostic tests for all accessible peripheral devices listed and currently connected to the facility life safety systems.  Test will be scheduled in advance at the convenience of customer’s staff (see list of equipment page for equipment to be tested).

Testing of peripheral devices for fire alarm and detection systems:

Accessible peripheral devices shall be functionally tested in accordance with NFPA 72, chapter 10 and the manufacturer’s recommended procedures.

Detector cleaning for fire alarm and detection system:

To help minimize false alarms, and in accordance with NFPA, accessible smoke detection devices will be cleaned using manufacturer’s recommended procedures at a rate of 100% annually.

Sensitivity testing for fire alarm and detection systems:

To ensure accuracy, and in accordance with NFPA guidelines, sensitivity testing will be performed on smoke detectors at a rate of 100% annually.  Testing will be performed using only UL approved sensitivity testing equipment.  Devices performing outside the listed sensitivity range shall be re-cleaned and tested, and if necessary, noted and recommended for replacement.

Documentation:  All accessible components and devices shall be logged for:

- Exact location of each device tested, including system address or zone location.

- Test results and applicable voltage readings.

- Any discrepancies found shall be provided to customer’s designated personnel and copies shall be archived by company.

Emergency Service Call and Labor:

Unlimited service calls shall be provided 24 hours a day, 7 days a week, for repairs associated with normal equipment failures (Provided during normal working hours, Mon-Fri, 8:00 a.m. to 5:00 p.m., excluding holidays).  This provision includes labor, travel and mileage charges for repairs associated with normal equipment failures.    Emergency service will be provided within 24 hours of notification Monday through Friday 8:00 a.m. to 5:00 p.m.  This provision covers labor to troubleshoot and diagnose system problems, and the labor to replace failed devices.

PARTS AND COMPONENTS REPLACEMENT:

The following shall be replaced when required due to failure; the central processing unit, to include reprogramming of system due to failure, replacement of circuit boards, and all components in the control panels, annunciator panels, transponders, printers, keyboards monitors, and peripheral devices (smoke detectors, pull stations, audible/visible units, door contacts, etc.) associated with system.

Work Periods:

Contractor shall perform all non-emergency work within the hours of 8:00 AM to 5:00 PM Monday through Friday.  The FAA representative shall approve work outside these hours in advance.

.

Warranty:

Upon completion and acceptance of all work the contractor shall provide the manufacture’s standard warranty on all workmanship.

Points of Contact:  Brian McPhillips - 540-349-7405.

# LIST OF EQUIPMENT – SIMPLEX MODEL NUMBERS

| Qty | Model No. | Description |
| --- | --- | --- |
| 1 | 4120-8201 | NETWORK CONTROL PANEL W/AUDIO |
| 1 | 4120-7003 | MASTER CONTROLLER W/LCD DISPLAY |
| 1 | 4120-6081 | VERSION 8 SOFTWARE |
| 1 | 4120-6050 | POWER LIMITED OPTION |
| 1 | 4120-4331 | 6 CIRCUIT CLASS A STYLE Z |
| 1 | 4120-4321 | 6 CIRCUIT CLASS B STYLE Y |
| 2 | 4120-4203 | CKT DUAL CHANNEL STYLE Z |
| 1 | 4120-4201 | 4 CIRCUIT DUAL CHANNEL STYLE Y |
| 4 | 4120-2003 | 6 UNIT W/GLASS DR & RETAINER |
| 6 | 4120-1203 | POWER LIMITED 100WATT AMPLIFIER |
| 5 | 4120-1108 | POWER LIMITED 8A POWER SUPPLY |
| 1 | 4120-0413 | 2 CHANNEL SPEAKER SELECT SWITCH |
| 1 | 4120-0404 | 8/16 3 POS MAINT SW/RED-GREEN L |
| 1 | 4120-0301 | 64/64 LED SWITCH CONTROLLER |
| 1 | 4120-0223 | CUSTOM MESSAGE FROM ARCHIVE |
| 1 | 4120-0211 | DUAL CHANNEL AUDIO CONTROLLER |
| 1 | 4120-0204 | MICROPHONE AND ENCLOSURE |
| 1 | 4120-0153 | DIGITAL ALARM COMM TRANSMITTER |
| 1 | 4120-0124 | ENHANCED CHARGER PACKAGE |
| 6 | 4120-0111 | MAPNET ISOLATOR MODULE |
| 6 | 4120-0110 | MAPNET IIADDRESSABLE/TRUEALARM |
| 1 | 4120-0100 | ZONE CONFIGURATION CHARGE |
| 1 | 4120-0113 | RS-232/2120COMMW/DIALINPLG |
| 1 | 4120-6014 | MODULAR 4120 NETWORK IFC CARD |
| 1 | 4120-0304 | STYLE 7 REMOTE UNIT INTERFACE |
| 2 | 4120-0142 | RS485 COMMUNICATION MEDIA MODULE |
| 1 | 4120-0451 | PANEL MOUNTED PRINTER |
| 1 | 4190-8101 | COMMAND CENTER |
| 1 | 4190-7003 | DESK TOP PC 200MHZ W/MOUSE |
| 1 | 4190-6030 | RS485 NETWORK INTF CARD – GCC |
| 1 | 4190-5003 | GCC ENGLISH SOFTWARE |
| 1 | 4190-8101 | COMMAND CENTER |
| 1 | 4190-7207 | 21" DESKTOP MONITOR W/TOUCH SCREEN |
| 1 | 4190-7003 | DESK TOP PC 200MHZ W/MOUSE |
| 1 | 4190-6005 | 250 MB TAPE BACK UP UNIT |
| 1 | 4190-5003 | GCC ENGLISH SOFTWARE |
| 1 | 4190-6030 | RS485 NETWORK INTF CARD – GCC |
| 46 | 4903-9305 | A/V 110CD SYNC 25VRMS SPKR RED |
| 5 | 4902-9703 | SPEAKER 25VRMS RED |
| 2 | 4904-9136 | V/O 24VDC 11OCD RED |
| 13 | 4904-9311 | V/O 24VDC 110CD RED SYNC |
| 39 | 4904-9305 | V/O LIFEALARM 15CD RED SYNC |
| 2 | 4904-9136 | V/O 24VDC 110CD RED SYNC |
| 4 | 4009-9002 | NAC POWER EXT 4 PT ST Z 120V |
| 8 | 2081-9272 | BATTERY 6.2AH |
| 24 | 4905-9938 | SYNC CONTROL MODULE CLASS A |
| 9 | 2190-9163 | ADDRESSABLE CONTROL ZAM-SURFACE |
| 4 | 2975-9194 | BACK BOX 6 UNIT BEIGE |
| 4 | 2902-9701 | SPEAKER 4091-14 AP-15TVC |
| 8 | 2081-9028 | ISOLATED LOOP PROTECTOR |
| 6 | 2190-9169 | SHORT CIRCUIT ISOLATION MODULE |
| PREACTION SYSTEM |
| 3 | 2081-9046 | COIL SUPERVISION MODULE |
| 3 | 2080-9029 | SERVICE DISCONNECT SWITCH |
| PRIVATE MODE VISUALS |
| 5 | 4904-9310 | V/O 24VDC 110CD SYNC WHITE |
| 1 | 4904-9302 | V/O 24VDC 30CD SYNC WHITE |
| 13 | 4904-9306 | V/O 24VDC 15CD SYNC WHITE |
| REMOTE ANNUNCIATOR |
| 1 | 4120-8009 | REMOTE ANNUNCIATOR |
| 1 | 4120-2001 | 2UNITW/GLASSDOOR |
| 1 | 4120-0413 | 2 CHANNEL SPEAKER SELECT SWITCH |
| 1 | 4120-0410 | REMOTE MICROPHONE |
| 1 | 4120-0404 | 8/16 3 POS. MAI NT SWITCH |
| 1 | 4120-0301 | 64/64 SWITCH CONTROLLER, |
| 1 | 2975-9190 | 2 UNIT BACK BOX |
| 1 | 4605-9101 | LCD ANNUNCIATOR |
| 1 | 4190-9008 | BACPAC PORTAL |
| 2 | 4190-8121 | GRAPHICAL SCREEN PROGRAMMING |
| 2 | 4190-4005 | 25 TRAVEL SCREEN KEYS |
| 2 | 4190-4004 | 25 CNTRL FUNCTION PTS ON/OFF |
| 40 | 4190-4003 | 25 STATUS ICONS |
| 8 | 4190-4001 | ONE SCREEN DXF TYPE |
| 1 | 4190-9007 | 24 PIN DOT MATRIX PRINTER |
| 75 | OPFA | SIGNAGE |
| PERIPHERAL DEVICES |
| 2 | 4098-9904 | STD DETECTOR VLP-002 |
| 4 | 2081 -9294 | BATTERY 12VDC 12AH VB-012 |
| 30 | 4098-9828 | POLYETHYLENE TUBING SOFT |
| 2 | 2081-9292 | PS 120VAC MZ VPS-300VS-120 |
| 1 | 4098-9924 | SP LABEL WRAP AROUND 200 |
| 112 | 4098-9714 | SSD PHOTO SENSOR |
| 112 | 4098-9792 | SSD SENSOR BASE |
| 333 | 4098-9717 | SSD IONIZATION SENSOR |
| 333 | 4098-9792 | SSD SENSOR BASE |
| 12 | 4098-9733 | SSD HEAT SENSOR |
| 12 | 4098-9792 | SSD SENSOR BASE |
| 10 | 2098-9489 | HEAT DET VERT N/O 302-EPM-194 |
| 10 | 4090-9001 | IAM SUPERVISED IDNET |
| 24 | 2099-9761 | PULL STATION MAPII D/A |
| 1 | 4100-8402 | PLATE MOUNTED GRAPHICS |
| 2 | 4100-7401 | 24 POINT I/O INTERFACE MODULE |
| 1 | OPGASS | OUTS PURCH GRAPHIC ANNUNCIATOR |
| 2 | 2081-9280 | BATT CABINET, 11OAH |
| 4 | 2081-9279 | BATTERY 11 OAH |
| 40 | 4098-9843 | ENCAPSULATED RELAY PAM-SD |
| 40 | 4098-9756 | DUCT SENSOR HOUSING 4 WIRE |
| 40 | 2098-9808 | REMOTE ALARM INDICATOR |
| 40 | 2098-9798 | SAMPLING TUBE 73" |
| 48 | 4090-9001 | IAM SUPERVISED IDNET |
| 31 | 2190-9163 | ADDRESSABLE CONTROL ZAMS |
| 31 | 4903-9301 | A/V LIFEALARM 15CD RED SYNC |
| 15 | 4903-9303 | A/V 30CD SYNC 25VRMS SPKR RED |