PI System

Enraf Tank Gauging System
 Interface, Version 3.20

OSI Software, Inc.
777 Davis St.
San Leandro, CA 94577
USA
(510) 297-5800
(510) 357-8136 (FAX)

OSI Software, GmbH
Hauptstra(e 30
D-63674 Altenstadt
Germany
(49) 6047 2770
(FAX) (49) 6047 6687

Table of Contents

Table of Contents	i

1. Introduction	1

2. PI Point Configuration	2

2. Configuration File	4

2.1. Keywords	4

2.2. Supported Field Codes and Commands	7

3. I/O rate counter on VMS	9

4. Point Source Table definition in PI2	9

5. Communication line in VMS	9

6. Terminal Server Configuration under VMS	10

7. Microlect Settings	11

8. Port Setup Examples	12

9. Installation on VMS	13

10. Sample Interface Installation on VMS	13

11. Installation on Windows NT	14

12. Linking the program on VMS	15

13. Linking the program on Windows NT	15

14. Interactive Startup	16

15. Starting the interface as NT Service	19

16. Shutdown in NT	19

17. Starting the interface as detached VMS process	19

18. Shutdown in VMS	20

19. Error and information messages in VMS	21

20. Error and information messages in NT	21

21. How the Enraf Interface operates	22

22. Hints for PI System Manager	23

23. Revision History	24

# 1. Introduction

This is a description of the Enraf Tank Gauging System Interface to the Plant Information (PI) System. The Interface runs on VAX/VMS, Alpha OpenVMS and Windows NT 4.0. It communicates with the Enraf Tank Gauging System via a LAT port or a local RS232 port connected to a communications port on a Microlect System.

The protocol is described in detail in:

ENRAF NONIUS Interactive Host Communication version PB.000.019.26-45C rev 7 (8.1...)

Supported transmission protocols are:

Asynchronous Communication:
- standard TTY envelope
- envelope for Honeywell TDC 4500/HS4400

The Enraf Tank Gauging System Interface is a scanning interface in which three rates are specified. The first specifies the rate at which all tank data are collected, the second specifies the rate at which the interface checks for exceptions of tank data and the third is used for Output (exception based). Exception reporting for Input is not executed by the interface, instead, the "Update Log" command specified in the Interactive Host Communication Manual is used. Only communication rates and the Microlect System response limit scanning rates. The Interface also supports ASCII text transfer and freeze-file handling. It is possible to synchronize the Microlect date and time with the local time of the interface node.

| Supported Features |  |
| --- | --- |
| Sign up for Updates | yes |
| Exception Reporting | yes, via Microlect |
| PI Net Support | yes |
| PI-API Support | yes |
| Outputs | yes |
| Vendor Software Required | no |
| Number of Points | unlimited |

# 2. PI Point Configuration

Each PI tag represents a single parameter in the Enraf Tank Gauging System for whom valid parameters are for example tank level, volume and temperature. In the following are given special hints, how to configure a PI point for use with the Enraf Tank Gauging System.

Point Name:

The point name is free, according to the normal PI point naming conventions.

Instrument tag:

The Instrument tag field gives the relation to the tanks defined in the Microlect System. The convention is

TKxnnnnn

where x is the measured parameter (ASCII Field code),

B = level
              C = Temperature
              K = Free water volume
              L = Gross measured volume
              M = Net volume
              N = Available product volume
                 .
                 .
                 .

nnnnn is the five character Microlect Tank Name.

Source tag:

For outputs, the tag you are creating is only a pointer tag. The name of the tag, containing the values to be sent to ENRAF, must be entered here. If this field remains empty, the pointer tag itself contains the values to be sent. 
Output tag and source tag must be of type R. However, if you have a PI3 system and the interface is running on Windows NT, you can use a string tag to down line load tank description and tank note. In this case, both output tag and source tag must be string tags.

In addition, set Location 1 to 1, if Output is specified.

Extended Descriptor:

In PI3 systems, if the interface runs on Windows NT, it is possible to store the status of the operation just performed in a string tag. In this case, the Extended descriptor must contain the name of this tag. The syntax is:

STATUSTAG=tagname

Location 1:

This parameter specifies, whether the tag is an input tag or an output tag.

0	for Input
1	for Output

Location 2:

This parameter is only used for Tank description tags.

0	For sending the Tank description to the Event Archive. Note
	that in PI3 systems, the notion of an Event Archive is
	unknown. The tank description will be sent to the PI
	message log and can be accessed via pigetmsg. (Look for 	messages for user “Eventlogger”.)
1	For sending Tank description to the PI Tag Descriptor.
	This works only on a PI2 Home Node and it reflects
	all tags for one tank

Point Source:

The point source is a single character, for example E. In PI2, the Point source must be defined in the point source library prior to point creation.

Point Type:

The Interface supports only the PI points of type real. There is one exception: In a PI3 system, when running the interface on Windows NT, you can down line load the tank description and tank note from a PI3 string tag. This means that besides Real tags, output tags of type String are allowed, too. However, additional checks are performed before the tag is accepted. In this version, output string tags must contain either the character ‘A’ or  ‘D’ at the 3rd position in the Instrument Tag name.
Starting with interface version 3.20, you can use string tags to receive the tank description (product name). To support this, the PI server must be PI3 and the interface must run on NT

Engineering Units:

Levels are given in mm, temperature in degree Celsius and volumes in Barrel. You can scale the values with a parameter in Enraf.cfg.
See chapter "Configuration File".

# 2. Configuration File

For starting the Enraf Interface, you need a configuration File Enraf.cfg. The interface will look for this file in the location you specified via the /cfgfile= startup switch.

This file must contain definition rows for every process value and several keywords. The parameters can be found in the Enraf Interactive Host Communication Manual.

## 2.1. Keywords

protocol

2 asynchronous protocols are supported. The standard envelope protocol is specified using TTY as argument. The argument TDC specifies the envelope for Honeywell TDC 4500/HS4400 systems.

If the protocol keyword is not entered, the standard protocol TTY will be used.

timesync

It is possible to synchronize the Microlect system with your host computer, running the Enraf to PI Interface. The time update happens on a daily basis and the time, when the Microlect is updated with your VAX time, can be specified.

Use

timesync = hh:mm,

where hh stands for hour and mm for minute.

Note: This feature has not yet been tested.

freeze

There are two ways to cause the Microlect to produce a freeze file. First, in using the features of Microlect itself and second, in processing a host request. If the Interface shall take this task, specify the freeze keyword in the form:

freeze = hh:mm

where hh stands for hour and mm for minute.

freeze = 00:00

will cause the Microlect to produce a freeze file every day at midnight.

reserve

If a Group Log is scheduled at freeze time, there are already values in the archive when the freeze file is transferred. The values have to be replaced. Replacing a value takes much longer than adding one. For the time performing replacement, no new values can be scanned. Therefore it is recommended to reserve the time for freeze file data.

The form:

reserve = hh:mm

reserves the specified timestamp once per day.

transmit

To transmit the freeze file at a certain time, use this keyword. The form:

transmit = freeze

can be used, if the keyword freeze is specified too. This is the way to transmit the freeze file direct after its creation and use the time passed to

freeze = hh:mm

as timestamp. The form:

transmit = hh:mm

transmits the current freeze file and assigns the time transferred from Microlect as timestamp.
In both forms all transferred values are written unconditionally to the PI Archive.

Note: To use this feature, freeze file creation must be supported in Microlect.

table

This keyword tells the Configuration File Interpreter, that the following lines are Input or Output configuration lines. All lines between "table = input" and "table = ..." keywords are treated as configured for one Group log/Update log command. The sum of all "length" values can only be up to 132, the items which do not fit are excluded.

table = input

table = output

are valid parameters.

In this Version, only a subset of output parameters is supported. Down line load of tank note book and tank descriptor are supported.

The supported transfer of ASCII text covers tank note book and descriptor as well. See Location 2 for setup.

The file structure is shown in the following example:

; enraf.cfg                         example of a configuration file

;

;  Semicolon is used to comment out the text till the end of the line

protocol = TTY          ; the standard protocol is used

timesync = 1:00         ; time synchronization at 1 o'clock

freeze   = 0:00         ; host initiated freeze file at midnight

transmit = freeze       ; transmit the freeze file, use VAX time

;       transmit = 0:05         ; transmit the freeze file, use Enraf time

table = Input                   ; the following table defines Input fields

; one table is serviced using one command

; No.  Field-  length  value    scale   badcode-   cmpstring       comment

;      code            length           pos

1.     B       7       5       1        5        "LTFSC? "   ; Level

2.     C       6       4       10       4        "FS? "      ; Temperature

3.     K       9       9       100      8        "F "        ; FWVolume

4.     L       10      9       100      9        "S? "       ; GRSVolume

table = Input                   ; here starts table number 2

; the table keyword works like a switch

; No.  Field-  length  value    scale   badcode-   cmpstring       comment

;      code            length           pos

5.     M       10      9       100      9        "S? "       ; NETVolume

6.     N       10      9       100      9        "S? "       ; AVAVolume

7.     G       5       5       10000    4        "F "        ; Density

8.     D       20      20      1        19       ""          ; Description

9.     T       20      20      1        19       ""          ; Tank NOTE

table = Output                  ; here starts output table number 1

; use a special application program

; to pass ASCII data (Descr., Tank Note)

; No.  CMD -   length  value    scale   			       comment

;      code            length

1.     F       5       5       1         			   ; Density

2.     I       20      20      1         			   ; Descr.

3.     J       20      20      1         			   ; Tank NOTE

A limit of 5 input tables each of 12 rows (12 possible Microlect parameters) per table is given in this version. 1 output table with 9 rows maximum can be specified. Each table will be scanned separately. If you need for example Temperature and Level for exactly the same time, group them together in one table. Field code and length are taken directly out of chapter 4 in Enraf Interactive Host Communication Manual (Layout of Tank Data Record). Value length means the length of numeric bytes or ASCII letters, if text is transferred.  Scale is the factor for converting Microlect value into PI value in engineering units:

PI value = Microlect value / scale

Badcodepos is the position in the data record, where the interface checks, if the transferred value is a "Bad Input". Use the dimension bytes. The value is the position in the record (first record position counts as zero). If the character in the badcodeposition equals to anyone of the characters in cmpstring, then the transferred value will be marked as a "Bad Input" in PI.

## 2.2. Supported Field Codes and Commands

See also Chapter 4 of Enraf Host Communication (Layout of Tank Data Record).

This table reflects Input tags:

| Input | ASCII field code | Parameter | comment |
| --- | --- | --- | --- |
|  | A | Tank name | 5 bytes text |
|  | B | Level | 5 + 2 bytes |
|  | C | Temperature | 5 + 1 bytes |
|  | D | Tank description | 20 bytes text |
|  | G | Density or degrees | 5 bytes |
|  | H | TCF | 5 bytes |
|  | I | Sediment and water ratio | 4 bytes |
|  | J | Total volume | 9 + 1 bytes |
|  | K | Free water volume | 9 bytes |
|  | L | Gross measured volume | 9 + 1 bytes |
|  | M | Net volume | 9 + 1 bytes |
|  | N | Available product | 9 + 1 bytes |
|  | O | Mass of the net product | 9 + 1 bytes |
|  | P | Empty volume above product | 9 + 1 bytes |
|  | Q | Flow rate | 6 bytes |
|  | R | Pressure | 5 + 1 bytes |
|  | T | Tank note book | 20 bytes text |
|  | U | Oldness of level data | 6 bytes |
|  | V | Float position | 6 bytes |
|  | W | Free water level | 5 + 1 bytes |
|  | Z | Free water volume | 9 + 1 bytes |
|  | a | Reference temperature | 4 bytes |
|  | b | Density at reference temperature | 5 + 2 bytes |
|  | c | Temperature | 4 bytes |
|  | d | Density at observed temperature | 5 + 1 bytes |

See also Chapter 2 of Enraf Host Communication (Basic Commands Supported).

This table reflects Output tags and other commands:

| Output | Command | Parameter | comment |
| --- | --- | --- | --- |
| Request | 1 | Group log | request for all Input values |
|  | 3 | Freeze command | specify in config file |
| Request | 4 | Transmit freeze file | specify in config file |
| Request | 5 | Update log | request Input by exception |
|  | C | Down line load date and time | specify in config file |
|  | D | Down line load manual level | 5 bytes numeric |
|  | E | Down line load manual temp. | 4 bytes numeric |
|  | F | Down line load density | 5 bytes numeric |
|  | G | Down line load free water level | 5 bytes numeric |
|  | H | Down line load free water volume | 9 bytes numeric |
|  | I | Down line load description | PI3 only, via string tag |
|  | J | Down line load note book | PI3 only, via string tag |
|  | W | Down line load manual pressure | 5 bytes numeric |

# 3. I/O rate counter on VMS

The I/O rate counter measures the input rate to PI. Insert the lines

SY:Enr001,n1

SY:Enr002,n2

in the file PISysDat:IORates.dat , where n1 is the counter number selected via /EC=. Use a free number between 0 and 34. Use n2 as n1 plus 1.

# 4. Point Source Table definition in PI2

To prepare PI 2 for interface use you must define an interface-specific point source code using the PI System Point Source Editor, for example:

|  | Loc 1 | Loc 2 | Loc 3 | Loc 4 | Loc 5 |
| --- | --- | --- | --- | --- | --- |
| Location Minimum | 0 | 0 | 0 | 0 | 0 |
| Location Maximum | 1 | 1 | 0 | 0 | 0 |

Point Source Code: E

Point Source Descriptor: Enraf Microlect

# 5. Communication line in VMS

Use a null modem cable between the Microlect System and the VAX or Alpha. To set up the port in the server, use the NCP program. For defining VMS port characteristics, you can use the PISysExe:EnrafSetTerm.com and PISysExe:EnrafSTerm.com template files. Modify them according to your needs. Then execute

@PISysExe:EnrafSetTerm.

$ !  ENRAFSetTerm.com                                    KP 10-Feb-1999

$ !====================================================================

$ !

$ ! This file creates and sets up the LAT ports for the Enraf interfaces.

$ ! Execute this procedure during system startup.

$ !

$   @PISysExe:ENRAFSTerm TTA2:

$ ! @PISysExe:ENRAFSTerm Lta102: Serv01 Port_4

$ ! @PISysExe:ENRAFSTerm Lta103: Serv01 Port_5

$ ! @PISysExe:ENRAFSTerm Lta104: Serv01 Port_6

$ ! @PISysExe:ENRAFSTerm Lta105: Serv01 Port_7

$ !

$ Exit

$ !  ENRAFSTerm.com                                      KP 10-Feb-1999

$ !====================================================================

$ !

$ ! This file creates and sets up the LAT port for one Enraf interface.

$ ! Modify this template where necessary (speed, parity)

$ ! P1 is the terminal name.

$ ! P2 is the terminal server name.

$ ! P3 is the terminal server port name

$ ! Execute this procedure during system startup.

$ !

$ Say := write sys$output

$ Latcp = "$LATCP"

$ !

$ !   Determine the Device to Create

$ !

$ Termname = P1

$ If (Termname .eqs. "") then inquire Termname "Terminal"

$ If (f$getdvi(Termname,"EXISTS")) Then goto Device_Exists

$ Server = P2

$ If (Server .eqs. "") then inquire Server "Server"

$ Port = P3

$ If (Port .eqs. "") then inquire Port "Server Port"

$ !

$ Latcp Create Port 'Termname'

$ Latcp Set Port 'Termname' /Node='Server' / Port='Port'

$ !

$DEVICE_EXISTS:

$ !

$ !   Setup Terminal Characteristics

$ !

$ wait 00:00:05

$ Set terminal                          -

/permanent                      -

/NoTTsync                       -

/Speed=4800                     -

/Noautobaud                     -

/NoEcho                         -

/NoCommsync                     -

/NoEightBit                     -

/Parity=odd                     -

/Pasthru                        -

/Altypeahd                      -

/NoModem                        -

/NoDisconnect                   -

/Nointeractive                  -

/NoBroadcast                    -

/NoScope                        -

/NoWrap                         -

'Termname'

$ set prot=(w:rwlp)/dev 'Termname'

$ !Show Term 'Termname'

$ Exit

# 6. Terminal Server Configuration under VMS

If you use a Terminal Server to connect to Enraf Microlect, it will be  necessary to configure the ports you are using. Below, you can find an example for an NCP session that was performed to set the correct values on terminal server ts01 for

character size	(to enable 8 bit transfer)
flow control	(to prevent XON/XOFF characters from having any meaning)
stop bits
speed		(Baudrate)

(Enter help at the Local> prompt for information on how to configure other important parameters.)

$ set default sys$system:

$ mc ncp

NCP>connect node ts01

Console connected (press CTRL/D when finished)

#<enter terminal server password (network)

Network Access SW V1.5 for DS700-08 (BL95D-34)

Copyright 1995, Digital Equipment Corporation – All Rights Reserved

Please type HELP if you need assistance

Enter username> <Username>

Local>  set privilege

Password> <enter terminal server password (local)

Local> define port 2 character size 8 flow control disable stop bits dynamic speed 9600

Local> set port 2 character size 8 flow control disable stop bits dynamic speed 9600

Local> show port 2

Port  2:                               Server: TS01

Character Size:            8           Input Speed:               9600

Flow Control:           None           Output Speed:              9600

Parity:                  Odd           Modem Control:         Disabled

Stop Bits:           Dynamic

Access:               Remote           Local Switch:              None

Backwards Switch:       None           Name:                    PORT(2

Break:                 Local           Session Limit:                1

Forwards Switch:        None           Type:                      Ansi

Default Protocol:        LAT           Default Menu:              None

Preferred Service: None

Authorized Groups:   0

(Current)  Groups:   0

Enabled Characteristics:

Local>CTRL/D

NCP>exit

$

# 7. Microlect Settings

The Microlect System requests:

Bit pattern

Start bit		:		one
Data bits	:		seven, starting with LSB
Parity bit	:           		one, odd parity (even for Honeywell TDC)
Stop bit		:           		one

Baud rate must be specified out of the following list:

50     75    150    300    600   1200   2400   4800

# 8. Port Setup Examples

Here is a correct Setup of a DEC-Server port (Honeywell envelope):

Port  8:                               Server: SERV01

Character Size:            7           Input Speed:               4800

Flow Control:            CTS           Output Speed:              4800

Parity:                 Even           Modem Control:         Disabled

Stop Bits:                 1

Access:               Remote           Local Switch:              None

Backwards Switch:       None           Name:                    PORT_8

Break:              Disabled           Session Limit:                4

Forwards Switch:        None           Type:                      Soft

Default Protocol:        LAT

Preferred Service: None

Authorized Groups:   0

(Current)  Groups:   0

Enabled Characteristics:

Input Flow Control,  Output Flow Control

The terminal setup is shown below:

Terminal: _LTA100:    Device_Type: Unknown       Owner: No Owner

Input:   4800      LFfill:  0      Width:  80      Parity: Even

Output:  4800      CRfill:  0      Page:   24      Terminate on parity errors

Terminal Characteristics:

Passall            No Echo            Type_ahead         No Escape

No Hostsync        No TTsync          Lowercase          No Tab

No Wrap            Hardcopy           No Remote          No Eightbit

No Broadcast       No Readsync        No Form            Fulldup

No Modem           No Local_echo      No Autobaud        Hangup

No Brdcstmbx       No DMA             Altypeahd          Set_speed

No Commsync        Line Editing       Overstrike editing No Fallback

No Dialup          No Secure server   No Disconnect      Pasthru

No Syspassword     No SIXEL Graphics  No Soft Characters No Printer Port

Numeric Keypad     No ANSI_CRT        No Regis           No Block_mode

No Advanced_video  No Edit_mode       No DEC_CRT         No DEC_CRT2

No DEC_CRT3        No DEC_CRT4        VMS Style Input

Distinguish Microlect setup:

Use Microlect Terminal to enter: LOOK 49        example result: 7C
                                 LOOK 53                        7C
Coding:

40 :   1 Stop      00 :    Parity none     08 :    1200

80 :   1.5 Stop    10 :    Parity odd      0B :    2400
   C0 :   2 Stop      30 :    Parity even     0C :    4800
                                              0D :    9600

# 9. Installation on VMS

To install the interface, you must define a point source code, setup the I/O port, select two I/O rate counters and modify the PI startup and shutdown command files. In addition, you need a configuration File Enraf.cfg, where you can define the Microlect parameters for your PI points. If the interface runs on VMS, you can optionally set two performance monitoring tags.

The following files are shipped:

ENRAF.OBJ;1                                  231/231      8-MAR-1999 15:22:06.79

ENRAFDEVICE.OBJ;1                             45/45       8-MAR-1999 15:23:36.01

ENRAFPIDETACH.COM;1                            2/3       10-FEB-1999 15:51:16.00

ENRAFPIGMBH.OBJ;1                             44/45       8-MAR-1999 15:23:52.81

ENRAFPILINK.COM;1                              3/3       10-FEB-1999 15:41:33.00

ENRAFPISTART.COM;1                             1/3       10-JUN-1997 11:22:49.16

ENRAFPISTOP.COM;1                              1/3       10-FEB-1999 15:52:06.00

ENRAFSETTERM.COM;1                             2/3        7-JUN-1997 14:26:25.34

ENRAFSTERM.COM;1                               3/3        8-MAR-1999 15:56:35.94

ENRAF_01.CFG;1                                 5/6       10-FEB-1999 14:21:55.00

ENRAF_01.COM;1                                 2/3        8-JUN-1997 13:09:20.93

KITINSTAL.COM;1                                1/3        8-MAR-1999 15:34:01.56

The interface files will be shipped on a 4mm DAT tape as a VMS Save Set. To install, log in as SYSTEM and enter the command

$ @sys$update:vmsinstal

Follow the installation procedure. Note that the name of your tape drive may differ from the above.

# 10. Sample Interface Installation on VMS

Welcome to OpenVMS (TM) VAX Operating System, Version V7.1

Username: system

Password:

Welcome to OpenVMS (TM) VAX Operating System, Version V7.1 on node V1

Last interactive login on Wednesday, 24-FEB-1999 14:57

Last non-interactive login on Monday,  8-MAR-1999 00:00

V1::SYS$SYSROOT:[SYSMGR]>@sys$update:vmsinstal

OpenVMS VAX Software Product Installation Procedure V7.1

It is 8-MAR-1999 at 15:37.

Enter a question mark (?) at any time for help.

%VMSINSTAL-W-ACTIVE, The following processes are still active:

NFS$SERVER

UCX$PORTM

* Do you want to continue anyway [NO]? y

* Are you satisfied with the backup of your system disk [YES]?

* Where will the distribution volumes be mounted: mkb400:

Enter the products to be processed from the first distribution volume set.

* Products: enraf031

* Enter installation options you wish to use (none):

Please mount the first volume of the set on  MKB400:.

* Are you ready? y

%MOUNT-I-MOUNTED, ENRAF mounted on _V1$MKB400:

The following products will be processed:

ENRAF V3.1

Beginning installation of ENRAF V3.1 at 15:38

%VMSINSTAL-I-RESTORE, Restoring product save set A ...

Copying Enraf Microlect (V. 3.10) Interface modules...

%COPY-S-COPIED, V1$DKA200:[SYS0.SYSUPD.ENRAF031]ENRAF.OBJ;1 copied to DKB0:[PIBUILD]ENRAF.OBJ;1 (231 blocks)

%COPY-S-COPIED, V1$DKA200:[SYS0.SYSUPD.ENRAF031]ENRAFDEVICE.OBJ;1 copied to DKB0:[PIBUILD]ENRAFDEVICE.OBJ;1 (45 blocks)

%COPY-S-COPIED, V1$DKA200:[SYS0.SYSUPD.ENRAF031]ENRAFPIDETACH.COM;1 copied to DKB0:[PIBUILD]ENRAFPIDETACH.COM;1 (2 blocks)

%COPY-S-COPIED, V1$DKA200:[SYS0.SYSUPD.ENRAF031]ENRAFPIGMBH.OBJ;1 copied to DKB0:[PIBUILD]ENRAFPIGMBH.OBJ;1 (44 blocks)

%COPY-S-COPIED, V1$DKA200:[SYS0.SYSUPD.ENRAF031]ENRAFPILINK.COM;1 copied to DKB0:[PIBUILD]ENRAFPILINK.COM;1 (3 blocks)

%COPY-S-COPIED, V1$DKA200:[SYS0.SYSUPD.ENRAF031]ENRAFPISTART.COM;1 copied to DKB0:[PIBUILD]ENRAFPISTART.COM;1 (1 block)

%COPY-S-COPIED, V1$DKA200:[SYS0.SYSUPD.ENRAF031]ENRAFPISTOP.COM;1 copied to DKB0:[PIBUILD]ENRAFPISTOP.COM;1 (1 block)

%COPY-S-COPIED, V1$DKA200:[SYS0.SYSUPD.ENRAF031]ENRAFSETTERM.COM;1 copied to DKB0:[PIBUILD]ENRAFSETTERM.COM;1 (2 blocks)

%COPY-S-COPIED, V1$DKA200:[SYS0.SYSUPD.ENRAF031]ENRAFSTERM.COM;1 copied to DKB0:[PIBUILD]ENRAFSTERM.COM;1 (3 blocks)

%COPY-S-COPIED, V1$DKA200:[SYS0.SYSUPD.ENRAF031]ENRAF_01.CFG;1 copied to DKB0:[PIBUILD]ENRAF_01.CFG;1 (5 blocks)

%COPY-S-COPIED, V1$DKA200:[SYS0.SYSUPD.ENRAF031]ENRAF_01.COM;1 copied to DKB0:[PIBUILD]ENRAF_01.COM;1 (2 blocks)

%COPY-S-NEWFILES, 11 files created

Linking Interface (PI must be running!) ...

creating PISysExe:ENRAF.EXE ...

copying command files to PISysExe: ...

%COPY-S-COPIED, DKB0:[PIBUILD]ENRAFPISTART.COM;1 copied to DKB0:[PISYSEXE]ENRAFPISTART.COM;1 (1 block)

%COPY-S-COPIED, DKB0:[PIBUILD]ENRAFPISTOP.COM;1 copied to DKB0:[PISYSEXE]ENRAFPISTOP.COM;1 (1 block)

%COPY-S-COPIED, DKB0:[PIBUILD]ENRAFPIDETACH.COM;1 copied to DKB0:[PISYSEXE]ENRAFPIDETACH.COM;1 (2 blocks)

%COPY-S-COPIED, DKB0:[PIBUILD]ENRAFSTERM.COM;1 copied to DKB0:[PISYSEXE]ENRAFSTERM.COM;1 (3 blocks)

%COPY-S-COPIED, DKB0:[PIBUILD]ENRAFSETTERM.COM;1 copied to DKB0:[PISYSEXE]ENRAFSETTERM.COM;1 (2 blocks)

%COPY-S-COPIED, DKB0:[PIBUILD]ENRAF_01.COM;1 copied to DKB0:[PISYSEXE]ENRAF_01.COM;1 (2 blocks)

%COPY-S-NEWFILES, 6 files created

copying cfg files to PISysDat: ...

%COPY-S-COPIED, DKB0:[PIBUILD]ENRAF_01.CFG;1 copied to DKB0:[PISYSDAT]ENRAF_01.CFG;1 (5 blocks)

done

%VMSINSTAL-I-MOVEFILES, Files will now be moved to their target directories...

Installation of ENRAF V3.1 completed at 15:40

Enter the products to be processed from the next distribution volume set.

* Products:

VMSINSTAL procedure done at 15:40

V1::SYS$SYSROOT:[SYSMGR]>

# 11. Installation on Windows NT

For Windows NT, the following files are shipped on a floppy disk or a CD ROM:

enraf.exe    (Interface executable)
enraf.bat    (Start file template, must be adapted)
enraf.cfg    (Configuration file template, must be adapted)

To install the interface, copy these files into a directory of your choice.

# 12. Linking the program on VMS

The interface program will automatically be linked during the installation via VMSInstal. To re-link, execute

@PIBuild:EnrafPILink

To ensure that the interface  is re-linked when the PI System (or PINet) is relinked, modify PISysMgr:sitespecificlink.com and insert the line

$ @PIBuild:EnrafPILink

# 13. Linking the program on Windows NT

Linking is not required on Windows NT because the interface executable is shipped.

# 14. Interactive Startup

The interface ships with a startup template file. Please modify this file and enter the correct startup switches that apply to your situation. For both the NT and the VMS version, when running as an NT Service or a detached process, respectively, the interactive startup file is read to evaluate the command line arguments. Running the interface non-interactively is the recommended method.

To start the interface manually on Windows NT, execute the start file enraf.bat.

To start the interface manually on VMS, log in as SYSTEM and enter this command:

@PISysExe:Enraf_01

The following startup switches are supported. You can specify them in any order. Do not type spaces left and right from the equal sign.

/PS=point source
/IN=interface number, default: 1
/DEB=debug level for Interface, default: 0
/OUTPUT=output filename (NT only)
/HOST=hostname:port (NT only)
/PI_USER=username, (NT only, default: piadmin)
/PI_PWD=password, (NT only, default: “” (empty = no password))
/PORT=portname, default: COM1
/CFGFILE=path + filename for configuration file, NT default: c:\enraf.cfg
                                                                 VMS default: PIResources:Enraf.cfg
/MORE=path + filename for enraf.more, NT default: c:\enraf.more
                                                             VMS default: PISysMgr:enraf.more
/BAUD=[baudrate, databits, parity, stopbits], default: [4800/8/2/1] (NT only)
/GRP=group log steps, default: 300
/UPD=update log steps, default: 60
/DWN=downline load steps, default: 30
/EC=input rate counter, default: 31 (VMS only)

The parameters have the following meaning:

/PS=Point Source

The interface will build the tag list based upon the point source. All tags whose point source matches the specification in the /PS= switch will belong to the interface. However, due to additional checking, tags may be rejected if other parts of the point configuration are incorrect.

/IN=Interface number

Multiple copies of the interface can run on the same node. However, for each interface, a separate serial line is needed. You must choose another point source to tell tags from different interface instances.

/DEB=debug level

Usually, the interface prints only a few informational lines to the log file. You can force it to provide more information by choosing a debug level > 0. Note that you must restart the interface if you want to change the debug level.

/OUTPUT=output file name                (NT only)

Specify the path to the interface log file. All interface information will go to this file. On the next interface start, this file will be renamed and a fresh one will be used.

/HOST=hostname:port                    (NT only)

Enter the name of your PI Home Node here. If your Home Node is a PI3 system, you must append :5450 to the host name.

/PI_USER=username                       (NT only)

The interface logs in to the PI Server. It will act with the rights of the user specified here.

/PI_PWD=password                        (NT only)

If PI_USER has a password in PI, it can be specified here. However, if you do not want to store the password in the interface startup file, there is another method. Specify /PI_USER, but omit /PI_PWD. Then start the interface interactively. You will be prompted for the password. Type it in and press <Return>. It will not appear on the screen. The interface will use the password for login to PI. In addition, it will encrypt the password and store it in the file ifc_pi.pwd. On the next start, either interactively or as NT service, the interface will use this information and not prompt for the password again. If you prefer to run the interface as an NT service, make sure that you ran it interactively at least once, in order to create ifc_pi.pwd.

/PORT=portname

This is the name of the serial port. For example: /PORT=COM1.

/CFGFILE=path + filename for configuration file

This is the path to enraf.cfg.

/MORE=path + filename for enraf.more

On interface startup, a list of all available tanks is created internally. The file enraf.more contains a list of those tanks for which PI tags have not been defined.

/BAUD=[baudrate, databits, parity, stopbits]                (NT only)

Specify the settings for the serial line here. Valid values are:
baud:		50, 75, 150, 300, 600, 1200, 2400, 4800
databits:	7, 8
parity:		0 (even), 1 (odd), 2 (no)
stopbits:	0 (1 stop bit), 1 (2 stop bits)

Make sure that the values match the Microlect settings. This parameter has no meaning for VMS.

/GRP=group log steps

number of  seconds between group log  (15 - 28800)

/UPD=update log steps

number of  seconds between update log (15 - 900)

/DWN=downline load steps

number of  seconds between down line load (15 - 28800)

/EC=input rate counter, default: 31 (VMS only)

Input rate counter number n1 (1 - 34)

# 15. Starting the interface as NT Service

It is possible to configure the Enraf interface as NT service. ‘cd’ to the interface directory and enter the following command:

enraf.exe –install –depend=tcpip –name=”PI Enraf Interface”

If PI-API buffering is enabled, the following line will install enraf.exe as an NT service, being dependent on bufserv and TCP/IP:

enraf.exe –install –depend=”bufserv tcpip” –name=”PI Enraf Interface”

Start the interface from the Windows NT Control Panel or via

enraf.exe –start

Make sure that enraf.bat resides in the same directory as enraf.exe.

If you are running the interface on a Windows NT PI3 Home node, put the enraf files enraf.exe, enraf.bat, enraf.cfg into an enraf subdirectory below the ‘interfaces’ folder, e.g. into C:\PI\interfaces\enraf. Modify pisrvsitestart.bat in order to look like this:

echo Starting Site Specific PI System Services...
..\interfaces\rmp_sk\rmp_sk –start
..\interfaces\random\random –start
..\interfaces\enraf\enraf –start
:theend

If your PI system starts automatically on System startup, configure the enraf service to be started automatically as well. Include –auto in the service installation command shown above or choose ‘Automatic’ from the Control Panel ->Services menu.

# 16. Shutdown in NT

If you had started the interface interactively in a DOS window, simply press CTRL/C. If the interface was started as service, stop it via the Control Panel or ‘cd’ into the interface directory and type

enraf.exe –stop

On a Windows NT PI3 Home Node, include the interface stop procedure in pisrvsitestop.bat. It should look like this:

echo Stopping Site Specific PI System Services...
..\interfaces\rmp_sk\rmp_sk –stop
..\interfaces\random\random –stop
..\interfaces\enraf\enraf –stop
:theend

All tags will receive the Digital State “Shutdown”.

You can remove the service via

enraf.exe -remove

# 17. Starting the interface as detached VMS process

To start the interface, execute

$ @PISysExe:EnrafPIStart

To insure interface start on PI or PINet start, add this line to PISysMgr:SiteStart.com

# 18. Shutdown in VMS

To shut down the interface, execute

$ @PISysExe:Stop Enraf-1

To insure interface stop on PI or PINet stop, add this line to PISysMgr:SiteStop.com

All tags will receive the Digital State “Shutdown”.

# 19. Error and information messages in VMS

You can find messages from the interface in two places:

The PI message log, PISysMgr:PIMessLog.txt.

The interface puts its error and information messages in this file, except for fatal errors that prevented the interface from starting up.

The interface's output file, PISysExe:Enraf_01.out.

If the interface encounters a fatal error that prevents it from starting up, it puts the error message in this file. If the interface stops because of a program error, VMS may place traceback or other information in this file. The interface also copies selected messages to this file.

A list of all expected but missing PI points will be logged in PISysMgr:Enraf.more.

# 20. Error and information messages in NT

You can find messages from the interface in two places:

- In the interface output file specified via /OUTPUT

- In pipc.log (e.g. c:\pipc\dat\pipc.log)

- In enraf.more (list of tanks for which tags do not exist). This file will

be created in the interface directory.

# 21. How the Enraf Interface operates

At startup, the Interface checks all command line parameters. If one of them is out of range, the interface stops itself and generates an error message. If the parameters are all right, the interface runs the initialization part. Here it assigns the passed communication line. The interface collects a list of all tank information from the Microlect System and attempts to find corresponding PI points based on the Extended Descriptor and the configuration file.

A list of possible instrument tags is generated for those tank parameters, which do not have corresponding PI tags. See the file Enraf.more.

Data 
Acquisition:

Data are scanned in two different ways. Similar to exception reporting the interface scans for update data using the "Update Log" command of the Microlect System. Second it uses the "Group Log" command for getting a full data set. The scanning rates have to be passed in the command line.  Update Log scan rate ranges from 15 to 900 seconds and Group Log is from 900 to 28800 seconds.

In this interface the commands "Group Log" and "Update Log" are used. In both types the records A (tank name), B (level), C (temperature), K or L or M or N (volume) and others according to the configuration file, are required.  If an error marked value is transferred by the Microlect System, this value will be marked as well as a "Bad Input" in the PI System.  The interface ignores any result that does not match a PI tag.

If freeze file is specified, the Interface makes sure, that at the specified freeze time the communication between the interface node and Microlect is ready for the Freeze Command. If "transmit = freeze" is part of the configuration file, the freeze file will be transferred directly after the "freeze command". Otherwise the transfer is done at the specified time. The timestamp for all tank parameters requested from the freeze file will be the one taken from the freeze = hh:mm line (transmit = freeze) or taken from the first reply record, if transmit = hh:mm.

Data
Output:

"Down line load" Microlect commands are supported according to table 2 in chapter 3.2. Note that PI3 string tags are required to provide tank name, tank description and tank note for download to Microlect.

All Output values are transmitted exception based, with a scan rate, specified via the /DWN parameter in the command line (range between 15 and 28800 seconds).

Physical connection:

For line noise or temporary disconnection the timeout is set to 300 seconds. If a timeout occurs, a message is written and all Enraf tags will get an "I/O Timeout" value. The reestablishment of the communication line will be reported too.  To communicate with the Microlect System the given protocol is used. See also ENRAF NONIUS Interactive Host Communication version PB.000.019.26-45C rev 7 (8.1...).

# 22. Hints for PI System Manager

Before Installation of the Enraf Interface, make sure that you definitely know the Microlect setup (protocol, serial line type, speed, parity, ...).
Is the Server set up correctly and does the serial line correspond to it?

# 23. Revision History

| Date | Author | Comments |
| --- | --- | --- |
| Apr 1993 | BB | Written |
| Dec 1998 | KP | Version 3.0, interface ported to NT |
| Feb 1999 | KP | Revised, added information about NT services |
| Mar 1999 | KP | Updated for VMS |
| Dec 1999 | KP | Revised, String tags can be used for Tank description etc. |
| Feb 2000 | KP | Added hints for terminal server setup |