PETROLEUM AND NATURAL GAS REGULATORY BOARD

NOTIFICATION

New Delhi, the 27th August,2008

G.S.R. 612(E).-In exercise  of the powers conferred  by section 61 of the Petroleum  and Natural Gas Regulatory  Act, 2006 (19 of 2006), the Petroleum  and Natural  Gas Regulatory  Board hereby makes the following regulations, namely:-

1. 	Short title and commencement.

(1) These regulations may be called the Petroleum and Natural Gas Regulatory Board (Technical Standards and Specifications including Safety Standards for City or Local Natural Gas Distribution Networks) Regulations, 2008.

(2) They  shall  come  into force  on the date  of their  publication  in the Official

Gazette.

2. 	Definitions.

(1) In these regulations unless the context otherwise requires,-

(a) 	“Act”  means  the  Petroleum and  Natural  Gas  Regulatory Board  Act,

2006;

(b) 	“active   regulator”  means   a  regulator  in  pressure   regulating  station

(PRS) that normally  controls  the outlet pressure;

(c) 	“authorized person”  means  a competent person  who  is assigned by the owner  or operator to carry  out a specific  job based  on his competency level as laid down by the Board under regulations;

(d) 	“city  or local  natural  gas distribution network” (hereinafter referred  to as  CGD  network) means  an  interconnected network  of  gas  pipelines and the  associated  equipments  used  for  transporting  natural   gas  from  a  bulk supply  high  pressure  transmission main  to  the  medium  pressure   distribution grid   and   subsequently   to   the   service    pipes   supplying   natural    gas   to domestic, industrial or commercial premises and  CNG  stations  situated  in a specified geographical area;

(e) 	“consumer meter”  means  a meter  that  measures gas  delivered to a consumer at the consumer’s premises;

(f) 	“creep   relief   valve”   means   a  relief   valve   installed   to  relieve   over pressure  caused  by creep in the downstream system  and having  maximum 1

% flow capacity;

(g) 	“city  gate  station  (CGS)”  means  the  point  where  custody  transfer  of

natural  gas from  natural  gas pipeline  to the CGD  network  takes  place  and this may also be referred  to as City Gate Measuring and Pressure  Regulating Station;

(h) 	“competent  person”   means   an  individual  recognized  by  the  CGD network  owner/operator based  on his proficiency and  skill set achieved by appropriate combination of education, training  and practical experience in the critical  traits as laid down by the Board under regulations;

(i) 	“Distribution Pressure  Regulating Station  or  District  Regulating Station (DPRS)”  means  a  station  located  within  authorized area  for  CGD  network having  isolation, pressure  regulating and overpressure protection devices;

(j) 	“electro  fusion  joint”  means  a joint  made  in thermo  plastic  piping  by passing   the  current  through   the  electrical coil  provided in  the  fitting  and heating   the  parts  sufficiently  to  permit   adequate  flow  and  fusion   of  the materials between the two surfaces  put in contact;

(k) 	“Monitor  and   Active   Regulators”  means   an   arrangement  of  two regulating  devices   in  series  whose  pressure   settings   are  stepped   so  as  to allow  one  (Active)   normally   to  control   the  outlet  pressure   and  the  other (Monitor) to assume  control  in the event of failure of the active device;

(l) 	“operator”  means   an  entity   that  operates  CGD   network   with  the authorization of the Board;

(m) 	“owner”  means  an entity  that  owns  the CGD  network  and  has  been authorized by the Board;

(n) 	“primary   network”  means  a  part  of  CGD  network   that  operates  at pressure  above  100  psig  (7 bar)  and  below  711  psig  (49 bar)  and  pipelines forming  part of this network  called Gas Main or Distribution Main or Ring Main shall  be  designed to ensure  uninterrupted supply  of gas  from  one  or more City Gate Stations  to supply  gas to the secondary gas distribution network  or service  lines to bulk customers through  service  lines;

(o) 	“Slam  Shut  Valve”  means  a valve  that  is designed to close  quickly  in the event  of an abnormal pressure  (whether excess  or low) being  detected at a selected point in a gas system;

(p) 	“secondary network” means  a part of CGD  network  that operates at a  pressure   below   100  psig  (7  bar)  and  above   1.5  psig  (100  mbar)   and pipelines forming  part of this network  shall be called  low-Pressure Distribution Mains  which  shall  be  designed  to  ensure   uninterrupted  supply  to  tertiary network  or to industrial consumers through  service  lines;

(q) 	“sub-transmission pipeline” means  a high pressure  pipeline  connecting the  main  transmission pipeline  to the  city  gate  station  but  is owned  by the CGD entity;

(r) 	“tertiary   network”  means   a  part  of  CGD  network   that  operates  at

pressure   less  than   1.5  psig(100   mbar)   and  pipelines  forming   part  of  this network   to  service  Pressure   Distribution Mains  shall  be  designed to  ensure uninterrupted gas supply to service  lines;

(2) Words  and  expressions   used  and  not  defined  in  these  regulations,   but defined in the Act or in the rules or regulations made thereunder, shall have the meanings respectively assigned to them in the Act or in the rules or regulations, as the case may be;

3.   Application.

Definitions, design,  materials and equipment, welding,  fabrication, installation, testing,  operation and maintenance and corrosion control of  CGD  network  shall  be  in  accordance with  requirements of  ASME B31.8  except  insofar  as such  requirements are  specifically cancelled, replaced 	or 	modified 	by 	the 	requirements 	specified 	in 	these regulations.

4.   Scope.

(a) These  regulations cover  the design,  materials, fabrication, installation, inspection and testing, commissioning, operation, maintenance, modifications and abandonment of CGD network  for domestic, commercial and industrial users.

(b) Requirements   of   these    regulations   shall    apply    to   all   pipelines, distribution  mains  and  piping  facilities   downstream  of  inlet  isolation valve  of city gate  station  (CGS)  up to and  including consumer meter for  commercial or  industrial customer and  up  to  final  isolation  valve including connecting hose to gas appliance for domestic consumer.

(c) Design,    materials,  fabrication,  installation,  inspection  and   testing, commissioning, 	operation, 	maintenance, 	modifications 	and abandonment of steel pipeline  between city gate station  and natural gas pipeline  (sub transmission pipeline) shall be as per separate regulations.

(d) The CNG Station,  CNG Mother  Station,  CNG On-Line  Station  and CNG Daughter Station  shall  be designed, operated and  maintained in line with the requirements of the Chief  Controller of Explosives as detailed in the Gas Cylinder  Rules,  2004  as modified or amended from  time  to time.  This includes  compression, handling and transportation activities of compressed natural  gas.

(e) These    regulations   also   cover    safety    aspects    of   operation   and maintenance of CGD  network  and  the  requirements covered  herein these  regulations are  meant  to  supplement the  safety  requirements already  covered  under ASME B 31.8.

5.   Intent.

(a) It is intended to apply these regulations to all new and such aspects  of already  existing  networks as design,  fabrication, installation, testing  at the time of construction and commissioning. However, if an entity  has laid, built,  constructed or expanded the CGD  infrastructure based  on some other standard or is not meeting  the standards specified in these regulations, the entity needs  to carry out a detailed  technical audit of its infrastructure through  a Board  authorized or approved third  party agency 	by 	the 	Board. 	The 	entity    thereafter   shall 	submit 	the recommendations made  by the  third  party  along-with its time-based mitigation plan and implementation schedule to the Board for authorization within  six months  from  the  date  of notification of these regulations.

(b) The continuation  of operation  of existing CGD network shall be allowed only if it meets the following requirements, namely:-

(i)  The  CGD  system  downstream  of  city  gate  station  shall  have  been tested initially at the time of commissioning  in accordance with ASME B 31.8 Chapter IV (with minimum test pressure of 1.4 times of MAOP for steel network and 1.4 time MAOP or 50 PSI whichever  is higher for PE network).   The entity should  have proper  records  of the same.  Such test   record   shall   have   been   valid   for   the   current   operation. Alternatively,   if  such  a  record  is  not  available,   the  entity  should produce in service  test record of the CGD network having tested at a pressure of 1.1 time of MAOP as per ASME B 31.8;

(ii) The CGD system has leak detection system in position and is operative.

For pipeline  network  it shall be odorisation  based and for enclosures such  as  CGS,  above  ground  DPRS,  it  shall  be  gas  leak  detection based.

(iii) The CGD system has in position necessary pressure relief valves;  and

(iv) There shall be protection  of the system against  third party damages both in respect to steel pipe, PE pipe and copper tubing.

Provided that-

(a) The  entity  shall  submit  self-certification   in  support  of  meeting  the above requirements within a month of notification of these regulations and in addition the certification  by the approved  or authorised  third party shall be made available to the Board within six months of notification;

(b) Certifications  referred to in para (a) shall be done both for operation and  maintenance   and  infrastructure   of  the  entity   and  shall   be submitted to the Board with mitigation plan and implementation schedule;

(c) The critical  components of the system  as identified by the Board for such  existing   networks  shall  be  complied  with  these  regulations within  a period  specified at Appendix-I and  the  authorized entity shall maintain the integrity  of the existing  system  at all times; and

(d) Provisions 	of 	these 	regulations 	related 	to 	operation 	and maintenance  procedures  shall   also   be   applicable  to  all  such existing  installations.

6. 	The standard.

Technical  standards  and specifications  including  safety  standards  (hereinafter referred to as standards) for city or local natural gas distribution networks are as specified in Schedule–I which cover material and equipment (Schedule–1A), welding (Schedule–1B),  piping system components  and fabrication  (Schedule–

1C), design, installation and testing (Schedule–1D), operating and maintenance procedures (Schedule–1E), corrosion control (Schedule–1F) and miscellaneous (Schedule–1G).

7. 	Default and consequences.

(1) There  shall  be a system  for ensuring  compliance  to the provision  of these regulations through conduct of technical and safety audits during the construction, commissioning and operation phase, as well as on an on-going basis as may be specified from time to time.

(2) The   Board   shall   monitor   the   compliance   to   Technical   Standards   and Specifications  including  Safety  Standards  either  directly  or  by  accredited third 	party 	through 	separate 	regulations 	on 	third 	party 	conformity assessment.

(3) In case of any deviation or shortfall, in achieving the targets for implementing the specified standards, the entities shall be liable to face the following consequences, namely:-

(i) 	in case  of critical  activities  at Appendix-I,  the entity  shall  be given  a single  notice  by  the  Board  specifying  the  time  limit  to  remove  the specified shortcoming  and ensure compliance  and if the entity fails to comply   within   the   specified   time   limit,   immediate   suspension   or termination, as deemed appropriate, of authorization shall be done;

(ii) 	in  other  cases,  the  Board  may  issue  a  notice  to  defaulting   entity allowing it a reasonable time to remove the specified short coming and ensure compliance and in case the entity fails to comply within the specified   time  or  in  case  the  entity  defaults   on  more  than  three occasions,  its authorization  to lay,  built,  operate  or expand  the CGD network  shall be liable for suspension  or termination  apart from taking legal action under the provision of the Act and regulations thereunder.

8. 	Requirements under other statutes.

It shall  be necessary  to comply  with  all statutory  rules,  regulations  and Acts  in  force  as  applicable  and  requisite  approvals  shall  be  obtained from the relevant competent authorities for the CGD network.

9. 	Miscellaneous.

(1) These  standards  are  intended  to  ensure  uniform  application  of  design principles and to guide selection and application of materials and components.   Though   the   standard   primarily   focuses   on   safety   of employees,  public and facilities associated  with city or local natural gas distribution networks, it does not eliminate the need for a competent designer and good engineering judgment.

(2) If  any  dispute  arises  with  regards  to  the  interpretation  of  any  of  the provisions  of these  regulations,  the decision  of the Board  shall be final. Further,  the Board  may at any time effect  appropriate  modifications  in these regulations.

APPENDIX-I

LIST OF CRITICAL ACTIVITIES In CGD NETWORK

{See  regulation  7(3)  (i)}

| Sr. No. | Critical infrastructure/ activity/ processes | Time period for implementation | Implementation plan |
| --- | --- | --- | --- |
| 1 | Pressure reduction skid CGS (active / monitor combination) with a minimum 50% redundancy including slam shut valve for over pressure protection and creep relief valves. | 1 year | Modification of CGS skid |
| 2 | On line odorisation equipment designed to minimize fugitive emissions during loading, operation and maintenance. | 1 year | Automated odorisation systems to be used |
| 3 | Height of the vent shall be minimum 3 meters above working level | 6 months | Increase height of vent |
| 4 | Gas detectors shall be installed at critical locations | 1 year | Install gas detectors in the CGS and District Pressure Regulating Station. |
| 5 | Pressure reduction for DRS (active / monitor combination) skid with minimum 50% redundancy including two safety devices at least one of them shall be a slam shut valve for over pressure protection/under-pressure and inlet and outlet isolation valves. | 2 years | Modification/ replacement |
| 6 | Steel reinforced rubber hose conforming to IS 9573 Type IV | 6 months * | Replacement of all rubber hoses @ fifty thousand per year |
| 7 | Pipeline test record and joint radiography and cover in the form of pipe book | 3 months | Can be submitted in stages |
| 8 | HSSE Management System | 6 months | To be implemented |
| 9 | Emergency Response Plan, Disaster Management Plan and written emergency procedures. Also, provide for an Emergency Control Room, manned round the clock and equipped with effective communication system and emergency vehicles fitted with communication facilities, first aid equipment, fire extinguishers, gas detectors, repair kits and tools, maps, plans, material safety data sheets etc. at its disposal. | 6 months | To be implemented |

* c o mmencement  of i m plementati o n

Schedule  – I

(See  regulat i on  6)

Technical Standards and Specifications including Safety Standards

for

City or Local Natural Gas Distribution Network

Schedule – 1A		MATERIALS AND EQUIPMENT Schedule - 1B	WELDING

Schedule – 1C	PIPING SYSTEM COMPONENTS AND FABRICATION DETAILS

Schedule – 1D	DESIGN, INSTALLATION AND TESTING

Schedule – 1E	OPERATING AND MAINTENANCE PROCEDURES

Schedule – 1F	CORROSION CONTROL Schedule – 1G	MISCELLANEOUS

Schedule – 1A

MATERIALS AND EQUIPMENT

MATERIALS AND EQUIPMENT

All materials and equipment forming a permanent part of the any piping system constructed according to this standard shall be qualified for conditions in which it is to be used.

MATERIALS 	FOR 	USE 	IN 	COLD CLIMATES

Materials to be used in facilities exposed to low 	ground 	or 	low 	atmospheric temperatures or low operating temperatures shall have adequate impact properties to prevent brittle fracture at low temperatures.

MATERIAL SPECIFICATIONS

In addition  to standards  and specifications covered in ASME B 31.8, standards and specifications listed in Annexure-I shall also be acceptable  for manufacturing  of various piping components forming part of the CGD network.

Steel Pipe

Carbon  steel  used  in CGD  networks  shall meet following requirements:

Carbon Equivalent

For pipes having Carbon Content > 0.12% CE(IIW) =  C  + Mn + Cr+Mo+V + Ni+Cu

6	5	15

CE (iiw) value shall be ≤ 0.43%.

For pipes having Carbon Content ≤ 0.12%

CE(Pcm) =C + Si + Mn + Cu + Ni + Cr + Mo + V + 5B

30   20	20	60  20   15   10

CE (Pcm) value shall be ≤ 0.25%.

Notch Toughness

For carbon  steel pipes of size NPS 2 and above, notch toughness shall be specified.

Electric welded pipes used shall also meet additional 	requirements 	specified 	under Annexure-III of this standard.

Ductile Iron Pipe

Use of ductile iron pipe is not permitted for

CGD networks for transport of natural gas.

Plastic Pipe and Components

Thermoplastic  pipes, tubes and fittings are recommended 	for 	use 	in 	city 	gas distribution networks.

Polyethylene  (PE)  pipes  conforming  to  IS

14885 or ISO 4437, and PE fittings conforming to ISO 8085 Part 3 shall be acceptable.

Reprocessed material shall not be used. Colour of pipes used for gas service  shall

be yellow for PE 80 grade and Orange for

PE 100 grade.

PE  pipes   shall   be  permanently   marked (either impressed or embossed to a depth / height of 0.02 to 0.15 mm).

Pipes   and   tubing   for   above   ground service lines up to meter set assembly

Galvanized Iron (GI) pipes shall be used in above ground service lines up to consumer meter  or meter  control  valve.   The use of copper tubing shall only be after consumer meter  such  that  this  is  not  accessible  to third party. GI pipes and copper tubing shall conform to the requirements given in Annexure–IV   of  this  standard. 	Use  of

non-galvanised  pipes  should  be  restricted as far  as possible;  however,  in case  they are  used  they  shall  be  properly  protected and painted.

PE pipe shall not be used for above ground gas pipes.

Tubing / Hose pipe for connecting consumer 	meter 	set 	assembly 	and consumer appliance

The  connection  between  consumer  meter set assembly  and gas appliance  (provided by consumer) may be made by GI pipes or copper  tubing  meeting  requirements  given in Annexure–IV of this standard or steel reinforced rubber hose.

Steel reinforced  rubber hose shall conform to IS: 9573 Type IV.

EQUIPMENT SPECIFICATIONS

Equipment 	used 	  in 	CGD 		network manufactured 		to 	standards 	listed 	in

Annexure-II  of this  standard  shall  also  be acceptable.

CONDITIONS FOR REUSE OF PIPE Reuse of Ductile Iron Pipes

Reuse of ductile iron pipes is not permitted.

Reuse of Plastic Piping

Reuse of plastic pipes is permitted  subject to the following.

a. 	Its 	original 	and 	manufacturing specifications 	 are 	 known 	and documented.

b. 	It  meets   the   requirements   of   new pipes conforming  to its manufacturing specifications.

c. 	The pipe is free from visible defects.

d. 	It is installed and tested in accordance with requirements of this standard. All testing 	shall 	be 	 carried		out 		at recognized 	independent 		laboratory and 	records 	 of 	the 	same 	are maintained

10

Schedule – 1B

WELDING

GENERAL

These  requirements  apply  to steel  pipe and components only.

Notches  or  laminations  on  pipe  ends  are not  permitted   and  must  be  removed  by cutting   the  pipe   as   a  cylinder   and   re- beveling of pipe end prior to welding.

QUALIFICATION  OF PROCEDURES  AND WELDERS

Welding 	 procedures 	 and 	  welders 	for welding  of gas pipelines  shall  be qualified as 	per 	API		1104 	and 	shall 	include toughness	testing 	 requirements 	 as applicable for the line pipe.

Welding procedures and welders, for station piping shall be qualified as per ASME Boiler and  Pressure  Vessel  (BPV)  Code  Section IX or API 1104.

When welders qualified under API 1104 are employed 	for 	station 	piping, 	their qualification  shall  be based  on destructive mechanical testing as per API 1104.

INSPECTION OF WELDS

All Non Destructive Testing (NDT) including radiographic 		examination 	shall 		be performed 	in 		accordance 	 with 	the requirements  of  API  1104  except  that  no root crack shall be permitted.

Regardless of operating hoop stress as well as location class all carbon steel butt welds shall be 100% radiographed. In case radiography is not possible due to safety reasons,  weld shall be examined  by using ultra sonic techniques.

REPAIR OR REMOVAL OF DEFECTIVE WELDS

Welds having defects  shall be removed  or repaired in accordance with API 1104 or ASME BPV code Section IX as applicable. Welders employed for repairs shall be qualified in accordance with “Qualification of Procedures and Welders”.

Weld repair areas shall be subjected to additional  radiography  or ultrasonic  testing after repair.

11

Schedule – 1C

PIPING SYSTEM COMPONENTS AND FABRICATION DETAILS

PIPING SYSTEM COMPONENTS General

In addition  to standards  and specifications covered  under  ASME  B  31.8  for  various piping 	components, 	piping 	components manufactured  conforming to standards and specifications   listed  under  Annexure–I   of this standard shall also be acceptable.

Valves and Pressure Reducing Devices

Valves   body,   bonnet,   cover   and/or   end flanges components made of cast iron and / ductile iron (as per ASTM A 395) shall not be used in CGD networks.

Valves used in service lines of size NPS 2 and below shall conform to BS EN 331.

Flanges

Flanges made of cast iron, ductile iron and non-ferrous   materials   (brass   or   bronze) shall not be used in CGD networks.

Use of flanges  in natural gas transmission and   distribution   piping   is   not   permitted except  for  station  piping  e.g.  CGS,  DRS, MRS etc.

For   piping   class   150   or  above   all   the flanges shall be with raised face.

Bolting

All   stud   bolts   and   nuts   used   in   CGD networks shall be hot dipped galvanized as per ASTM A 153 or equivalent.

Fittings other than Valves and Flanges

Fittings  made  of cast iron and ductile  iron shall not be used in CGD networks.

All  plastic  fittings  used  in  CGD  networks must 	have 	been 	type 	tested 	by 	an internationally   recognized   testing   agency prior to their use.

Thermoplastic  / thermosetting  fittings  shall not be used in above ground piping system. Thermoplastic   fittings   conforming   to  ISO

8085 Part 3 shall be acceptable  and shall

meet following requirements:

a. 	Polyethylene 			resin 		used 		for manufacture of thermoplastic fittings shall 	be 	 virgin, 	cadmium 	free pigmented 	compound. 	Anti-oxidant and  UV  stabilizers  used  in  PE  resin shall not exceed 0.3 and 0.5 percent respectively. 		Reprocessed 	material shall not be used.

b. 	Grade  of PE compound  used for the

fittings should not be less than that of PE   pipes.   In   case   fittings   are   of different grade than that of pipes, compatibility  of  the  same  with  pipes shall be established prior to their use. However,   in  case   of  higher   grade fittings separate compatibility test shall not be required. Heating element shall not be exposed and all coils are embedded into the body of the fittings.

c. 	Colour  of  fittings  shall  be  yellow  or

black.

d. 	Electro-fusion  fittings  complying  with ISO 8085 Part 3 / EN- 1555 -3 shall be  used  for  all  sizes  of  PE  pipes. Fittings fabricated  from pipe shall not be 	used. 	Only 	injection 	moulded fittings are recommended.

e. 	For  fusion  fitting  upto  63  mm,  pipe

fixation device shall be an integral part

of the body of the fitting and for size above   63   mm   external   alignment clamp shall be used.

f. 	Each Electro Fusion fitting shall be bar

coded. 	Fusion 	fittings 	shall 	have permanent  fusion  indicator  or a data card   conforming   to   ISO-7810/ISO-

7811.

g. 	The fusion jointing shall be carried out as per  the  procedure  outlined  in the standard DVS 2202 or equivalent.

h. 	Carbon steel part of transition  fittings used for connecting PE system with Carbon  Steel  system  may  have  butt weld/plain/flanged ends.

Special Fittings

Mechanical  fittings  for making  hot taps on pipelines   and  mains  shall  not  be  used. Fittings  for  hot  taps  shall  be  welded  type (for steel pipelines  and mains)  and electro fusion type (for thermoplastic mains and service lines).

EXPANSION AND FLEXIBILITY Flexibility Requirements

When maximum gas temperature  expected during operation is below 65°C, thermal expansion    and   stresses   in   the   above ground steel piping shall be evaluated considering pipe temperature of 65°C.

Schedule – 1D

DESIGN, INSTALLATION AND TESTING

DESIGN INSTALLATION AND TESTING General Provisions

The 	selection    of 		design 	for 	city	   gas distribution  network  shall be based  on the gas 	 properties, 	required 	  flow 	rates, operating pressures and the environment.

CGD network Description

A typical CGD Network should comprise of one or more or all of the following:

i) Primary network: A medium Pressure Distribution System comprising of Pipelines, Gas Mains or Distribution Mains normally constructed using steel pipes and connects one or more Transmission Pipeline to respective CGS or one or more CGS to one or  more  DPRS.  The  maximum  velocity  in the  pipeline  network  should  be  limited  to

100  ft  /  sec  (30  m/sec)  immediately  after

pressure regulating instrument.

As far as practical, primary network should be fed through more than one city gate stations / sources of supply. The operating pressure shall be as defined under General Terms.

ii) 	Secondary  Network:  A  low  Pressure Distribution    System   comprising   of   Gas Mains 	or 	Distribution 	Mains 	usually constructed 	 using 	thermoplastic 	 piping (MDPE) and connects DPRS to various service regulators at commercial, industrial, and domestic consumers. The network shall be sized for maximum flow velocity of 100 ft

/ sec (30 m/sec).

iii) 	Tertiary  Network:  A service  Pressure Distribution System comprising of Service Lines, Service Regulators and customer/ consumer 	Meter 		Set 	Assemblies constructed 	 using 	a 		combination 	of

thermoplastic 	(MDPE) 	piping 	and 	GI/

copper tubing components.

[Note: For italicized terms used in description of above networks, definitions as per ASME B 31.8 shall apply]

iv) 	City   gate   station   (CGS):   typically comprising   of,   but   not   limited   to,   the following facilities:

- 	Filters

- 	Separators (if required).

- 	Metering facilities.

- 	Heater (if required)

- 	Pressure   reduction   skid   comprising active and  monitor combination with a minimum 	50% 	redundancy 	with stream 	discrimination 	arrangement, including slam shut valve for over and under   pressure protection  and creep relief valves (stream redundancy shall not be less than 2+1).

- 	Online 	odorization 	equipment

designed 	to 	minimize 	fugitive emissions   during   loading,   operation and maintenance.

v) 	Distribution 	Pressure 	Regulating Station 	or 	District 	Regulating 	  Station (DPRS): 		Located 	  at		various 	demand centers for domestic / commercial users typically consists of:

- 	Gas filter

- 	Heater (if required)

- 	Pressure   reduction   skid   comprising active   and monitor  combination  with minimum 	50% 	redundancy 	with stream 	discrimination 	arrangement, including slam shut valve for over and under 	pressure 		protection 	with additional feature of under pressure protection 		if 		   required(stream redundancy   shall  not  be  less  than

2+1).

- 	Inlet and outlet isolation valves.

vi) 	Individual Pressure Regulating Station (IPRS): Located at the premises of an individual customer and having facilities similar to DPRS however, monitor regulator may or may not be provided. Metering facilities  may  or  may  not  be  part  of  this station.

vii) 	Service Regulators: Usually located at customer premises for maintaining supply pressure and designed to maintain safe condition even in the event of rupture in the regulator downstream section.

Network Design Requirements

The design of CGD Networks and its components shall be such that it ensures:

- 	Supply of gas at constant volume into a system, which fluctuates in pressure between pre-determined upper and lower limits in the distribution network, or

- 	Supply of gas at a constant pressure at consumer end, and

- 	The design should recognize the need for safe guard against  malfunction  of any equipment  and provide  sufficient redundancy  to ensure that the supply is secured against such malfunctions.

Facilities   forming   part  of  CGD  networks shall be designed considering:

- 	Range  of  flow  rates  and  pressures required in various sections of the network

- 	Quality of gas, including cleanliness in respect 	of 	both 	solid 	and 	liquid particles.

- 	Metering requirements.

- 	Noise control and

- 	Corrosion Protection

Necessary calculations  shall be carried out to verify  structural  integrity  and stability  of the pipeline for the combined effect of pressure, temperature, bending, soil/pipe interaction, 	external 	loads 	and 	other environmental parameters as applicable, during all phases of work from installation to operation.  Such  calculations  shall  include, but not limited to, the following:

- 	Buoyancy   control   and   stability   of pipeline 	in 	areas 	subjected 	to flooding / submergence,

- 	River   crossing   to   be   installed   by trench less techniques, wherever soil data 	is 	favorable 	for 	such installations,

- 	Damage  potential  for  steel  pipeline from 	hazards 	associated 	with earthquake, if applicable.

Layout of Station Facilities

The following aspects are to be considered in   deciding   layout   of   facilities   at  CGS, DPRS, IPRS, etc.

i. 	Type and size of equipment. ii. 	P&IDs

iii. 	Utility requirement.

iv. 	Venting wherever required.

v. 	Operation 	and 	Maintenance philosophy.

(a) 	City Gate Station

As  far  as  possible  the  city  gate  station (CGS) shall be installed at the periphery of populated   area.  The  entity  should  make best endeavor to have more than one CGS for supply security.

Inter distance between various facilities required at CGS shall be as per Table – 1.

Notes :

1.	All distances are in meters. All distances shall be measured between the nearest points on the perimeter of each facility.

2.	For all the distance from the compound wall, the distance mentioned in this table and the local byelaws, whichever is  higher  is  to  be considered.

#	As	per	State	Electricity	Board recommendations.

Properly laid out roads around various facilities 	shall 	be 		provided 	within 	the installation 	area 	for 	smooth 		vehicular access.

Facility shall be provided with proper boundary  wall / fencing with gate(s) in line with 	MHA 	(Ministry 	of 	Home 	Affairs) guidelines.

Buried  piping  inside  the  CGS  area  shall have a minimum  depth of cover of 1.2 m. Where buried pipes come out of the ground, the underground coating on the pipe will continue  for  a  length  of  at  least  300  mm above ground.

Platforms and crossovers shall be provided for  ease  of operation  and  maintenance  of equipment and piping where required.

Provision   should   be   made   for   venting, purging  and  draining  all  sections  of  pipe work  and  equipment  that may  have  to be isolated 	during 	construction 	or maintenance.

All vents shall be routed to a safe area and in a manner  that gas vented  out is blown away  from  the  nearest  building.  Height  of vent  shall  be  minimum  three  (3)  meters above working level. Distance between vent and boundary wall / fence shall be minimum five (5) meters.

Gas detectors shall be installed at strategic locations 	covering 	to 	detect 	any 	gas leakage.

In case  fired  gas heaters  are  installed  for heating  of gas,  all other  facilities  handling gas should be located down wind from heaters.

(b) 	Distribution 	Pressure 	Regulating Station (DPRS) and Individual Pressure Regulating Station (IPRS)

DPRS   facilities   can   be   located   above ground or below ground.

In case DPRS is located below ground, the facilities shall either be inside a enclosed chamber with a provisions for entry of authorized 	personnel 	or 	be 	a 	buried hermetically sealed module type with proper cathodic protection.

For below ground installations, the vent line shall be terminated at a minimum height of three (3) meters above the ground level.

IPRS   shall   normally   be   located   above ground.

DPRS/IPRS installed above ground shall be provided with proper security fencing as per requirement 	of 	local 	authorities. 	The distance between fencing and the wall of nearest building / structure shall not be less than two (2) meters.

[NOTES:

i.	The  consumer,  shall  be  responsible  for ensuring the separation distances for customer owned IPRS

ii.	Customer	shall		ensure		that	IPRS installation		has	been	independently approved by certified third party agency before the entity supplies the gas.

iii.	The consumer shall ensure recertification once in 3 years.

Requirements  for  Electrical   Installations in CGD Network

All   electrical    equipment   /   installations shall meet following  requirements:

- 	Electrical 	area 	classification	of Installation, as basis  for selection  of Electrical  Equipment, shall follow IS-

5572.

- 	The 	specification	of 	Electrical equipments shall  be in line with IS -

5571, 	“Guide 	for 	selection 	of Electrical   Equipment for  Hazardous Area”.

- 	Fire 	protection	in 	Electrical installations shall be provided  as per requirements 	specified 	 in 	this standard.

- 	All   electrical    equipment,  systems, structures and fencing,  etc. shall  be suitably  earthed  in accordance with IS  3043.  The  earthing  system  shall have an earthing network grid with required  number  of electrodes. All Electrical 	equipment 	operating above   250   volts   shall   have   two separate  and distinct  connections to earth  grids.    Separate  earthing  grid shall be provided  for instrument and electrical  power.

- 	Lightening	protection 	shall 	be provided  as per the requirements of IS:2309.   Self  conducting structures having  metal  thickness of more than

4.8mm   may   not   require   lightning

protection with  aerial  rod  and  down conductors.	They   shall,   however, be 	connected	to 	the 	earthing system,  at least, at two points  at the base.

Instrument and Control  System

Instrumentation  and   control   system   for the CGD  networks, shall  in general  meet the  requirement of  API  Standards: API- RP-551,   552,   553,   554,   555   and   556 "Manual 	on 	Installation	of 	Refinery Instruments and  Control  Systems” to the extent applicable.

Buildings 	Intended 	for 	Human Occupancy and Location Classes for Design and Construction

For the purpose  of determining  number  of buildings 	for 	human 	occupancy 	and Location Classes, 1 - mile distance shall be replaced by 1600 m and fractions thereof.

In  case  of  cluster  of  buildings,  Location Class 2 or Location Class 3 may be terminated a distance of 200 m from the nearest building in the cluster.

Location Class 2 or 3 shall be terminated at least  200  m  from  the  end  dwelling   i.e.

dwelling  located  at  the  boundary  of  the

Location Class 2 or 3 as the case may be.

When   presence   of   multi-story   buildings alone   result   in   Location   Class   4,   the Location  Class  4  ends  200  m  from  the nearest   building   with  4  or  more  stories above ground.

This standard does not allow Design of pipelines and piping as per Location Class

1, Location Class 2 and Location class 3.

Location  Class  1,  2  and  3  shall  be  used only 	for 	re-certification 	of 	existing Installations 	 and 	facilities, 	which 	were laid/built/constructed before the date of notification of these regulations.

STEEL PIPE

Additional Requirement for Nominal Wall

Thickness

Consideration shall also be given to loading due to following while selecting nominal wall thickness t as per ASME B 31.8 as appropriate:

- 	Overburden loads

- 	Dynamic and seismic loads

- 	Cyclic and vibratory loads

- 	Internal pressure fluctuations

- 	Geo-technical  loads  (including  slides, differential settlement of piping, loss of support, and thermal effect of the pipeline on soil properties).

In any case minimum thickness of pipe permitted as per this standard shall not be less than 6.4mm, irrespective  of the grade of the pipe material.

In all existing cases where thickness of pipe is less than 6.4 mm, Quantitative Risk Assessment  shall  be  carried  out  and  the risk  level  shall  be reduced  to ALARP  (As low as reasonably possible).

Design Factors F and Location Classes

Design   factor   corresponding   to  Location

Class 4 shall only be used.

All exceptions to basic design factors to be used  in  design  formula  shall  be  as  per Table – 2 of this standard.

Pipelines or Mains on Bridges

Pipeline   on  bridges   should   be  avoided. Under 	unavoidable 	conditions, 	pipeline installed  on railroad,  vehicular,  pedestrian, or other pipeline bridges, a design factor of

0.40 shall be used for Location Class 4.

In  cities  where  crossing  the  river  through HDD   crossing   is   not   possible,   pipeline laying on river bridges is permitted.

Metering Facilities

Upstream dry gas filter(s) shall be installed when rotary or turbine meters are used.

Pressure / Flow Control Facilities

(a) 	Protection  against  over  pressure  of pipeline  or mains  downstream  of city gate station (CGS) shall be provided as follows:

(1) 	The   provision   of   Active   /   Monitor Regulator  System (i.e. monitor regulator  in series  with  a controlling  (active)  regulator) shall be the principal method of controlling pressure.

[Note : To avoid problems associated with a regulator being at rest for prolonged periods it is recommended that  the  monitor  regulator  is  so impulsed that it can also operate as a first stage regulator.]

(2) 	Adequately 	sized 		pressure 	relief valve(s) could be used for overpressure protection 	downstream 	  of 	controlling regulator(s) 	 provided 	Quantitative 	 Risk Assessment is made for environmental hazards  (fire / explosions)  associated  with large release of gas volume of gas release and the risks are found within acceptable level.

Pressure relief valve(s) should be carefully sized to meet their required duty and to minimize  the volume  of gas released.  The speed of relief valve opening should be adequate and they should re-seat cleanly when normal pressures are restored. The relief valve should be installed and provided

with  test  connections  in  the  impulse  pipe work in such a way as to enable them to be set up and tested in-situ.

(3) 	Over   pressure   shut-off   valve(s)   or Slam-Shut 		Valve(s) 	upstream 	 of 	the controlling 	  regulators 	 are	preferred 		as overpressure protective devices instead of pressure 	relief 	valves. 	Being 	ultimate overpressure protection for the pipeline system, it is essential that the Slam-Shut valves  are fast closing,  highly reliable  and secure valve.

(b) 	The  isolation   valve   of  the  sensing lines of regulators and slam shut valves should have provision for locking in open position.

(c) 	Additionally 	suitable 	gas 	heaters upstream of regulators / control valves/ pressure 	reduction 	system		should 	be provided in case after pressure let down operating conditions would result in low temperatures beyond design conditions of downstream facilities.

(d) 	Sound pressure levels shall be limited to the values  prescribed  by Environmental Authorities  but  in  no  case  it  shall  exceed

110dbA.

| Table 2 - Design Factors for Steel Pipe Construction |
| --- |
| Facility | Location Class |
|  | 1* | 2* | 3* | 4 |
| Pipelines | 0.72 | 0.60 | 0.50 | 0.40 |
| Crossings of roads, without casing: (a) Private roads (a) Unimproved public roads (b) Roads, highways, or public streets, with hard surface | 0.72 0.60 0.60 | 0.60 0.60 0.50 | 0..50 0.50 0.50 | 0.40 0.40 0.40 |
| Crossings of roads, with casing: (a) Private roads (b) Unimproved public roads (c) Roads, highways, or public streets, with hard surface and Railway crossings | 0.72 0.72 0.72 | 0.60 0.60 0.60 | 0.50 0.50 0.50 | 0.40 0.40 0.40 |
| Pipelines on bridges | 0.60 | 0.60 | 0.50 | 0.40 |
| Parallel Encroachment of pipeline on roads and railways (a) Private roads (b) Unimproved public roads (c) Roads, highways, or public streets, with hard surface and Railway crossings | 0.72 0.72 0.60 | 0.60 0.60 0.60 | 0.50 0.50 0.50 | 0.40 0.40 0.40 |
| Pipeline on bridges | 0.50 | 0.50 | 0.50 | 0.40 |
| River Crossing- open cut [1] | 0.72 | 0.60 | 0.50 | 0.40 |
| Horizontal Direction Drilling (HDD) [1] | 0.72 | 0.60 | 0.50 | 0.40 |
| Compressor station piping | 0.50 | 0.50 | 0.50 | 0.40 |
| Fabricated assemblies (scraper traps, SV stations, pressure/flow control and metering facilities, etc.) [2] | 0.60 | 0.60 | 0.50 | 0.40 |
| Near concentration of people in Location Classes 1 and 2 [3] | 0.50 | 0.50 | 0.50 | 0.40 |

Notes:

1	Higher thickness may be used if required to control stresses or stability during installation and operation.

2	Thicker pipe in Location Class 1 is required throughout the assembly and for a distance equal to lesser of 5 diameters or 10 ft in each direction beyond the last fitting.

3	Near concentration in Location Class 1 and 2 means places of public assembly (school, temple, church, hospital, club, markets places etc.) used by 20 or more people frequently.

*  Location Class 1, 2 & 3 shall be used for the purpose of recertification of Existing

Installations only.

(e) 	Gas velocities in piping up to 20 m/sec before filter and 40 m/sec (120 ft / sec) after filter, at peak flow conditions, may be permitted  provided  care is taken to ensure that  allowable  sound  pressure  values  are not exceeded and materials selected are suitable to prevent erosion at such high velocities.

However,  the  gas  velocity  shall  not  cross the recommended velocity given by the Original Equipment Manufacturer for the equipments used in the PRI.

(f) 	Gas   filtration   facilities   with 	100% redundancy shall be provided to avoid damage 	to 	instrumentation 	and 	 other facilities.

(g) 	Immediately downstream of regulators or control valves, use of conical reducers is recommended.

(h) 	In order to prevent over pressurization of piping downstream of regulators / control valves, 	creep 	relief 	valve 	should 	be provided, if required.

(i) 	For   isolation   of   the   CGS   during emergency, 	quick 	 closing 	  valve 	(with remote 	operation 	facility 	in 	case 	of unmanned  station) shall be installed at the inlet of CGS.

Protection  of pipelines  and  mains  from hazards

When steel pipelines or mains are installed in areas that are normally under water, anti- buoyancy measures adopted shall be such that specific  gravity of resulting  installation is 1.10 or more.

Pipelines  and  mains  installed  on  bridges and other locations where they are exposed to  accidental   damages   due  to  vehicular traffic,  suitable  barricades  /  crash  guards shall be installed for their protection.

The pipeline  in close proximity  to unstable structures, 	landfill 	sites 	or 	where construction    could   lead   to   damage   to pipeline, should be avoided.

Pipelines  and mains  installed  in the areas

normally under water or subject to flooding (i.e. lakes,  bays, or swamps  etc.) shall be provided 	 with 	 addition 	anti-buoyancy measures such as concrete weight coating, geo-textile bags filled with graded stones or anchorages, 	etc. 	to 	prevent 	floatation. Minimum specific gravity of installation shall be 	1.2 	after 	providing 	anti-buoyancy measures.

Cover, 	Clearance 	and 	Casing Requirements  for Buried Steel Pipelines and Mains

Minimum depth of cover for buried steel pipelines shall be as per the table given below;

| Table – 3 : Minimum Cover Requirements for Steel Pipelines |
| --- |
| Location | Min. Cover[1] (m) |
| Normal / rocky terrain | 1. 0 |
| Minor river / unlined canal / nala crossings, tidal areas and other watercourses[2] | 1. 5 |
| [2] Major river crossings | 2.5 |
| Rivers with rocky bed | 1.5 |
| Lined canals / drains / nalas etc. | 1.5 |
| Drainage ditches at roadways and railroads | 1. 0 |
| Rocky Areas | 1. 0 |
| Cased / ] uncased road crossings[3 | 1. 2 |
| Cased railroad crossings[3] | 1. 7 |

NOTES:

1. 	Cover  shall  be  measured  from  the  top  of coated pipe to the top of the undisturbed surface of soil or the top of graded working strip, whichever  is lower. The fill material in the working strip shall not be considered  in the depth of cover

2. 	For  river  /  watercourses  that  are  prone  to scour  and / or erosion,  the specified  cover shall be measured from the expected lowest bed profile after scouring / erosion.   Where scour level cannot be established,  an additional cover of minimum 1 meter shall be provided   from   the   existing   bed   of   the river/water course.

3 	The cover shall be measured from the top of road or top of rail, as the case may be.

Whenever the above provisions of cover cannot be provided due to site constraints, additional protection in form of casing/ concreting etc. shall be provided.

Clearance  between  Pipelines  or  Mains and other underground structures

(a) 	When a buried steel pipeline  or main has to cross any existing underground pipeline,   cable,   drain  or  other  services, the pipeline  shall be laid at least 300 mm below from such services.

(b) 	When   laid  parallel   to  any  existing underground cable, drain or other utilities, the  pipeline  or  main  shall  be  laid  with  a clear distance of at least 300 mm from existing  utility.

(c) 	As   far   as   practical,    a   minimum separation of  three  (3)  meter  should  be maintained between  the  steel  pipeline  or main and footing of transmission tower.

(d) 	A   clearance   sufficiently   large    to avoid  electrical   fault  current  interference shall  be maintained between  the pipeline and the grounding facilities  of electrical transmission lines.

(e) 	Clear   distance   between   new  steel pipeline 	or 	main 		running 		parallel 	to existing pipeline should be minimum 5.0 meters 	 when 		heavy 	conventional construction equipment is expected  to be utilized.   This  distance   may  be  reduced, after  careful  assessment of  construction methodologies,	to 	 three 	(3) 	meters, provided it does not result in unsafe conditions during construction. Existing pipeline  should  be clearly  marked  on the ground during construction. Bi-language (local    language    and   Hindi    /   English) caution signs should be installed while working  in such areas.

(f) 	While   laying   more   than   one   new hydrocarbon  pipelines   or  mains   in  the same 	trench, 	clear 	separation 	of minimum 500 mm shall be maintained between  adjacent  pipelines.

(g) 	No steel  pipeline  or main  should  be located within three (3) meters of any habitable 	dwelling 	or 	any 	industrial

building  unless  it is provided  with at least

300 	mm 	of 	cover 	over 	and 	above minimum  cover specified  under  Table  – 3 above   or   special    protective  measures such as concrete slab, steel casing are provided.

Casing  Requirements under  Railroads, Highways, Roads or Streets

Steel   casing   at  road/railway  crossings, when 	provided 	to 		meet 	statutory requirements, 	shall 	be 	designed 	in accordance with  API  1102.  Casing  pipe diameter  shall be minimum  two pipe sizes bigger  than  carrier  pipe.  In  case  of  PE, the casing  can  be RCC  pipe  of min  NP3 class.

Bends,   Elbows   and   Miters   in   Steel

Pipelines  and Mains

Miters bends and wrinkle bends are not permitted in pipelines  and  mains  used  in CGD   networks   regardless  of  operating hoop stress.

Cold  field  bend  radius  for  pipes  of  size NPS  20 and  larger  shall  be minimum  40 times the pipe diameter.

As  far  as  possible   use  of  short  radius elbows should be avoided.

Hot Taps

Split tees designed to fully encircle the pipe shall be used for making hot taps. The split Tees shall be designed considering a minimum design factor F = 0.40.

However,  in case of Hot taps of size upto

1/4th    of   the   nominal   bore   of   the   main pipeline,  use  of  weldolets  is  permitted  in

place of split tees.

Full bore ball valve shall be used when making branch connections using hot taps.

Recommendations as per API RP 2201 - Recommended 	Practice 	for 	Safe 	Hot Tapping Practices in the Petroleum and Petrochemicals Industry shall be followed while carrying out hot tapping works.

Where it is not possible to maintain the clearances, cover,  vent locations  etc. mentioned  in   this   standard,  the   entity shall 	carryout 	special 	design 	and construction		methodologies	through experienced 	personnel/consultant 	and seek clearance from the Board.

Testing after Construction

General Provisions

Proper  communication facilities  shall  also be arranged  for during testing.

Testing  equipments / instruments shall be properly   inspected and  shall  have  valid calibration  certificates  before   they   are used for testing.

Test 	Required 	to 	Prove 	Strength 	of Pipelines and Mains to operate at Hoop Stresses of 30% or more of Specified Minimum Yield Strength of Pipe

All buried steel pipelines and mains shall be pressure   tested   after   installation    using water as a test medium. Minimum test pressure   shall   be   equal   to   1.4   times Maximum Allowable Operating Pressure.

Test   procedure   as   per   ASME   B   31.8

Appendix N “Recommended Practice for Hydrostatic  Testing  of  Pipelines  in  Place” shall be followed.

Hold-up  time for the pressure  testing shall be minimum 24 hours for underground  and four hour aboveground pipeline.

Safety During Tests

Relevant 	Warning 	Signs 	shall 	be displayed at the test area

The test area  shall  be properly  cordoned to prevent  any accidents.

A proper Emergency Response Plan shall be   in   place    and   emergency   contact numbers of relevant agencies should be visible.

Commissioning of Facilities

Appropriate	Work 	Permit 	should 	be issued based on the kind of activity.

Fire 	fighting 	equipments	should 	be available  during commissioning.

Proper   communication  facilities    should also be arranged  for.

A proper  Emergency Response Plan should 	be 	in 	place 	and 	emergency contact numbers  of relevant  agencies should be available.

OTHER  MATERIALS

Ductile 	Iron 	Piping 	System

Requirements

Use of ductile iron piping is not permitted for

CGD networks as per this standard.

Design of Plastic Piping

Plastic  pipe shall not be used for Pipeline and 	Distribution 	Mains 	operating 	at pressure in excess of 100 psig.

Use  of  thermosetting  plastic  piping  is  not permitted as per this standard.

Plastic Pipe and Tubing Design Formula

Nominal wall thickness of plastic pipe shall be calculated as per following formula:

P = 2S * (t / (D-t)) * 0.32

Where

D   = 	Specified outside diameter in mm

P 	= 	Design pressure in psig

t 	= 	Nominal wall thickness in mm

S 	= 	Long  term  hydrostatic   strength   in barg 	(psig) 	determined 		in accordance 	with 	 applicable 	pipe specification at temperature equal to

73°F, 100°F or 120°F.

Thermoplastic Design Limitations

The design pressure  shall not exceed  100 psig (7 bar).

Thermoplastic pipe, tubing and fittings shall not be used where operating temperature of the materials will be:

1) 	Below 32°F(0 degree centigrade) or

2) 	Above  120°F  (50 degree  centigrade) or temperature at which long term hydrostatic strength used in design formula  in  para  842.31  of  ASME  B

31.8   is   determined,   (whichever   is lower).

Minimum  thickness  shall  not  be  less  than

2.3 mm.

Pipe wall thickness  selected  shall be such that it corresponds  to Standard  Dimension Ratio  indicated  in Table  – 4 below.  Pipes with non standard SDR should not be used.

Design Pressure of Plastic Fitting

All fittings used shall be electro fusion type. Other types of fittings are not permitted. All PE fittings shall conform to ISO 8085 –Part

3. The wall thickness of the fittings shall be

more or equal to the wall thickness  of the pipe jointed.

Protection from Hazards

In addition to requirements  specified under Para   titled   Protection   of   Pipelines   and Mains   from   Hazards   in   this   standard, following additional requirements shall be complied with.

The relative  position  of CGD  network  with respect  to other  underground  utilities  shall be as given in Figure 1:

Where open cut techniques are used, a warning tape of Yellow colour shall be laid

200 mm above the pipe.

| Table 4 - Wall Thickness and Standard Dimension Ratio for Thermoplastic pipes |
| --- |
| Nominal Outside Diameter in mm | Minimum wall thickness in mm for Standard Dimension Ratio, SDR |
| D | 17.6 | 13.6 | 11 | 9 |
| 16 | 2.3 | 2.3 | 2.3 | 2.3 |
| 20 | 2.3 | 2.3 | 2.3 | 2.3 |
| 25 | 2.3 | 2.3 | 3.0 | 3.0 |
| 32 | 2.3 | 2.3 | 3.0 | 3.6 |
| 40 | 2.3 | 3.0 | 3.7 | 4.5 |
| 50 | 2.9 | 3.7 | 4.6 | 5.6 |
| 63 | 3.6 | 4.7 | 5.8 | 7.1 |
| 75 | 4.3 | 5.5 | 6.8 | 8.4 |
| 90 | 5.2 | 6.6 | 8.2 | 10.1 |
| 110 | 6.3 | 8.1 | 10.0 | 12.3 |
| 125 | 7.1 | 9.2 | 11.4 | 14.0 |
| 140 | 8.0 | 10.3 | 12.7 | 15.7 |
| 160 | 9.1 | 11.8 | 14.6 | 17.9 |
| 180 | 10.3 | 13.3 | 16.4 | 20.1 |
| 200 | 11.4 | 14.7 | 18.2 | 22.4 |

Road Berm / Footpath

1	2	3

4

5	7

6

1 / 2 - Elec. Cable (Low Voltage)

3 Telecom Cable

4 Elec. Cable (High Voltage)

5 Gas Pipeline

6 Water Pipeline / sewage line

7 Other hydrocarbon product pipelines

Figure  1 – Relative Position of Gas

Pipeline and Distribution Mains

Figure 2 (a) - Concrete Slab

Figure 2 (b) - Concrete Slab with supports

When 	insisted 	by 	the 	authorities 	at identified   locations,   a   layer   of   brick   / concrete  or  impact  resistant  tape  may  be laid over pipeline as a protection against excavating machinery as indicated in the Figure – 2 (a) or (b).

Plastic   Pipe   and   Tubing   Joints   and

Connections

General Provisions

Threaded joints in plastic pipe are not permitted.

Plastic   piping   joints   shall   be   made   by Electro Fusion fittings only. Fusion fittings shall have inbuilt positioning provision upto

60 mm and beyond external clamp system.

Jointing of plastic piping by butt fusion method, solvent cement method, adhesive method, heat fusion method or by means of compression couplings or flanges is not permitted. Recommendations of the fitting manufacturer   shall   be   followed   in   this regard.

All electro fusion fittings shall be bar coded and the control unit shall be equipped with bar code  reader  to directly  transfer  fusion data to control unit. Bar coding shall be long lasting even when the joint is buried in corrosive soil, alternatively each fitting shall have a data card which can be read by the computer 	and 	thereafter 	the 	card 	is positioned with the joint.

Installation of Plastic Piping

Installation Provision

m	Use of thermoplastic piping in above ground piping is not permitted  unless the piping is completely protected against deterioration (e.g. 	high 	temperature, 	ultra 	violate degradation) by corrosion protected metallic or reinforced  concrete or Glass Reinforced Plastic (GRP) enclosure.

Direct Burial

Directly   buried   thermoplastic   pipe   shall have a minimum thickness of 2.3mm.

Trench width shall be at least 300 mm.

The bed of the trench shall be free of sharp objects,  stones  etc.  In rocky  areas  trench shall be padded with soft soil or sand to minimum depth of 150 mm below the pipe.

Bends and Branches

Branch connections  shall be made only by socket type electro fusion tees or electro fused Saddle connections.

Hot Taps

Use  of  special  saddle  or  split  tee  type electro fusion fittings for hot tapping is permitted.

Testing Plastic Piping after Construction

General Provisions

Testing  equipments  / instruments  shall  be properly inspected and shall have valid calibration certificates before they are used for testing.

Proper communication facilities shall be available during testing.

Test Requirements

Thermoplastic  piping shall not be tested at material   temperature    above   120°F   (50 degree centigrade).

Test medium shall be air or nitrogen for test pressure up to 100 psig. For test pressure higher  than 100 psig, water shall be used as test medium.

Test duration shall be minimum 24 hours for plastic  distribution  mains  of length  greater than 1 km and minimum 4 hours for length shorter than 1 km.

In case water is used as test medium, test duration  shall start after  achieving  thermal stabilization.

Suitable  relief valve set at 5% higher than test  pressure   shall  be  fitted  at  the  test heads to avoid over pressurization during testing.

Test Requirements for DPRS  and IPRS Piping

DPRS and IPRS piping shall be subjected to strength test and leak test, before commissioning, as given in table-5 below:

| Table 5 – Testing Requirements for DPRS and IPRS Piping |
| --- |
| Design Pressure | Min. Test Pressure | Test medium | Min. Test Duration |
| Up to 138 mbarg (2 psig) | 3.45 barg (50 psig) | Air | 2 hours |
| From 138 mbarg to 4.14 barg (2 to 60 psig) | 1.5 times Design Pressure | Air | 2 hours |
| Above 4.14 barg (60 psig) | 1.5 times Design Pressure | water | 2 hours |

Acceptance criteria  shall  be  no  pressure loss after accounting for temperature variation.

Safety During Testing

Relevant Warning Signs shall be displayed along the test section.

The test area should be properly cordoned to prevent any accidents.

A proper  Emergency  Response  Plan  shall be 	in 	place 	and 	emergency 	contact numbers of relevant agencies should be available.

CONTROL 	AND 	LIMITING 	OF 	GAS PRESSURE

Control and Limiting of Gas Pressure in High  Pressure  Steel,  Ductile  iron,  Cast Iron or Plastic Distribution system

Use of automatic shut-off device (slam shut valves) as a means of accidental over- pressure 	of 	high 	pressure 	distribution system   is  preferred   over  pressure   relief

valves   or  weight-loaded   relief   valves   or spring loaded diaphragm type relief valve.

DPRS/IPRS   shall   normally   be   equipped with minimum  two safety devices.  At least one of them shall be a slam shut valve operating on over pressure for those installations whose inlet operating pressure is more than 60 psig.

To 	prevent 	over 	pressurization 	of downstream  system  during  periods  of low flow, creep relief valve can be used. If a monitor regulator is installed in the system, it  shall  be  such  that  it  is  the  first  acting device in the pressure safety system.

Control and Limiting of Gas Pressure in low Pressure Distribution Systems

A 	combined 	Over 	Pressure 	Shut-Off (OPSO) regulator with built-in creep relief is also   acceptable   device   for   control   and limiting of gas pressure in low pressure distribution system.

Control and limiting of pressure of gas delivered  to  domestic,  small  commercial, and small industrial consumers from high – pressure distribution system.

Service regulator with a built-in Under Pressure Shut-Off (UPSO) regulator is also acceptable device for control and limiting of gas pressure to consumer.

VALVES

As far as practical, the valves in the distribution mains should be installed below ground   with   the   valve   operating   device readily  accessible.  A  stem  extension  may be used to elevate the valve operator above ground 	provided 	it 	does 	not 	cause obstruction to traffic and / or pedestrians. In such cases, sealant / lubrication points and vent   pipe   work   shall   also   be  extended above ground for ease of operation.

Valves of size 4 inches and above shall be fitted with double block and bleed facility.

Spacing   between   valves   on   distribution mains, whether for operating or emergency purpose shall be decided as follows:

(a) 	High Pressure Distribution System:

Based 	on 	operation 	and 	maintenance flexibility requirements, valves may be provided on:

- 	Either side of water body crossings.

- 	Strategic 	take-off 	points 	including future developments.

Based on risk associated with emergency situations requiring speedy isolation and resulting number and type of customers affected by such emergencies etc.

- 	In 	steel 	distribution 	mains 	valve spacing should normally  not be more than 3 km,

- 	In   plastic   distribution   mains   valve spacing should normally  not be more than 1 km.

The above spacing, however, may be increased or decreased based on risk assessment and to allow location of valve at an easily accessible location.

(b) 	Low Pressure Distribution System:

Valves  in low pressure  distribution  system may be provided at locations requiring isolation for ease of maintenance in addition to those required as per following Para.

Distribution System Valves

A valve shall be installed  on the inlet and outlet piping of each regulator station controlling flow or pressure of gas in distribution  system.  The  distance  between the valve and regulator(s) shall be adequate to allow operation of the valve during emergency  (such as large leakage or fire). These   valves   should   be   located   in   a manner   that   they   are   easily   accessible during emergency.

VAULTS Accessibility

In case part of Vault or Pit extends  above ground (e.g. to avoid water flooding in low lying areas that cannot be avoided), then, it shall   be   located   such   that   it   causes minimum  interference   /  hindrance  to  the traffic / pedestrians.

CUSTOMERS’ 	METERS 	AND REGULATORS

Location 	for 	Customers’ 	Meter 	and

Regulator Installations

Customer meter shall preferably be located on the wall outside the kitchen, however, when customers’ meters and regulators are located  inside  the  building,  it  should  be located in a well ventilated area.

GAS SERVICE LINES

General Provisions Applicable to Steel, Copper and Plastic Service Lines

Service lines shall be sized for a maximum flow velocity of 15 m / sec.

Installation of Service Lines

All plastic pipe and fittings shall be laid underground and shall not be exposed.

The buried  service  lines shall be provided with a minimum  cover of 1.0 m.  Where  it is impractical to provide  1.0 m cover  due to 	physical 	constraints,	additional protective  measures  such   as   concrete slabs   or  high  impact   resistance  plastic sheets  shall  be installed  at least  300 mm above   the  service   line.  In  no  case  the depth of cover shall be less than 600mm.

For transition  from plastic  pipe to GI pipe, transition   fittings   shall  be  used.   Plastic part  of  transition   fitting  protruding above ground  shall  be  protected by encasing  it with concrete  guard.

In case carbon  steel section  beyond transition   fitting  is  below  ground,  it  shall be 	protected 	against 	corrosion 	by

minimum   400  micron  thick  2  pack  high build epoxy coating.

Above ground service piping shall be Galvanized  Iron or copper  or carbon  steel protected by anti corrosive coating.

Wherever the service line riser is installed in confined 	spaces 	like 	basements, 	only welded   risers   shall   be   used.   The   gap between riser and wall shall be minimum 25 mm to and shall be supported at every 2 m. Ventilators shall be provided in confined space.

Type of Valves Suitable for Service Line

Valves

Soft seated valves in service  lines are not permitted.

Steel Service Lines

Design of Steel Service Lines

All underground  steel service lines shall be joined by welding using qualified welding procedure and welders.

Installation   of   Service   Lines   into   or

Under Building

Use of sleeve for laying steel pipe through wall, or under outer wall foundations of building or under the building is not recommended.    Such   underground    lines shall be protected against corrosion by minimum 400 micron thick 2 pack high build epoxy coating.

Ductile Iron Service Lines

Use of ductile iron service lines is not permitted.

Plastic Service Lines

Design of Plastic Service Lines

Only electro fusion fittings shall be used in plastic service piping including pipe to pipe joints.

Installation of Plastic Service Lines

Installation  of plastic pipe above ground is not recommended.   In case any section of plastic pipe extends  above ground,  it shall be   completely    encased   in   a   concrete casing.   Use   of   flexible   conduit   is   not permitted.

Installation  of Plastic Service Lines into or Under Buildings

Installation  of plastic service lines under or inside  the building  is not permitted  as per this standard.

Service 	Line 	Connections 	to 	Mains Service 	Lines 	  Connections 		to 		Steel Mains

Service line connection to steel mains shall be as follows:

- 	In 	case 	of 	plastic 		service 	line, connection to underground steel main shall be by use of transition  fitting in plastic 	piping 	  with 	steel 	part	of transition  fitting  welded  to steel main piping.

- 	Direct connection of galvanized iron or copper service lines to underground steel mains is not permitted.

Service   Lines   Connections   to   Plastic

Mains

- 	In 	case 	of 	plastic 	service 	line, connection to plastic main shall be by

use of electro fusion fittings only.

- 	Direct connection of galvanized iron or copper service lines to underground plastic mains is not permitted.

PIPING   BEYOND   CONSUMER   METER SET ASSEMBLY TO GAS APPLIANCE

Piping connecting consumer meter set assembly  to consumer  gas appliance  shall be  either  GI  or  copper  up  to  last  valve located near actual appliance.

A metal seated leak detection  cum excess flow  shut  off valve  shall  be provided  near the appliance located at easily accessible location by the authorised entity. The  valve shall  be  designed  to  shut  off  in  case  of sudden leakage of gas from the hose or in case of burner flame-off condition.

Appliance  shall  be  connected  to  gas  line with a flexible and braided  hose as per IS

9573.  The  hose  shall  not  be  exposed  to

internal  or external  temperature  exceeding the recommended limits. Care shall be exercised  not  to exceed  permissible  bend radius specified in IS: 9573 (Table 1 - Dimensions   and   bend   radii   for   rubber hoses).

Length of this hose shall be kept minimum. However,  in  no  case  the  length  shall  be more  than  1.5  meters.  Both  ends  of  the hose shall be firmly clamped on the nozzle by metallic clamps.

Schedule – 1E

OPERATING AND MAINTENANCE PROCEDURES

The present  standard  covers the City Gas Distribution, 		  Design, 			 Installations, Commissioning  and  Operation  in  general. The 	Operation 	  and 		Maintenance Procedures prescribed herein under are for general  guidelines  to  be  implemented  as per  the  provisions  of  the  standard. 	The entities 		engaged 	in 	 laying, 	building, operating and expending City or Local Gas Distribution 	Network 	will 		create 		 an organization 	  handling 		operating 	 and maintenance 		including 		   meeting 		the emergencies arising in the system.

The   main   operation   area   would   be   to handle 	gas 	receipt, 	odorisation 	and pressure  reduction  (including  heating  the gas, if required)  and managing  the district regulating  station,  field  regulators  and gas metering for  all kind of customers such as domestic, commercial and industrial.

The gas measuring billing including energy balance shall be part of the operation.   The safety, health and environment including compliance of regulatory measures shall be a part of the responsibility  of the operating group.  The maintenance activity shall cover the  maintenance  and  upkeep  of  the  City Gate 		Station(s),	District 		 Regulating Stations, Field Pressure regulating Stations and end consumers facilities, sectionalising valves and other assets and facilities.   This inter-alia will evolve regular maintenance, route 	patrolling 		to 	 contain 		third 		party damages 	and 	maintenance 	  of 	safety provisions including offsite emergency  plan and onsite emergency plan, mutual aid and disaster  management  plan. 	The  following sections briefly refer to such activities:-

1. 	Operating 	and 	Maintenance

Procedures  affecting  the  safety

OPERATING 	AND 	MAINTENANCE PROCEDURES 		AFFECTING 	THE SAFETY OF GAS TRANSMISSION AND DISTRIBUTION FACILITIES

Basic Requirements

The  entity  operating  a CGD  network  shall have 	an 	effective 	Health, 	Safety 	and Environment Management System (HSE Management  System) and Management  of Change  System  in place to ensure  overall safety during operation and emergencies.

The HSE Management  System shall cover the following key elements.

•	HSE Policy Statement

•	Organizational   objectives   to  ensure implementation of the policy

•	Set  of detailed  processes  supporting each 	activities 	of 	the 	HSE management system

•	Implementation 	of 	control 	and monitoring activities

•	Periodic 	monitoring, 	review 	and reporting of performance

•	Audit of internal and external activities

Following  processes  shall  be  prepared  as part of HSE Management System:

•	Emergency   Management   System  to safely 	handle 	emergencies 	with minimal risk.

•	Disaster 	 Management 		Plan encompassing 	offsite 	and 	onsite emergency 	response 	 plans 		 and mutual aid system

•	Hazard  Identification  Processes  such as HAZOP

•	Risk  Analysis  and  Risk  Assessment

Process such as QRA

•	Safety   and   Technical   Competency

System.

•	An   Operational   Health   and   Safety Legal applicability Matrix as well as Operational 	Health 	and 	Safety (OH&S) Legal Compliance matrix.

•	An Environmental Legislative Register (ELR) to provide the user a register of practical  implementation   in  terms  of day-to-day activities with which the operation has to comply. Of particular relevance are the details of consents / permits / authorization or licenses required for an activity and from whom and how it is obtained.

•	Additional  practices  like  carrying  out periodic  Work  Place  Inspection  of all Critical 		Activities 		by 	senior management  team, implementation  of Behavior Based Safety Programs and implementation  of Safety  Intervention System 	should 	be 	considered 	to improve the safety culture of the organization.

For Safe Control of Operations (SCO), a systematic Management of Change process shall be developed to identify and consider the impact of changes  to pipeline  systems and their integrity. Management  of Change should 	address 	technical, 	physical, procedural  and  organizational  changes  of the 	system, 	whether 	permanent 	or temporary

GIS  based  asset  management  system: The  entity  operating  a CGD  network  shall put 	in 	place 		a 	GIS 	(Geographical Information System) based system with the intention 		of 	capturing 	   the 	entire underground gas network and customer database. This system shall include details of the entire pipe network. All the pipelines laid shall be identified  in GIS through geo- referenced  co-ordinates.  All failures  in the pipelines shall be mapped in GIS for investigations.

The system shall include the following features:-

A) Entire network view ability on one platform 	to 	manage 	the 	huge database.

B)  All 	network 	extensions 	and

expansions 	to 	be 	mapped 	and

updated in GIS with geo-referenced co-ordinates for better identification.

C) Immediate availability of the new constructed pipeline locations and customer   base  information   to  the user 	groups 	allowing 	related analysis, 	planning 	and 	  future projections of new possibilities of pipelines, customers, gas volumes and revenue including jobs to be undertaken by third party.

GIS shall be used during the entire life cycle of the asset.

Essential Features of the Operating  and

Maintenance plan

Operating 	and 	Maintenance 	procedure should also address the following;

•	Preventive 	maintenance 		plan 	and procedures   required   in   accordance with 	recommendations 	of 	Original Equipment Manufacturer(s) (OEMs).

•	A  well-designed   system  of  periodic inspection for all facilities.

•	Calibration   plan  for  meters,  gauges and other instruments affecting quality and safety of system.

•	Plan for functional testing of pressure regulation 	and 	control 	equipment (Active / Monitor Regulator, Slam Shut Valve, Pressure Relief Valves, control valves etc.).

•	Isolation 		scheme 	(complete 		 with drawings  showing  the  orientation  of the 	facilities, 	location 	of 	major services, power switches, entry and emergency exits, fire assembly points etc.). 		It 		should 		cover 	 main components, 			including 			their identification number.

•	Limits 	of 	operating 	parameters (pressure,   temperature,   flow,   levels etc.)

•	An   Alarm   Management   System   to monitor, 	analyze, 	segregate 	and appropriate action.

•	“Work 	Permit” 	procedures 	to 	be followed   by  maintenance   personnel for protection of property from damage and fire etc.

•	Procedures 	to 	log 	operation 	and maintenance activities.

•	Personal 	Protective 	Equipments (PPE) to be used by all operating personnel.

•	Do’s 	and 		Don’ts 		and 	safety precautions 	during 	operation 		and maintenance.

Provisions of periodic inspections along the route   of   steel   pipelines   or   mains   shall include all sections  of pipelines  and mains irrespective of operating hoop stress.

Essential   Features   of   the   Emergency

Plan

Entities   operating   CGD   Networks   shall provide for an Emergency Control Room, manned round the clock and equipped with effective 	communication 	system 	 and emergency 		  vehicles 	fitted 	with communication 		facilities, 		first 		aid equipment, 		fire 		extinguishers, 	 gas detectors,   repair   kits   and   tools,   maps, plans, material safety data sheets etc. at its disposal.

The CGD entity shall put in place an Emergency Response Plan, a Disaster Management Plan and a Pandemic Plan. While preparing these plans the entity shall take into confidence the various local authorities  (i.e. The Fire authorities,  Police authorities, 	Health 	authorities, 	local administration, 	Disaster 	Management authorities, Mutual aid, Factory inspectorate etc)  and  clearly  elaborate  on  their  role  in case of an incident.

Accident 	/ 	emergency 	reporting procedures

The entity shall put in place a documented in house accident  reporting  procedure  and its 	response 	plan 		for 	all 	kind 	  of accidents/emergencies    such   as   (i)   near miss accidents, (ii) accidents without loss of production, 	supply 	or 		human 	 life, 	(iii) accidents with loss of production, supply or human life, (iv) fire (v) explosion or other emergencies leading to disaster effecting outside public.   The level of reporting shall also be mentioned in the procedure. The Board  shall  be informed  in respect  of the accidents/emergencies  under category  (iii), (iv) and (v) above with remedial  measures

for avoiding recurrence in the format placed at Enclosure-I of Schedule -1E. The entities shall  investigate   and  report  each  of  the above incident/accident  to different level as specified in the above enclosure.

Notwithstanding anything contained herein under,  in case  any incident  escalates  and gets media attention or gets published in newspapers,   the   entity   shall   proactively inform the Board of the same immediately with 	preliminary 	investigation 	report. Further, detailed report of the findings shall be furnished to the Board within a period of thirty days.

Written Emergency procedures

Special attention should also be given to following 	while 	preparing 	Emergency procedures:

•	“Do’s 	and 	Don’ts” 		during 		and emergency 	and 	other 	safety instructions.

•	Telephone   numbers   of   emergency response  team members,  emergency services, mutual aid industries, district authorities, law enforcing agencies, contractors / vendors, fire services, district civic authorities, etc.

•	Actions 	to 	be 	taken 		during 	an emergency 	 including 	warning 	   / cordoning off of affected area and informing the civil authorities  and / or other utility companies affected by any emergency.

Training

•	Training shall be imparted to the CGD Network operating and maintenance staff at the time of induction  followed by  periodic  refresher  courses. 		The training 	program 	should 	cover following:

•	Hazardous characteristics of Gas.

•	Familiarization  with  commissioning, operation 	and 	maintenance procedures.

•	Hands  on  experience  on  operation of   emergency   and   manual   shut down systems.

•	Effective isolation of any gas leak.

•	Safety 	regulations 	and 	accident prevention.

•	Firefighting 	equipment 	operation and its upkeep.

•	First Aid and Housekeeping

The training process should be subjected to periodic  internal  audits  to ensure  effective implementation and improvement.

Training shall include mock safety drills, at least twice a year.

Training 	program 	shall 	also	envision imparting 	  training 	 to 	  employees 	and contractors 	of 	other 	utility 	companies sharing the same corridor to make them aware about hazards associated with leak / damages.

Liaison

Entity owning or operating CGD networks should have designated personnel to liaison with other existing utility companies, district local administration and gas supplying companies. A utility co-ordination team consisting  of representatives  from all other utility companies and civil authorities can substantially improve safety records.

Educational Programs:

Entities operating CGD Networks shall undertake 		  a 	comprehensive 	 public awareness program for consumers and general   public.   The  educational   material shall be prepared in local, Hindi and English language. 		Local 		audio 	visual 	media available 	should 		be 	used 	for 		such educational programmes.

Pipeline Failure Investigation

Besides reporting and recording of all instances of asset related failures, damage to the environment  and third party property shall also be recorded.

Failure investigating team shall comprise personnel trained in failure investigations.

The data from all failure occurrences should be analyzed for trends so that proper initiatives  including  training  could be taken to minimize failures.

Prevention of Accidental Ignition

Site Specific Risk Assessment should be carried  out before  commencing  any repair activities. 	The 	outcome 	of 	such 	risk assessment should be documented and considered  while  preparing  safety  plan  for the repair work.

No hot work should be undertaken  without proper work permit issued by authorized personnel.

Blasting Effects

No blasting should be carried out within city limits and near any third party structures or facilities. In any case blasting shall only be used after proper authorization from civil authorities even if it is safe to carryout such operations.

DISTRIBUTION PIPING MAINTENANCE.

Markers

Markers shall be positioned along entire network   at  a  maximum   spacing   of  100 meters in urban area and 200 meters within industrial parks for steel mains.

Additional  warning  signs  or  markers  shall be installed to indicate the presence of a pipeline at road, highway, railroad, stream, canal, nala crossings and other locations where  there  is a possibility  of damage  or interference.

A  marker  shall  be  marked  in  bold  and legible  local  language  and  Hindi  / English with at least the following:

•	Name   of   CGD   Network   Operating

Company

•	Contact  Telephone  Number  to report emergency.

•	Location Area Code

•	Warning  - “High  Pressure  Gas  Line, Dial before Digging” etc.

Markers may not be installed for service pipeline 		within 		consumer 	premises, however, the Operating Company shall maintain 	such 	service 	pipeline 	routing drawings for easy reference. The operating

company shall provide minimum safety information 	to 	the 	consumer/customer before starting the gas supply.

It shall be mandatory for the group housing societies/cluster of houses etc. which are providing the inbuilt facilities for the natural gas connectivity to each and every dwelling unit in such buildings to have the line diagrams  of the connection  piping  fixed at the main entrance of such premises.

Patrolling

Patrolling schedule shall be such that entire primary network is inspected  at least once in three (3) month and secondary network is inspected at least once every month to observe surface conditions, construction activity, encroachments,  soil wash outs and any other factors that may affect the safety and operation of the network.

Leakage Surveys

Operating company must have an effective method  to  identify  and  locate  leakages  in the system. Any one or combination of methods 	described 	in 	ASME 	B 	31.8, Appendix M can be adopted based on their effectiveness for the specific areas.

Highly  congested  areas  shall  be surveyed using gas detectors  at least once  in three months.  Other  less  congested  areas  shall be surveyed at least once a year.

Leakage Surveys using gas detectors shall be 	done 	in 	accordance 	with 	the requirements of ASME B 31.8.

Gas detectors, duly calibrated, shall be available at all times in ready use conditions for emergency surveys and use.

Requirements 	for 	Abandoning, Disconnecting, 	 and 	 Reinstalling Distribution Facilities

Abandoning, disconnecting, or reinstalling distribution  facilities  shall be as per ASME B31.8.

Any activity associated with abandoning, disconnecting,  or reinstalling  of distribution

facilities  shall  require  Work  Permit  issued by the authorized person.

Plastic Pipe Maintenance

The following safety precautions shall be ensured 	during 	emergency 	repairs 	or breakdown maintenance of pipelines:

.

•	All naked  flames,  sources  of ignition and   mobile   phones   shall   not   be allowed in the immediate work area.

•	Gas level should be monitored during the  repair  work  with  gas  detectors. The repair shall not be carried out in atmosphere   which   contains   natural gas.

•	Adequate fire extinguishing equipment shall be available during such repair.

Squeezing-off 	 and 		reopening 		of Thermoplastic 	Pipe 	or 	Tubing 	for Pressure Control

Location where Squeezing and reopening is done once shall be marked appropriately to identify  that  the  pipe  has  been  squeezed and reopened.

Squeezing of reopened pipe at the same location is not permitted. Minimum distance between consecutive squeeze-off locations shall not be less than five (5) meters.

Repair of Plastic Pipe or Tubing

Damaged or defective plastic pipe shall be cut and replaced with new pipe.

Repair of damaged plastic pipe by using repair patches is not permitted.

Only repair method allowed is use of full encirclement split sleeves which shall be in accordance with ASME B 31.8.

MISCELLANEOUS FACILITIES MAINTENANCE

Flexible steel braided hose used to connect consumer  appliances  should  be  inspected at   least   once   every   year   for   leakage, kinking,  corrosion,  abrasion  or  any  other signs of wear and damage.

Any hose worn out or damaged must be removed from service and replaced.

PIPELINE SERVICE CONVERSIONS

Steel pipelines and mains used in CGD Network shall not be used for duel service.

Conversion 	of 	existing 	steel 	pipelines, previously   used   for   service   other   than natural gas, for use in CGD Networks is not permitted.

RECORDS

Besides   the   details   of  leak   records   as covered under ASME B31.8 Para 851.6 and

852.6,  the  CGD  Network  Company  shall also maintain following records/ documents:

•	Design specification

•	Alignment  sheets for primary network of steel pipeline  and associated  pipe book and other installation and test records

•	Surveillance 	inspection 	and maintenance records

•	Material 	certification 	including dimension, metallurgy, destructive and non-destructive 		testing 	 records, performance 		and		functional 	test reports

•	Welding records including PQR, WPS

and welder qualification records

•	Commissioning reports

•	Non-conformance / deviation records

•	Calibration 	records 	of 		Inspection, Measuring, 		Metering	and 	Test equipment

•	Audit compliance reports

•	Statutory clearances

•	Approved drawings /documents

•	HAZOP   /  Risk  Assessment   reports and  compliance  to  recommendations of such reports

•	All 	operation 	and 	maintenance manuals

Enclosure-1 of Schedule-1E

Reporting Format

|  | Type-I Near Miss incident | Type-II Without Loss of Production, Supply or Human life | Type-III With Loss of Production, Supply or Human Life | Type-IV Fire | Type-V Explosion /Fire/Gas Leakage/other emergencies involving public |
| --- | --- | --- | --- | --- | --- |
| Location | √ | √ | √ | √ | √ |
| Time | √ | √ | √ | √ | √ |
| First Witnessed by | √ | √ | √ | √ | √ |
| Details of Incident | √ | √ | √ | √ | √ |
| Action Taken | √ | √ | √ | √ | √ |
| Reporting Authority | Operat or (O&M) | Operator (O&M) | Shift I/C | HSE Officer | Section I/C |
| Internal Investigating Authority | Head (HSE) | Head (HSE) | Head (O&M) | Head (HSE) | Head of Station |
| External Investigation | X | X | √ | √ | √ |
| Report to PNGRB | X | X | √ (*) | √(*) | √(*) |

√  To be filled in/reported

X Not required to be reported

(*) Shall also include the history of Type-I & Type-II incidents

Schedule – 1F

CORROSION CONTROL

EXTERNAL CORROSION CONTROL

New Installation/Buried Steel Facilities

Coating  Requirements,

Coatings 	shall 	fulfill 	following requirements:

•	Coating  shall provide  good electrical isolation  between  external  surface  of the pipe and environment.

•	Coating 	shall 	have 	sufficient resistance to moisture  transmission.

•	Coating  shall have sufficient  ductility to resist cracking;

•	Coating  shall have good mechanical strength   or  otherwise be  protected to resist damage  due to normal handling  (including concrete  coating application  where   applicable)  and soil stress.

•	Coating   shall   be   compatible  with Cathodic  Protection system  and field joint coatings.

For  carbon   steel  pipelines   or  mains   of size 	NPS 	2 	and 	above, 	3 	Layer Polyethylene or Fusion Bonded  Epoxy coating  is recommended.

All   buried   bends   and   fittings   shall   be coated  with  Heat  Shrink  Sleeves  or  two pack high build liquid epoxy coating with minimum  DFT 450 microns.

Cathodic  Protection Requirement

Electrical  Isolation

Where  insulating devices  are  installed  to provide  electrical  isolation  of pipeline systems  to facilitate  the application of corrosion   control,  they  shall  be  properly rated    for 	temperature,   pressure,   and electrical  properties and shall be resistant to the gas carried  in the pipeline  systems. These devices shall not be installed in enclosed 	 areas 	where 	combustible

atmospheres  are   likely   to   be   present unless  precautions are  taken  to  prevent arcing.

Pipes  shall  be installed  so that the below grade  or  submerged portions   are  not  in electrical  contact  with any casing,  foreign piping 	systems 	or 	other 	metallic structures. 	This  shall  not  preclude   the use of electrical  bonds where necessary.

Electrical   Connection  and  Monitoring

Points

Where  a higher  current  carrying  capacity is required,  a multi-strand conductor shall be 	used 	and 	the 	strands 	shall 	be arranged  into groups  no larger  than  No.6

AWG. 	Each  group  shall  be  attached  to

pipe  with  a  separate   charge. 	Attaching test leads directly to the pipe by other methods  of brazing  is prohibited.

When  thermit  welding  process  is used for electrical  lead  installation on  pressurized pipelines   or  mains,  precautions shall  be taken   to   avoid   possible   failure   of   the pipeline  or  mains  during  installation due to loss of material  strength  at the elevated welding  temperatures. Where a thermit welding  process  is not  deemed  suitable, consideration shall be given to other methods  of installation.

Electrical  Interference

Electrical   interference  due   to   following shall also be considered in cathodic protection design:-

Fault Currents

Fault  current  interference shall  be  taken into consideration.

Fault   current   resulting   from   lighting   or upset   conditions   of   electrical    facilities

could  result  in serious  damage  to coating and  pipe  wall  and  danger  to  personnel. These adverse  effects may occur where a pipeline  or main is close to the grounding facilities  of electrical  transmission line structures,	sub-stations, 	generating stations  or  other  facilities  that  have  high short circuit current-carrying grounding networks.

Where  a buried  pipeline  or main  is close to grounding facilities,  remedial  measures may be necessary to control  the effect  of these fault currents  in order to reduce  the resultant  rise  in  potential  gradient  in  the earth near the pipeline or main to an acceptable level.

Induced  Potential  Interference

Pipelines  or  mains  paralleling alternating current electrical  transmission lines are subject 	to 	induced 	potentials. 	When studies   or   tests   show   that   alternating current   potentials  will  be  or  are  being induced   on  a  buried   pipeline   or  main, devices  shall be installed  to reduce  these potentials to a tolerable  level.

When  such  pipelines  or mains  are under construction, or when personnel are in contact    with    the   pipelines    or   mains, special   precautions  shall   be   taken   to nullify the possible effects of induced alternating current potentials.

Install bonding across points where the pipeline  or  main  is  to  be  separated and maintain 	this 	connection	while 	the pipeline  or main is separated.

Make a study in collaboration with the electric 	company 	on 	the 	common problems   of  personnel safety,  corrosion, electrical 		interference	 and 		lighting problems.

Existing  Installations

Cathodically Protected Pipeline  Systems

Temporarily out of Service

Cathodic    Protection   systems    shall   be

maintained on any pipeline  or main temporarily out of service.

Temporary Cathodic  Protection System

When 		considered	necessary, 	a temporary   Cathodic    Protection   system with sacrificial  anodes  shall be installed  to ensure  adequate protection of pipeline  or mains   from  external   corrosion   from  the time  the  pipeline   or  main  is  laid  in  the trench 	till 	the 	permanent	Cathodic Protection system is commissioned.

The 	temporary 	cathodic 		protection system 	shall 	preferably	be 		installed simultaneously keeping  pace with the pipeline   or  main  laying/installation  work and shall be monitored periodically.

RECORDS

CGD 	Network 	Company	shall 	also maintain  following  records / documents related to corrosion  control:

•	Cathodic 	Protection 	Design documents

•	Soil Resistivity Survey Report

•	Electrical  Interference Report

•	Inspection and maintenance reports

•	Material 	certification 	including dimension, metallurgy, performance and functional report

•	Material  test reports

•	Approved drawings/documents

Schedule – 1G

MISCELLANEOUS

ODOURISATION

Natural gas supplied through CGD Network shall have a distinct  odour, strong enough to detect its presence in case of leakage.

A pre – determined quantity, equivalent to a max  12.5  ppm  Ethyl  Mercaptan,   of  any other  odorant  shall  be dosed  into the gas stream.

Odour level tests shall be carried out to recognise the odour imparted by the gas supplier/distribution   company.  These  tests are to be carried out at various defined locations on the network and at network extreme ends. If odour level falls below the minimum acceptable level same shall have to be intimated  to the control  room  of the gas supplier and accordingly corrective actions are to be taken.

The odorizing equipment shall be located in a separate area at CGS. There should be a clear  safety  distance  of 1.5 m around  the odorizing and other facilities at the station to facilitate easy maintenance and personnel movement.

The odorant unloading should be done in a safe way.  Precautions for handling odorant shall be prominently displayed.

Odourant   absorber   like  activated   carbon saw dust, dry sand and odorant neutralizer like 	sodium 	hypochlorite 	for 	spillage handling of odourant shall be provided.

Provision  should be made for eye wash or emergency  shower  near  odorant  handling and 	injection 	systems, 	in 	case 	ethyl mercapton is used as odourant.

Use  of  personal  protective  equipment  like face shield, mask, rubber hand gloves, gumboot, safety goggles etc. for handling of odourant spillage shall be ensured.

References

ASME B 31.8 – Gas Transmission and Distribution  Piping Systems  (ASME 3 Park Avenue,   New  York,  NY 	USA 	10016. www.asme.org).

API 	1104 	- 	Welding 	procedures 	and welders for welding of gas pipelines.

ASME Boiler and Pressure Vessel (BPV) Code Section IX - Welding procedures and welders, for station piping.

ASTM  A 395 - Valves  having  shell  (body, bonnet, 	cover 	and/or 	end 	flanges) components made of cast iron and / ductile iron (as per shall not be used in CGD networks).

BS EN 331 - Valves used in service lines of size NPS 2 and below.

ISO 8085  - Electro-fusion  fittings  for sizes up to NPS 8.

IS-5572  - Electrical  area  classification of Installation	for 	selection 	of 	Electrical Equipment

IS 	- 	5571, 	“Guide 	for 	selection 	of Electrical 	Equipment		for 		Hazardous Area”.

IS 3043 – For earthing of all electrical equipment, 	systems, 	structures 	and fencing,  etc.

IS:2309  – for Lightening protection

IS 9573 – Steel braided Hose

ANNEXURE – I

List of Specifications of Piping Materials used in

CGD Network

Steel Pipe

API 5L 	Specification for Line pipes

ASTM A106 	Seamless Carbon Steel Pipe for High Temperature Service

ASTM A333 	Seamless and Welded Steel Pipe for Low-Temperature Service

Galvanized Iron Pipes

IS 1239 (Part-1) 	Steel Tubes, Tubular and Other Wrought Steel Fittings - Specification  - Part 1 : Steel Tubes

Valves

API 6D 	Pipeline Valves

ASME B16.34 	Valves Flanged, Threaded and Welding End

BS 5352 	Specification  for steel wedge gate, globe and check valves 50 mm and smaller for the petroleum, petrochemical and allied industries

BS 5351 	Specification  for steel ball valves for the petroleum,  petrochemical  and

allied industries - Small Floating ball valve

BS 1873 	Specification  for Steel globe and globe stop and check valves (flanged and  butt-welding   ends)  for  the  petroleum,   petrochemical   and  allied industries

Flanges and Blanks

ASME B16.5 	Steel pipe flanges and flanged fittings - Size upto 24" NB. ASME B16.36 	Orifice Flange

MSS SP-44 	Steel Pipeline Flanges

API 590 	Steel Line Blanks

Fittings

ASME B16.9 	Factory-Made Wrought Steel Butt welding Fittings

MSS SP-75 	Specification for High Test, Wrought, Butt Welding Fittings

MSS SP 97 	Integrally  Reinforced  Forged  Branch  Outlet  Fittings  - Socket  Welding, Threaded and Butt welding Ends

IS 1239 (PART-2) 	Steel Tubes, Tubular and Other Wrought Steel Fittings - Specification  -

Part 1 : Mild Steel Tubular and other wrought steel pipe fittings

Stud Bolts and Nuts

ASTM A194 	Standard Specification for Carbon and Alloy Steel Nuts for Bolts for High

Pressure or High Temperature Service, or both.'

ASTM A193 	Standard   Specification   for   Alloy-Steel   and   Stainless   Steel   Bolting Materials  for  High  Temperature  or  High  Pressure  Service  and  Other Special Purpose Applications

ASTM A153 	Standard  Specification  for  Zinc  Coating  (Hot-Dip)  on  Iron  and  Steel

Hardware

ASME B18.2.1 	Square and Hex Bolts and Screws, Inch Series

ASME B18.2.2 	Square and Hex Nuts

Gaskets

ASME B16.20 	Spiral-wound  metal  gaskets  and  metal  jacketed  gaskets  for  use  with raised face and flat face flanges.

Copper Tubes

BS EN 1057 	Copper and copper alloys. Seamless, round copper tubes for water and gas in sanitary and heating applications

Copper Fittings

BS EN 1254 PART 1  Copper  and  copper  alloys.  Plumbing  fittings.  Fittings  with  ends  for capillary soldering or capillary brazing to copper tubes

Plastic Pipes

ISO 4437 	Buried polyethylene  (PE) pipes for the supply of gaseous fuels -- Metric series -- Specifications

IS 14885 	Specifications for polyethylene pipes the supply of Gaseous Fuels

Plastic Valves

ASME B16.40 	Manually  Operated  Thermoplastic   Gas  Shutoffs  and  Valves  in  Gas

Distribution Systems

EN 10204 	Excess flow check valve

EN 1555-4 	Plastic piping system for supply of gaseous fuels polyethylene – Part 4

Plastic fittings

ISO -8085 -3 	International Standard for thermoplastic fittings

EN – 1555-3 	European standard for plastic piping system for supply of gaseous fuels – Polyethylene (PE) Part -3 : fittings

ISO/TC-138/SC4 N 521 & 523 – 1990 Thermoplastic fitting procurement requirements

High Pressure SS Tubing and Fittings

ASTM A269 	Standard  Specification  for  Seamless  and  Welded  Austenitic  Stainless

Steel Tubing for General Service

Brass Ball Valves (Up To 2”)

BS EN 331 	Manually  operated  ball valves and closed bottom  taper plug valves for gas installations in buildings

Brass Fittings

IS 319 	Free Cutting Leaded Brass Bars, Rods and Sections – Specification

ANNEXURE – II

List of Specifications for Equipment used in CGD Network

Pressure Safety Equipment (Regulators, Slam Shut Valves and Creep Relief Valves)

EN 334 	Gas pressure regulators for inlet pressures up to 100 bar

EN 14382 	Safety 	devices 	for 	gas 	pressure 	regulating 	stations 	and installations  - Gas safety shut-off devices for inlet pressures  up to 100 bar

API 526 	Flanged Steel Pressure Relief Valves

Filters

ASME Section VIII 	Boiler and Pressure Vessel Code

Metering Equipment

AGA Report No. 3 	Orifice Metering of Natural Gas and Other related Hydrocarbon fluids

AGA Report No. 5 	Fuel Gas Energy Metering

AGA Report No. 9 	Measurement of Gas by Multi-path Ultrasonic Meters

OIML R6 / OIML R31 Diaphragm gas meters

BS 1359 / BS 4161 	Diaphragm gas meters

EN 12480 	Gas meters - Rotary displacement gas meters OIML R32 	Rotary piston gas meters and turbine gas meters AGA Report No. 7 	Measurement of Gas by Turbine Meters

EN 12261 	Gas meters - Turbine gas meters

Pressure Measuring Equipment

BS EN 837-1 	Pressure  gauges - Part 1: Bourdon tube pressure gauges; dimensions, metrology, requirements and testing

BS EN 837-2 	Pressure Gauges - Part 2: Selection and Installation Recommendations for Pressure Gauges

BS EN 837-3 	Pressure  gauges  -  Part  3:  Diaphragm  and  capsule  pressure  gauges;

dimensions, metrology, requirements and testing

Electro fusion machine for jointing PE pipe and fittings

EN - 55014

EN – 50081-1

EN – 50082-1

EN – 61000-3

EN – 60335-1

EN -  60335-2-45

ISO- 12176-2

ANNEXURE – III

Additional Requirements for Electric Welded Pipes

Electric  Welded  pipes shall meet following requirements.

Reverse Bend Tests

Reverse  bend tests shall be performed  on the  pipe   piece   cut  from   the  crop   end, selected   from  the  front  end  of  the  first length and the back end of the last length produced  from  each  coil.  The  specimen shall be 100mm  to 115mm  long and shall be reverse bend tested in accordance  with procedure and figure given hereinafter.

The reverse bend test shall be carried out with a mandrel. Radius (R) and width (A) of mandrel 	shall 	be 	calculated 	for 	any combination of diameter, wall thickness and grade with the formula.

1.4 (D-t) t

A = 2R  = ----------------- 	-  t e (D-2t)-1.4 t

where,

D 	- 	Outside diameter of pipe t 	- 	Wall thickness of pipe

1.4 	- 	Peaking factor

e 	- 	Strain

Minimum values of 'e' shall be as follows: Grade of Steel 	Min 'e' value

API 5L Gr. B 	0.1425

API 5L X-42 	0.1375

API 5L X-46 	0.1325

API 5L X-52 	0.1275

API 5L X-60 	0.1225

Procedure

The mandrel is to be plugged into the specimen, with the weld in contact with mandrel, to such a depth that the angle of engagement 	between 	mandrel 	and specimen  reaches  60° (see Figure).  If the combination of diameter and wall thickness of pipe, and radius of mandrel is such that the  angle  of  engagement  does  not  reach

60°, the mandrel shall be plugged into the specimen 	until 	opposite 	walls 	of 	the specimen meet.

Acceptance Criteria

A   specimen   which   fractures   completely prior 	to 	the 	specified 	engagement 	of mandrel and specimen, or which reveals cracks and ruptures in the weld or heat affected zone longer than 4mm, shall be rejected. Cracks less than 6mm long at the edges of the specimen  shall not be cause for rejection.

Micrographic and Hardness Examination

A test specimen  shall be taken across the longitudinal weld from one length of finished pipe from each lot of maximum 100 lengths from the same heat manufactured  from the same process.

These specimens shall be polished and etched 	for 	micro-examinations. 	The examinations   shall  provide  evidence  that heat  treatment  of  weld  zone  is  adequate and there is no un-tempered martensite left.

Hardness 	measurements 	on 	each specimen  shall  be  made  as  indicated  in figure given herein after in accordance with ASTM E-32. 		The maximum  difference  in

hardness between base material and any reading  taken  in  the  Heat  Affected  Zone (HAZ) shall be less than 80 points Vicker's HV10.

ANNEXURE - IV

Minimum Requirements for GI Pipes and Copper

Tubing used in service lines up to consumer appliance

Galvanized Iron (GI) Pipes

Pipes shall be conforming  to IS: 1239 (Part-1)  – 1990. The manufacturer  shall have a valid license to use ISI Monogram for manufacturing of pipes in accordance with the requirements of IS: 1239 (Part-I) – 1990.

| NOMINAL BORE | 15 mm | 25 mm | 50 mm | 80 mm |
| --- | --- | --- | --- | --- |
| GRADE | MEDIUM (‘B’ CLASS) or HEAVY (‘C’ CLASS) | MEDIUM (‘B’ CLASS) or HEAVY (‘C’ CLASS) | MEDIUM (‘B’ CLASS) or HEAVY (‘C’ CLASS) | MEDIUM (‘B’ CLASS) or HEAVY (‘C’ CLASS) |
| O.D. mm max. Min. | 21.8 21.0 | 34.2 33.3 | 60.8 59.7 | 89.5 88.0 |
| THICKNESS mm | 2.6 for B Class and 3.2 for C Glass | 3.2 for B Class and4.0 for C Glass | 3.6 for B class4.5 for C Glass | 4 for B class and4.8 for C Glass |
| NOMINAL WEIGHT Kg / mtr. | 1.21 for B Class and1.44 for C Glass | 2.41 for B Class and2.93 for C Glass | 5.03 for B class6.19 for C Glass | 8.36 for B class and9.90 for C Glass |

Note :

Maximum tolerance on thickness (-) 10%, Tolerance on weight for single tube ± 10% and for quantities per load of 10 tones, ± 7.5%

•	Pipes shall be designed to withstand a test pressure of 5 MPa (50 bar), maintained for at least 3 second without showing any kind of defects.

•	Eddy Current test may be done in place of hydrostatic test as per the procedure given in

Annex - C of IS: 1239 (Part-1) - 1990.

•	All Galvanized Tubes shall be Zinc coated by hot dip galvanizing in accordance with IS:

4736-1986 & its relevant parts.

•	Minimum mass of zinc coating determined as per IS: 6745-1972 shall be 400 gms / m2.

•	The zinc coating on external  and internal  surfaces  shall be adherent,  smooth and free from  such  imperfections  as flux, ash and dross  inclusions,  bare  patches,  black  spots, pimples, lumpiness, runs, rust stains, bulky white deposits and blisters.

•	Rejection and acceptance for these defects shall be as per Appendix-A of IS:  2629-1985

•	The galvanized coating when determined on a 100 mm long test piece in accordance with

IS:  2633 - 1986 shall withstand 4, one - minute dips.

•	The adherence of zinc coating on tubes above 50 mm nominal bore, shall be determined by the pivoted hammer test given in IS : 2629 - 1985.

Each pipe shall be legibly and durably marked at intervals of not more than one metre with the following  information  (i) Manufacturer’s  name or trade mark, (ii) Class of Pipe – HEAVY, (iii) Indian Standard mark – ISI, (iv) Batch No. of Production, if any.

Fittings conforming to the requirements of IS 1879 : 1987, IS  14329 : 1995  are permitted to be used in Tertiary network, operating at pressures 100 mbarg and below :

Copper Tubing

For  a  copper  service  in  domestic  natural  gas  installations,  materials  supplied  shall  be  in accordance with BS EN 1057:1996. It has replaced the copper tube standard BS 2871 Part 1. BS EN 1057 ensures the quality of the copper product by specifying  the pipe in terms of its chemical  composition,  mechanical  properties  e.g. tensile strength,  hardness,  elongation  etc., dimension and tolerance, surface quality, freedom from defects and suitability for pipe bending.

Copper pipe work shall be jointed by soldering  or brazing, using mechanical  compression  or capillary type fittings. Fittings for use in joining copper tube shall be as per BS EN 1254 Parts 1 and  2. Fittings  for  capillary  soldering  and  brazing  are  specified  in Part  1 and  compression fittings are specified in Part 2.

Soft soldering utilizes filler metals with melting points at temperatures up to 450°C. Filler metals shall be as per BS EN 29453:1994  - Soft solders alloys - Chemical compositions  and forms. Solders for use with copper tube and fittings generally melt within the temperature range 180°C to 250°C. Compression fittings shall comply with BS 864 Part 2 or BS 2051 Part 1.

For capillary fittings:

•	Soft solder shall not be used for pressure in excess of 75 mbar

•	If the operating pressure is to exceed 75 mbar, then, a solder with a melting point of not less than 600 degrees C shall be used. This shall also apply to brass fittings.

Height limit for copper risers: Although there is no specific guidance regarding maximum height of copper risers, IGE/UP/2  only allows the use of steel for risers above heights of 15 meter. Thus, unless local information is available to the contrary, 15-meter maximum height shall be considered safe due to weight and mechanical strength of material.

General  guidance  in BS 6891  also states  that copper  pipe work  is not acceptable  inside  a protected shaft. Requirements  for ventilation and fire stopping shall apply to ducts conveying copper pipe work. For an external copper riser system, protection against lightning conductors shall be considered.

A copper gas line shall never be used as a ground for an electrical system.

(F.No.-S-admin/11/8/2007-Vol I

Ratan P. Watal

Secretary, PNGRB

# Text boxes

| Table – 1 : Inter-distance between Facilities at CGS |
| --- |
| Sr. No. | From / To | 1 | 2 | 3 | 4 | 5 | 6 |
| 1 | Compound Wall | - | 6 | 6 | 6 | 6 | 6 |
| 2 | Control Room / Office Building / Store | 6 | - | 12 | 12 | 2 | 15 |
| 3 | Pressure Regulation and / or Metering | 6 | 12 | - | 2 | 12 | 15 |
| 4 | Odorant System | 6 | 12 | 2 | - | 12 | 15 |
| 5 | Electrical Sub Station | - # | 2 | 12 | 12 | - | 15 |
| 6 | Gas fired heaters | 6 | 15 | 15 | 15 | 15 | - |

500 mm

250 m

|  | of gas transmission | and |
| --- | --- | --- |
|  | distribution facilities. |  |
| 2. | External Corrosion Control |  |
| 3. | Odorisation |  |