HVAC CONTROL SYSTEM - September 2011

Also referred to as Building Automation System (BAS)

Red is used to identify potentially controversial content and content that almost surely needs facility specific editing.

Design Instructions for Mechanical Consultant and Architect

This text should be read in conjunction with the Building Automation System guide specification that follows.  Because the guide specification is frequently updated, the current version should be obtained directly from the Project Manager for each project.

Use of Guide Specifications

To create a network of buildings and/or expansions that can be maintained and operated efficiently as a coordinated facility, Each new control system must conform to the facility standards.  However, your suggestions as an experienced designer are encouraged and may be incorporated into the facility standards.

The guide specifications shall be modified to the extent necessary to meet the needs of the particular project, but the final specification shall not deviate from the basic facility concepts and requirements set forth.

Make an exact copy of the guide specifications and then modify it to meet the particular project needs and numbering system.  Do not try to blend it with your own standard specification or that of a vendor.  If you require vendor support, you must use the approved vendors.

Your primary input will be the Sequence of Operation, Points Matrix and indication of point locations on the drawings.

Guide Specification Contents

The following is a list of some of the guide specification requirements:

Electric actuators will generally be used but pneumatic actuators may be used, with owner approval, for large devices and in high temperature applications.

Hard-wired fan high-limit pressure switches and low-limit freeze stats should be provided as backup to software-based protection sequences.

Control system must return to normal operation without human action after a power outage or fire alarm

Operator interface with the control system should be possible from remote PCs, portable PCs and the primary operator station.

Coordination with Dedicated Controls

Indicate the relationship between the HVAC control system and the dedicated controls for specific HVAC equipment such as VFDs, chillers, heat pumps, furnaces, and boilers.

- Use dedicated controls provided under other sections of the project specifications to handle staging and coordination of parts within each major piece of equipment.  This provides a sole source of responsibility for the equipment’s performance to avoid damage to the equipment, to increase safety, and to increase Contractor and manufacturer responsiveness during problem solving.

The building’s HVAC control system may offer chilled water temperature reset, monitoring and enable the local controls for “on/off.”  Coordinate with facility O&M staff to determine the parameters monitored by the HVAC control system.

Insure that appropriate interface occurs between the BAS and equipment such as chillers, boilers, VFDs, etc.

Make sure equipment submittals and on-site testing include the interface between dedicated controls and the building’s HVAC control system.

Gauges and Test Ports

Coordinate with piping specialties to assure there is a test port, gauges, sensor attachments and sensor wells at each BAS piping sensor location.

Provide gauges and test ports at all entering and leaving points of chillers, boilers and other primary equipment.

Commissioning

Much of the labor required for commissioning is provided by the Control Contractor.  Coordinate control specifications with commissioning requirements in other specification sections so that the control system is operated by the Control Contractor for all commissioning tests that require the control system.

Fire and Emergency Power must be coordinated with BAS to insure full code compliance and desirable performance.  Here are some sample ideas:

- Only the fire alarm system should control life safety fans such as atrium, elevator shaft, and dedicated fire/smoke control dampers.  Fire smoke damper status is not of concern to the HVAC controls as the fire alarm system should not release the fans to run until those dampers are open. The fire alarm system should directly shut down all HVAC fans over 2000 cfm and that shut down authority should be effective for all positions of the local HOA or VFD controls. The HVAC control system shall not control fans after shutdown by the fire alarm system until after reset of the fire alarm system.  Toilet and other non-recirculating exhaust fans shall remain on unless this creates a problem with air quality or excessive pressure on exit doors.

- In units where mechanical systems operate under BAS control in emergency power conditions, the HVAC control system shall monitor the fire alarm panel to determine when the building is under a fire alarm condition.   The HVAC Control System shall monitor the emergency power transfer switch to determine when there is loss of normal power and restoration of normal power.

- Smoke/fire dampers and smoke/fire damper actuators are to be specified under the air distribution system, not under the HVAC control specifications.  When a pneumatic system is already available, use pneumatic actuators and copper pneumatic lines for smoke/fire dampers.  Coordinate control specifications to provide pneumatic lines to any pneumatic smoke/fire damper actuators specified under other sections.

Design Evaluation

The following information is required to evaluate the design:

Programming Phase:  On retrofit projects, description of existing control system if relevant to project.

Schematic Design Phase:  None

Design Development Phase:  Provide sequences of operation for all controlled equipment.  In the sequences, provide initial setpoints for all user-adjustable values, including the fan high-limit pressure switch setpoints, and water and air static pressure and differential pressure setpoints.  In the sequences, include HVAC responses to fire and loss of normal power, even if these are determined under Division 16, and note where appropriate that a sequence is performed under Division 16.  Place the sequence of operations on the mechanical drawings, not in the specifications.  Indicate control diagram/panel locations.  Provide a preliminary point list.

Construction Document Phase:  Provide a points-list showing all input/output requirements.  For each point, designate DI/DO/AI/AO/PWM/FPC, and two-position or modulating.  For valves, designate the Cv (and, where appropriate, the close-off pressure differential).  Use equipment identifiers for all controlled equipment and sensors that are integrated and consistent with standard facility practices.

Construction Submittals

See the HVAC Control Systems guide specification.

Related Sections

Variable Frequency Drives

Heating Ventilation and Air Conditioning

Commissioning

Central Cooling Water

Electrical – Fire Alarm System

Products, Materials and Equipment

Manufacturers

- All control components shall be 100% compatible with the base system, base system software and programming shall be used and there shall be no learning curve associated with non base equipment.  Standalone equipment such as chillers, boilers, VFDs, etc must digitally interface effectively with the base system.

Remodels and Expansions

On remodels and expansion projects, consult with Facility Department on how to coordinate new and existing controls.

Owner should describe how pneumatic and DDC systems should interface and if all existing controls are replaced as part of a project.

HVAC Actuation

Generally, actuators shall use 24 VAC power, analog control (or floating point control with position feedback) and mount around a rotating shaft to modulate dampers and valves.

Large damper sections shall be made up of multiple small dampers operating in parallel so one actuator controls one small damper.  Control sequences may first open and modulate only one or two dampers to improve low flow control accuracy and perhaps be the source of minimum airflow requirements.

When adequate control air is available, use pneumatic actuators for steam valves and for large valves that would otherwise require 120 VAC actuators.

Two stacked 24 VAC actuators may be used with owner approval for large valves.

Mount electric actuators horizontally to steam and hot water valves.

Approved manufactures of electric actuators...

Approved manufacturer of pneumatic actuators...

Provide actuators with at least 150% of the required torque.

END OF DESIGN INSTRUCTIONS SECTION

GUIDE SPECIFICATION

The following guide specification is to be copied verbatim.  Items to be modified will be decided by consultation between the Architect/Engineer (A/E) and OWNER’S Design Team.  The A/E is expected to modify this and other specifications as necessary to accurately reflect the requirements of the project.

Building automation systems (HVAC Control)

PART 1 GENERAL

SCOPE

Provide an operational control system, including all software and equipment necessary for integrated operation with other facility control systems.

Provide all software and hardware necessary for communication among installed controllers and a Portable Operator’s Stations (POS) which can be plugged into local receptacles.

Provide all software and hardware necessary for communication between all newly installed controllers and existing facility controls.  Vendor is required to provide all miscellaneous parts and labor required in establishing a complete and working system.

GENERAL

- This section includes controls for heating, ventilation, air conditioning systems and interfaces to other systems such as fire alarms.

Quality assurance

    - All materials and equipment used shall be new, standard components, regularly manufactured and not custom-designed or fabricated specifically for this project.

    - All components and software shall have been previously tested and proven in regular use.  Note:   Minimum in-use requirements are 24 months for hardware and 12 months for major software (whole number revision) releases.

Modularity - The HVAC control system shall possess a modular architecture, permitting expansion through the addition of more distributed processing units, input/output units, sensors, actuators and operator stations.

Approval - Vendor shall submit and receive approval for all submittals including materials, floor plan, schematics and programming prior to installation.

1.03	APPROVED MANUFACTURERS

- Provide a HVAC control system with distributed processing units, input/output units, firmware and standard operating software provided by base brand or a completely compatible equal.

    - New equipment and software shall be selected for compatibility with systems presently installed on base.

    - Vendor shall provide all upgrades to allow new controls to work with existing control components.

Design, component selection, installation, custom programming, documentation, testing, training and warranty service shall be the direct responsibility of the manufacturer or their local representative.  These services shall be provided from a business address located within 75 miles of the project site.

1.04	SUBMITTALS

- Schedule of submittals

Submit the point-to-point (PTP) and sequence-of-operation verification test plans at least 30 days prior to the scheduled beginning of testing.  PTP testing shall be part of the construction schedule.

Provide printout of programming code.

    - Show initial setpoints.

    - Provide all documentation necessary to interpret programming related submittals.

Provide sequences of operation detailing all control strategies, including initial setpoints and referencing all points by the point name used in the DDC controls programming.  (These sequences of operation will also be provided in the construction and record drawings.)

Provide a complete set of reproducible control drawings using computer aided design and drafting (CADD) technology.  Include the following information:

    - Show general physical arrangement of component devices installed in the panels.  Indicate applicable detailed drawing reference.

    - Provide a typical schematic drawing of each control circuit.

    - Identify equipment and devices by the reference designations shown on the drawings and by unique point identification used in system software.  Provide material list with or on each drawing.

    - Supply block diagrams and schematics showing riser diagrams, the layout of equipment, communication cabling, and wire type.

    - Provide schematics showing the general mechanical system layout with all sensors/devices of each mechanical system.

    - Supply floor plan drawings showing the location of all controlled equipment and devices used for sensing and control.

    - Provide a schematic drawing of each control circuit, complete with individual wire identifications.  Typical drawings are acceptable.

    - Provide LAN truck riser diagram showing cable routing and location of all repeaters.

Provide a complete list of equipment to be furnished and provide a manufacturer’s catalog sheet for each item on the material list with each specific item clearly identified if the catalog sheet shows several items.

    - Catalog cut sheets shall be clear and legible and indicate item being submitted.

    - Supplement catalog sheets as necessary to fully describe the device being furnished.  Include information to aid the Owner in judging the suitability of each device.

    - Provide a damper schedule with one line per damper.  Provide for each damper:  The project TAG, the size, the model of the damper, the model of the actuator, and whether the damper fails open, closed, or in place.  Indicate whether the actuator is electronic or pneumatic.

    - Provide a valve schedule with one line per valve.  Provide for each valve:  The project TAG, the size, the model of the valve, the pressure rating, the model of the actuator, the valve Cv, and whether the valve fails open, closed, or in place.  Indicate whether the actuator is electronic or pneumatic.

Provide a detailed test plan describing the specific procedures used to complete and document the “Owner-witnessed Testing” described in the Final Acceptance requirement.

    - Test plans shall include a complete schedule for tracking each phase of the testing, e.g. zone testing by floor, fan testing by system, chiller interface testing, heating system testing, etc.

    - The vendor is required to supplement the planned work effort to meet the progress dates given in the schedule.

As part of the submittal process, the vendors shall meet with representatives of the Owner’s engineering and operations divisions, giving them a thorough briefing on the DDC programming design.  This briefing shall describe in detail the methods the control programmer has used to meet the requirements of the sequence of operations.

Submit sizing calculation data for pneumatic air dryer for approval, if used.

1.05	POST-INSTALLATION INSTRUCTION AND MATERIALS

- The manufacturer and Control Contractor shall instruct operating personnel in the operation of the system as follows:

    - Provide a minimum of 8 hours of classroom and on-site training in the operation and maintenance of the installed system.  Hold part of this training prior to point-to-point testing.  Provide each trainee with a copy of the sequence of operations and the graphics during each training session.  Training shall address the following subjects:

Review of sequence of operations

System troubleshooting

Emergency service support

Fire alarm interface

System restart after power failure

Replacement procedures of each system component

Calibration and initialization procedures

Regeneration procedures on all installed programming at operator’s control stations

    - Provide one set of the special tools, reference materials (manuals), test instruments, and software manufactured or modified by the manufacturer for use in the installation, troubleshooting, and repair of installed devices.  Include portable test terminal, test boxes, circuit card extenders, calibration modules, etc.

Provide software for the portable operator’s station as required to perform system maintenance and operation functions.

Owner will provide computer support for the generation of backup database records.  Actual use of computer support is during Owner training for generation of backup database records.

1.06	SYSTEM COMMISSIONING

- Consultant to provide specific language to coordinate this section with any commissioning requirements in other specifications sections.

Vendor shall provide assistance, staff and materials to support the commissioning activities.

    - This includes all testing apparatus in use by the vendor to test and calibrate or verify calibration of the control system and all other apparatus for which the vendor has control or calibration responsibility.

    - Assistance includes but is not limited to reviewing test procedures and providing software enhancements to accommodate testing methods.

Vendor shall provide staff and materials to support the point-to-point testing, also referred to as Owner-witnessed Testing and described under Final Acceptance Requirements.

Operate the control system for any commissioning tests specified in other specification sections.

1.07	FINAL ACCEPTANCE REQUIREMENTS

- Vendor is required to provide the standard numbers and types of corrected documentation to show changes made to correct deficiencies discovered during commissioning tests.  Vendor shall reassemble manuals and drawing packages to reflect corrected documentation records.

Drawings and software

    - Submit shop drawings reflecting final “as-built” condition.

      - Provide record drawings on AutoCAD 2000i or Release 14.  Deliver two copies of data two CDs without compression.

      - Provide 3 copies of reproducible record drawings.

These record drawings shall accurately depict the final as-built conditions and shall be on Architectural/Mechanical backgrounds provided by the A/E.

The Owner will provide a standard template.

These drawings shall include accurate depiction of location of sensors and controlled equipment (motor starters, valves, chillers, dampers, AHUs, etc.)

Insert one copy of applicable shop drawings, panel layout drawing, and points list at each enclosure’s documentation holder.

Furnish one original set of application software on CDs.  Disks shall bear the manufacturer’s label.  Field copies are not acceptable.  Application software includes operating system, controls application generation, graphic support, maintenance support and all other utilities provided in support of the installed system.

    - Operation and Maintenance (O&M) Manuals:  Provide two paper copies of material required and five copies on CDs in MS Word format.  Describe operation, maintenance and servicing requirements of the HVAC control system and associated equipment.  Provide the following information in separate sections, each with an index.

      - Technical literature for all equipment, including catalog sheets, calibration, adjustments and operation instructions, and installation instructions

      - Hardware and software manuals, including information supplied by the original product developer, on the application programs and on the computers and controllers provided by vendor

      - System description and complete sequence of operation

      - Reduced size (11” x 17”) copies of record drawings

      - Input/output (I/O) summary forms for the system, listing all connected analog and binary input and output functions and the number and types of points.  Indicate spare input/output capacity

      - Control programs specific to this system

      - Completed point-to-point checkout plan used in Owner-witnessed testing, and the completed data sheets showing the results of the point-to-point testing.

    - Owner-witnessed testing:  All parts of the testing described in this section are to be performed as point-to-point tests and control sequence verification.

      - The complete local operator station, including all controls software and programming development, shall be installed and made available to support the point-to-point testing and commissioning activities.

      - One copy of the preliminary as-builts (site drawings) shall be provided to support this testing.

      - After receipt of all system documentation by the Owner, notify Owner 10 working days before testing begins.

      - Testing shall be performed by the manufacturer or its local representative, witnessed by the Owner.  The procedure for the test must provide a format for documenting the results, comments, vendor repair activity, vendor’s initials, and retest witnessing.  Provide data sheets with one line for each physical point on the system, and columns to record the results, dates, and initials of witnesses for both pretests and witness tests.

      - The Contractor shall perform point-to-point pretests before the witnessed tests, and shall fill out data sheets during pretests to demonstrate successful performance prior to witnessed tests.

    - Installation verification tests

      - Verify operation, location and identification of power sources, including circuit breakers and control power transformers.

Start/stop points:  Issue start and stop commands from the local operator station (LOS).  Verify that controlled equipment responds appropriately and that the start/stop status is accurately reflected at the LOS.

Analog points:  Analog inputs and outputs shall be verified at both extremes of their ranges and at the midpoint.  Verify tight shutoff and full opening of dampers and valves.

Binary points:  Verify that both commanded conditions (on/off, open/closed, etc.) are accurately reflected at the LOS.

Test fan and pump failure alarms by turning off the motor at the HOA switch and observing the run-state indication at the operator station.

Temperature points:  Verify calibration of sensors by comparing displayed temperature values with the reading of an independent measuring device located in the same flow.   Test liquid temperature sensors as installed in piping thermowells to verify effectiveness of heat conducting compound.

Pressure points:  Verify calibration of sensors by comparing displayed pressure with the reading of an independent measuring device located in the same flow stream.  Retain the services of the balancer as required to confirm readings.

Control valves:  Verify tight shutoff by comparing water or air temperatures entering and leaving the heat transfer device.

Operator response and sequencing:  Demonstrate that sequenced or modulated valves and dampers position accurately in response to posit multiple operators to provide simultaneous modulation of parallel dampers or valve assemblies.

Control signal stability, general:  Demonstrate that control loops are tuned so that the output does not change until the controlled system has had time to respond to the last output signal.

Control signal stability, response to step input:  Demonstrate that control loops are tuned so that they are stable without excessive hunting following a step input of not less than 20% of the operating/reset range of the controlled variable.

Control signal stability, floating point devices:  Verify that minimum pulse output duration is no less than the value required to assure repositioning of the controlled device.

Demonstrate the capability of the controls system to execute the complete sequence of operation as given in the mechanical design documents.

Verify tight shut-off of all actuated control valves (for 3-way valves, demonstrate capacity for 100% by-pass of coil).

    - Local operator station tests

      - Override test:  Verify manual override capability for start/stop and modulated point types.

      - Control logic

        - Exercise all control logic packages.

        - Check response to upset, change in setpoint.

Supervisory function

        - Verify content of time clock schedules.

        - Verify alarm’s reporting capabilities.

Failure modes

        - Verify all stand-alone operation by disconnecting communication lines between stand-alone control units and verifying continued operation.

        - Disconnect and reapply 120 VAC Local Operator Station (LOS) power to confirm proper recovery from power failure.

        - Disconnect and reconnect controller power to confirm proper recovery from power failure (sample

    - Remote operator station tests

      - Verify communication with each field device installed.

      - Verify transmission and reporting of alarms.

      - Verify acquisition of data.

      - Duplicate local operator’s station functions.

Other software tests

      - Trend logging

Report generation

Remote access

Test the ability of the control system to automatically restart all the connected systems which are scheduled to run following a power restoration and fire alarm recovery.

  - SERVICE AND GUARANTEE

- The complete control system shall be warranted to be free of defects in manufacturing, workmanship and materials for one year.  Temperature sensor accuracy shall be warranted for 3 years.  Software and documentation shall be revised to reflect system changes required to meet warranty obligations.

During the warranty period, provide a 24-hour emergency service telephone number where a qualified service technician, familiar with the installed system, may be reached.

    - This technician shall have the capability of remote communication with the control system for troubleshooting and program alterations.

    - The vendor shall pay all costs to provide communications for remote access.

    - A fully equipped, qualified repair technician shall be at the job site within 4 hours of a request for emergency service.

All replacement parts must be available on site within 48 hours during the term of the warranty.

Provide free of charge during the warranty period 2 DDC software sequence modifications as instructed by the Owner.  Modification shall be in software only.

PART 2 - SYSTEM DESCRIPTION

GENERAL

The following requirements are modified by section “Small Scale and Renovation Accommodation” when the DDC point count is less than 100 control/monitor points.

- Provide all software, hardware, input/output devices, wiring and necessary control power if not shown in electrical bid documents, actuated dampers, actuated valves, actuators, operation and maintenance training, special maintenance tools and aids, supervision of labor, and warranty.

- Provide all equipment and software necessary to make three remotely located computers act as operator’s stations.

- Provide all equipment and hardware necessary for communication among distributed processing units and remote operator’s stations via base Ethernet using…

- The system shall be built only of standard components kept in stock by the supplier.

    - All replacement parts shall be available on site within 48 hours.

    - The components shall not require customizing other than setting jumpers and switches, or adding firmware or software modules, or on-site software programming to do required functions.

System display should meet the following requirements:

    - The system is to be fully menu-driven.

    - All system titles, prompts, and instructions are to be in the English language.

    - All entries to be in natural units, i.e., a setpoint value shall be entered in its actual control unit of value, such as 74º F.

    - The primary means of information display and system management shall be by graphic display.

      - System shall be controlled and monitored through a color Graphical User Interface (GUI).

      - Graphical presentation shall group all elements of a system in a clear and logical manner and present on-screen display of system status.

      - Each display will contain comment sections to indicate building area served (if area-specific) and also contain a graphical presentation for all other interlocked systems.

System management shall occur at a dedicated computer.

BASIC SYSTEM FEATURES

- Zone-by-zone control of space temperature, usage scheduling, and equipment failure reporting  (A zone is the area served by one HVAC terminal unit, fan coil, heat pump, air terminal, etc.)

Provide Werner Electric Stabiline UPS (Uninterruptable Power Supply) model SW1500 (or approved equal having 5 year battery life and battery hot swappable capability) for all cabinets having a mounting area over 120 square inches and containing controllers.  These cabinets shall be provided with a fused duplex receptacle to be used a source for UPS power.  Cabinet shall draw power from the UPS.  Provide shelf for UPS.

Totally tamper-proof room sensors installed with Allen, Bristol or similar hardware with no local setpoints.  All temperatures are to be set from an operator’s station or portable terminal.  {Consultant to modify this statement when it is appropriate to include a limited adjustment capability by the occupant.}

Individually assignable priority password security system to prevent unauthorized use.  Provide at least 4 levels including the following:  Information only, change of setpoint & ON/OFF, programmer, and a fourth master level for assigning appropriate local access.

Equipment monitoring and alarm function including information for diagnosing equipment problems.

    - All system points shall be programmed to report alarm conditions by fully expanded point names that are tailored and specific to this project.

    - Assign alarm limits at 20% (user adjustable) above highest expected level and at 20% below lowest expected level (subject to control sequence design) or as requested by Owner.

    - Interlock all alarm points to system status so as to lock out alarms when the system is not operational by schedule or operator command.

Auto-restart, without operator intervention, the operator stations and all controlled equipment to the control state that would be in effect if the power failure or fire alarm event had not occurred.  Start/stop outputs shall continue to command the affected device while motor power is unavailable and allow for equipment restart, as previously commanded or scheduled, upon restoration of motor power.

Equipment run-time totalization of motor driven equipment

Interactive displays of all input and output points:  As a minimum, each of 200 screens on the CRT shall be able to display 25 interactive points and custom text.

Operator may, through keyboard interface, disable any control logic for any output or setpoint, temporarily substitute the value for any input/output, and introduce a different value or state for all inputs, outputs and setpoints.

Individual controllers will be programmed with nonvolatile stand-alone control logic necessary to maintain appropriate HVAC equipment operation.  While in temporary stand-alone mode, energy efficiency can be sacrificed to maintain temperature control and operational conditions that will not damage equipment or compromise health and safety.

Controllers shall, upon loss of valid programming, be capable of requesting and receiving a programming download of all required program code from the local operator control station.

FACILITY personnel shall be able to create and modify control software with an IBM compatible computer utilizing menu-driven programming.  FACILITY personnel shall be able to store the programming on a removable computer disk and preprogram a nonvolatile, transportable memory storage device, which can be used for replacement of the programming in system controllers.

SYSTEM ARCHITECTURE

- The HVAC control system shall consist of a network of controllers providing full stand-alone operation of the building.  The controllers shall contain the necessary programming to accomplish the sequence of operations for building control.

- Controllers shall normally execute the control strategy to use peer-to -peer communication capabilities.  Upon loss of communication, the stand-alone control unit shall be able to execute its own stand-alone programming.  This distribution of control authority is mandated so that the lost communications capability shall not cause a complete loss of control for affected systems.

Operator station shall not be necessary to sustain building operation.

System shall support a logical minimum of 64 operator stations.

OPERATOR STATIONS

- Operator stations shall be IBM compatible ISA bus personal computers selected to meet the specification requirements of the vendor-provided control system software.

- All operator station hardware and software shall be provided, installed and made operational by the control vendor.

- The personal computers shall use the latest Microsoft Windows-type operating system compatible with control vendor applications.

Stations will provide complete facilities for local printing on bubble jet and laser type printers.

Stations will provide complete facilities for loading and archival storage of computer software as well as provide CD ROM Drive facility.

Specification for processor type, speed and memory shall be consistent with those recommended by the software manufacturer.

Station will provide all hardware and software to communicate with remote operator stations over the base Ethernet system using TCP/IP protocol.

Local Operator Station (LOS):  Provides a computer selected to meet all specifications for operation of control system software and provide additional unused disk store space for operational requirements such as trending and totalization.  Disk storage shall be no more than 20% utilized by the initial installation.

Remote Operator Station (ROS):  Vendor to upgrade two existing remote operator stations as necessary to communicate with the local operator station over the base Ethernet system using TCP/IP protocol.

Portable Operator Station:  Provides one “lap top” computer capable of operating all vendor-supplied field maintenance programs.

CONTROLLERS

- Each controller shall operate as part of the building-wide control system and as an independent unit when not in communication with other controllers or an operator station.  Global controllers shall be able to share Global information on a peer-to-peer basis without relying on an operator station.

- It shall be possible to define control strategies at each controller from any operator station.  Each controller shall be able to interface directly with an operator station.

- Each controller shall include its own microprocessor, power supply, and, if necessary, battery with automatic charger.  Upon loss of system power, the controller memory shall be maintained for a minimum of 60 hours with no external source of power.  Upon restoration of system power, the control unit shall resume full operation without operator intervention.

- Provide control programming logic at each controller for proportional and/or proportional plus integral control capabilities as necessary to assure complete and stable control of each controlled variable.

2.06	CONTROLLER FUNCTIONALITY

- Each controller shall maintain and perform its own stand-alone control strategy upon communications failure.  The controller stand-alone control program shall be adequate to maintain the basic control function and provide protection from inappropriate equipment operation.  The controller shall retain its programming during a power failure and resume operation without program reloading from another device.

- The controllers shall be powered by 24 VAC.

- Each controller shall be isolated (optically or by other means) from communication trunk and have fuse or overload protection.

- The controller point monitoring and control capabilities shall include but not be limited to the following:

    - Binary inputs (contact closures)

    - Analog inputs (use only resistive, 0-10 volt, and 4-20 ma. inputs; provide A/D conversion of 10 bits, minimum)

    - Binary output (start/stop or latching and momentary contacts)

    - Floating point control

    - Analog outputs (must include 4-20 ma. @ 10 VDC minimum, 0 -10 VDC; provide A/D conversion of 12 bits, minimum)

2.07	FAILURE MODE

- Upon failure of any global controller, the operator station shall display off-line occurrence for each affected point, and provide communication verification to each controller for each I/O channel.

- In the event of communication failure, controller shall continue to operate equipment using appropriate backup values for missing global information.  If sensor information is necessary for proper stand-alone function, then that sensor shall be attached directly to the appropriate controller.  Provide failure mode programming to accomplish safe operation of equipment in case of communications failure on local trunk.

- Upon return of primary power after a power failure of up to 72 hours, the system shall automatically return to completely normal operation with no action required from operating personnel.

Unless otherwise indicated in the design documents, provide the following failure modes, (that is, the position that the controlled device attains under failure due to loss of power, loss of air pressure, or loss of communications) for valves and dampers:

    - All heating converter steam valves shall fail closed.

    - All fan preheat steam valves shall fail open.

    - All Fan and unit heating hot water heating valves shall fail open.

    - All Fan cooling water valves shall fail closed.

    - All central cooling water differential pressure control valves shall fail closed.

    - All fan exhaust air and outside air dampers shall fail closed.

    - All fan recirculation dampers shall fail open.

    - All fume exhaust control and fan isolation dampers shall fail open.

    - Zone-level air terminal unit hot water valves and dampers, unit heater hot water valves, and perimeter hot water heater valves may fail in place.

EP transducers shall be selected so that valves and dampers go to the above-listed failure positions on loss of power.

2.08	ENERGY REDUCTION AND SPECIAL OPERATION SOFTWARE

- The system shall be designed to control energy-consuming loads.  Provide engineering, consulting, and programming to develop and set up the following energy reduction software:

    - Time schedules:  Software should provide at least 16 time schedules.  Each schedule is to be an 8-day type, capable of 6 entries minimum per day.  Time program shall provide ON/OFF commands, and reset SETPOINT capabilities.

    - Holiday time programs:  Provide a holiday time schedule capability.

    - Optimal start/stop:  Provide the ability to optimize start/stop times to attain and maintain temperature setpoint only during occupied times.  The system shall be self tuning, with compensation for weekends and holidays.

    - Setpoint reset:  Provide a means of automatically resetting water and ventilation air temperatures, volumes and pressures based on the prevailing minimum needs of the facility with a primary focus on terminal units.

    - Parallel variable speed motor operation:  Provide sequences of operation that minimize energy consumption for multiple fans, pumps, chillers, etc that can operate in parallel at reduced speed for part of their operating hours.

    - Provide a program to automatically restart all DDC controlled equipment upon the resumption of power or return from fire alarm condition.  Equipment shall be restarted according to a prearranged, prioritized and staggered restart schedule.

    - For loads that have been turned off at the MCC controller, either by positioning of the HOA switch or the line disconnect; provide a restart strategy that automatically restarts load upon the reset of switches to their normal on-line positions.

    - Provide global command software to support balancing work including, as a minimum, single command authority to command all terminal units and zone reheat valves to their full open position.  Provide single command authority for return to normal operation.

    - Provide capability to adjust the setpoints of main mechanical systems from the operator station using simple ‘point and click’ command windows.

2.09	ALARM PROGRAM

- For each analog input point, assign operator high and low alarm limits according to design data or as Owner requests.

For each alarm input, provide the following assignable alarm responses:

    - Display English language point description in addition to system point identification.

    - Print out alarm description and operator-created alarm message.

    - Require acknowledgment by operator and print occurrence if directed by Owner.

2.10	LOGS

- Trend log:  As a minimum, provide capacity for 50 trend logs.  Store time segments.  Provide for review of data on monitor and printer.  Each trend log shall have assignable individual start/stop times/dates.

- Current alarm log:  Display all points currently in alarm.

- Operator activity log:  Record operator activity by operator account identification and work performed  during a minimum of the last 10 log-in sessions or last 20 commands.

2.11	SENSORS

- Temperature sensors

    - Sensors shall be completely precalibrated with no electrical adjustments or calibration required for standard installation conditions.

    - The temperature displayed at an operator terminal shall be accurate to within 1º F.  This accuracy shall be warranted (parts and labor) for a minimum of 3 years.

    - Wall sensors shall be housed in tamperproof enclosures installed with Allen, Bristol or similar mounting hardware.  Wall sensors for zone controls shall provide jack for operations laptop connection.  That connection shall allow communication with system for monitoring and adjusting at least the zone-level equipment serving that zone.

    - Freeze protection sensors shall be non-averaging.

    - Thermowells shall be bronze, brass, or stainless steel with 1-inch NPT threads.

    - Install piping temperature sensors adjacent to temperature gauge or test port.

Use heat-conducting compound.

Mount and shield outside air sensors so as to avoid solar influence.

Mount outside pressure reference sensors so as to eliminate wind effect.

Air velocity transmitter:  Shall provide air velocity information independent of the effects of static pressure.  Transmitter shall operate at rated accuracy from 0º F to 120( F.  The minimum accuracy of displayed value at an operator terminal shall be 95% through the range of 20% to 100% of sensed airflow, with a drift rate no greater than 1% per year.  The proportional output shall be 4 to 20 ma.

Humidity transmitter:  Shall be of the solid state type using a hygroscopic sensing element.  The sensor shall operate from 40( F to 100( F.  The minimum accuracy, as displayed at an operator terminal, shall be 95% through the range of 10% to 95% RH, with a drift rate no greater than 1% per year.  The proportional output shall be 4 to 20 ma.

Differential and static pressure transmitter:  Transmitter shall operate from 50% of minimum to 150% of maximum anticipated pressure.  The maximum error of displayed value at an operator terminal shall be 2% through the range of 20% to 150% of the intended maximum setpoint.  Minimum pressure tolerance shall be 150% of the maximum pressure expected in normal operation.  The maximum drift rate shall be no greater than 1% per year.  The proportional output shall be 4 to 20 ma.  Provide designed pressure pitot sensor Dwyer type A-301/A 302 or approved equal.

Freeze protection thermostat

    - Provide DPDT contacts.

      - One set of contacts shall be wired directly to controlled mechanical equipment contactor/ASD in order to affect both automatic and manual (HOA) switch positions.

      - The second set of contacts will be wired to a digital input for annunciation of freeze protection alarm condition.

    - Manual reset type is required.

      - Locate the reset head outside the plenum wall.

Current sensors shall convert AC to proportional DC (4 to 20 ma).  Response time:  300 milliseconds to 99% of final value.  Manufacturer:  Neilson-Kuljian or approved equal

AC relay shall indicate the presence of current flow.  Device to be powered by induction from the line being monitored.  Manufacturer:  Veris Industries series 700 and 900 or approved equal

Averaging elements shall be mounted so as to cross a minimum of 80% of the plenum width and shall be located so as to provide an indication of temperature within +/- 1( F.  Provide support at 36 inches maximum.

Outside air sensors shall be a waterproof assembly protected from solar radiation.  Span shall cover the range of – 30º F to 100( F or better and not exceed a 150( F span.

2.12	CONTROLLED DEVICES

- Actuators

    - Actuators for steam valves and actuators located in mechanical rooms shall be pneumatic.  Air distribution system air terminal (zone) box damper and valve actuators and perimeter hot water heater valve actuators may be electronic.

    - Provide pneumatic actuators selected from the standard vendor catalog.

      - Provide in sufficient size, quantity and type to assure reliable operation throughout the normal aging process of valves and dampers.

      - Full stroke actuation of pneumatic actuators shall not be more than 30 seconds.

    - Large damper assemblies shall be made of individually driven segments that are small enough to ensure reliable operation and uniform closure across the entire damper assembly.  If electronic actuators are used, they shall be operated independently so that if one damper segment or actuator becomes inoperable, the others remain operable.

    - See the failure mode section above for actuator responses under failure due to loss of power, loss of control air, or loss of communication.  Where an actuator is to fail open or fail closed, provide spring return.  Actuators shall not be dependent on batteries or capacitors to stroke to the power fail position upon loss of power.

    - Permanently stamp or scribe position indication on the end of driven shaft unless damper is visible from same location as end of shaft.

    - Select electronic actuators from the vendor standard product line.

      - All electronic actuators shall be 24 VAC.  The use of any other actuator must be approved by the Owner.

      - Proportional electronic actuators shall use 0 to 10 VDC, 4 to 20 ma. or floating point control.

      - Multiple electronic actuators may be powered by one separately fused 24 VAC transformer, providing the transformer size does not exceed 100 VA.

      - Electronic actuators may be stacked no more than two units high.

    - Actuated dampers

      - Provide low leakage control dampers where not furnished with packaged units.

      - Damper leakage rate shall not exceed 6 CFM/sq. ft. at 4-inch wg. and 1% of full flow rate.

      - Dampers shall have blade seals and stops.

      - Provide American Warming and Ventilation, Ruskin, or approved equal dampers.

    - Install actuators in the orientation recommended, or stated as preferred, in manufacturer’s literature.

    - For actuator selection, see "Failure Mode" requirements, above.

Actuated valves

    - Valves shall be selected to meet CV and pressure requirements.

      - Valve body and actuator selection shall be sufficient to handle system pressure, and shall close against the system differential pressures.

      - Valve service rating shall be 125 psig. or greater as needed.

      - All electronic valve actuators shall have field manual positioning capability to allow manual positioning of valve in absence of control power.

      - The shafts to which the actuators are coupled shall be square or hexagonal or round with one side flattened to permit secure coupling.

      - Install valves in the orientation recommended, or stated as preferred, in manufacturer’s literature.

    - Use 2-way valves and actuators directly marketed and warranted by the controls vendor.  Third party and after-market devices will not be accepted where the vendor’s catalog shows appropriate devices.

    - All Modulated valves shall be pressure independent and use actuators provided and warranted by the valve manufacturer.  Use Belimo, Flow Control or approved equal valves.

    - Zone valves:  Valves shall be constructed with a cast brass body.  The valve shall provide for 100% shut-off and silent operation.

    - AHU valves:  Valves shall be constructed with cast brass or iron body and screwed or flanged ends.  Valves to provide a full open pressure drop within 25% of the pressure drop through the coil at full design flow.

Control relays

    - Panel relays shall be plug-in type with contacts rated at twice the amperage rating of circuit requirements:  Minimum temperature range –25º C to +70º C.

      - Enclosure:  Clear dust cover and shock resistant, rated for minimum of 2.5 million mechanical operations and 100,000 electrical operations at full load.

    - Remote/interposing relays shall be used for all remote switched loads.

      - They shall be housed in a NEMA-rated enclosure.  Where two or more relays are mounted in the same enclosure, provide a hinged cover.

      - Besides meeting panel relay requirements, they shall have 24 VDC coils and form C dry contacts with a minimum rating of 5 amps @ 240 VAC.

      - Relays controlling inductive loads shall be equipped with coil transient suppression devices to limit transients to 150% of rated coil voltage.

2.13	ENCLOSURES

- All enclosures to be NEMA 1, unless otherwise required for intended service.  All controls and instruments shall be logically assembled at one or more panels, have hinged doors and be marked with engraved melamine labels.

- All enclosures used as a mounting site for control devices shall also contain a documentation holder located on the inside of the door.

- All enclosures shall be provided with locks.

- Label each equipment panel furnished with 120 VAC power with power source label showing identification of power panel and breaker.

2.14	WIRING AND CONDUIT

- Install wiring and conduit in accordance with Division 16 requirements.

- Minimum wire size shall be 10 Ga. for ground, 12 Ga. for 120 VAC power, 14 Ga. for actuator power, and 16 Ga. for switched output.  Single conductor wire insulation shall be THHN.  All wires shall be sized in accordance with the NEC for the load serviced.  A single conductor shall not be used for more than one leg of an input or output device circuit (no “common” conductors) unless approved by Owner.

- All wiring shall be stranded.  Exceptions will be made for wiring used in preassembled factory crimped cables, 20 g and smaller, where connectors provide support to the insulated cable jacket at the point of connection.

- Junction box covers shall be labeled “DDC” or show the vendor logo.

- Splicing shall be accomplished by a fully insulated crimped barrel connector.

- Conduit shall be cleaned of foreign material just before pulling the wire or cable.  Lubricants shall be compounds specifically prepared for cable pulling and shall not contain petroleum or other products that will affect cable insulation.

- Wire that has scrapes, nicks, gouges, or crushed insulation shall not be used and shall be removed when present.

- Groups of conductors, where installed in cabinets and wire trays, shall be neatly grouped with wire ties or equal.

- All wiring contained in metal wireways shall be in wireways dedicated to low voltage service.

- Low voltage energy-limited wiring shall not be run in the same wireways with, or closely parallel to, high voltage or switched power wiring.  Interposing relays shall be used for all switched power loads and shall be located so that the switched power conductors do not run in the same wireway as the interposing relay coil power or any other energy-limited low voltage conductors.

- All wire shall be new and brought on the jobsite in original packages bearing Underwriter’s label and the date of manufacture.

- Aluminum wire is prohibited.

No conduit shall be filled so that the maximum bundled cross sectional dimension exceeds 40 % of conduit inside diameter.  No raceway shall be filled to more than 40% and maximum fill for “wiremold” (surface raceway) shall be 20%.

No wire run or circuit shall be longer than 80% of the maximum allowable length or power consumption for the wire size and application.  No output circuit shall exceed 80% of the maximum load capacity specified by the manufacturer.

Wiring and conduit shall comply with Division 16 specifications.

    - The basic wiring method shall be in conduit unless otherwise permitted in this section.

    - Where conduit direct connection is not possible, all permitted open wiring shall be plenum rated.

    - Permitted open wiring is limited to the following applications:

      - Wiring from a zone airflow control unit to a nearby temperature sensor not to exceed 50 feet

      - Wiring from a zone airflow terminal control unit to a nearby water control valve not to exceed 6 feet

Wiring from any controller to a device which has otherwise been approved for installation and cannot accept conduit connection shall meet the following requirements:

    - Conduit shall be used to within 12 inches of the device.

    - Install in wireway all trunk communication wiring between the operator station and the controllers, and between controllers.  Open wiring is not otherwise permitted.

Conduits shall be provided with appropriate bushings and end fittings to protect cabling from sharp conduit edges.

Conduit size shall be ¾-inch minimum for all wiring groups consisting of 6 or more conductors.  NEC requirements shall apply as though conductors were used to their full current carrying and thermal capacity.

Wireway runs shall be parallel or perpendicular to walls, pipes and sides of openings.  Passageways for access and servicing shall not be blocked.

All trunk or LAN cables shall be 100% backed up with spare conductors.

All conductors that become bundled or pass from an enclosure shall be identified with typed or machine lettered labels, Briade or approved equal.  Tag numbers shall agree with wire numbers assigned on wiring diagrams and the installation drawings.

Wires shall be labeled with mechanically prepared labels at their connection point to each apparatus point of connection.

Open wiring, when permitted, shall be installed in compliance with WAC 296-46-725 with reference to NEC 336-15 and shall also be installed as follows:

    - All open wiring that penetrates through walls and crosses structural ceilings shall do so within 18 inches of the structural ceiling surface.

    - Wiring shall be attached to vertical supports at attachment points prepared by a protective wrap of electrical tape around the support.  This wrap shall create a surface free of sharp edges.

    - Absolutely no wire is to be attached to pipe work or conduit of any kind.

    - Wire ties, if used, shall be trimmed so as to reduce sharp edges.

    - The vendor shall provide required cabling attachment points for control’s use if the ceiling structure does not provide acceptable attachment points.

2.15	DEVICES INSTALLED BY OTHERS

- Under the vendor’s guidance, the Mechanical Contractor shall install controlled valves and dampers, thermowells, and pressure taps with isolation valves.

2.16	INSTALLATION STANDARDS AND DEVICE TAGGING

- These standards supplement other guidance found outside this control specification and within sensor specification.  In case of conflict, the issue shall be brought to the attention of the Architect, who will make a decision.  All work shall comply with the NEC (National Electric Code) as adapted by the City of Seattle, and with the WAC (Washington Administrative Code) section 296-46-725.

The DDC control system described here shall only control equipment while the HOA switch is in the Auto position.  Where equipment is controlled by both the fire alarm system and DDC controls, separate start/stop contacts shall be provided, and the fire alarm system shall always override the DDC controls.

The freezestats used on fan shut-down control shall be wired to stop the fan in both the Auto and Hand positions of the HOA switch.  Freezestats shall be overridden by the fire alarm controls.

Wall mounted temperature sensors shall be mounted on electrical boxes, and all wire penetrations shall be sealed to prevent thermal convection.

It is the responsibility of the controls vendor to ensure that all sensors are placed in the measurable flow path so as to accurately measure the sensed variable.  As a minimum, water flow sensors shall be installed with a straight section of piping 10 diameters upstream and 4 diameters downstream.

Sensors installed for outside air measurement and pressurization shall be located to optimize the accuracy of the measurement.  Coordinate with Mechanical Consultant.

Valve operators shall be installed directly above the controlled valve whenever possible (with the exception of steam control valves where actuator is rotated to about 30 degrees to avoid hot zone directly above valve) unless rotation is needed to permit maintenance access.  However, in no case shall the operator be rotated to or beyond horizontal.

Freezestats shall be installed with capillaries supported by non-metallic standoffs.  No part of the capillary shall otherwise touch the coil or frame.

    - Provide mounting support for the capillary at least every 36 inches and at the capillary end, within 6 inches.

    - Freezestats shall be mounted to the upstream face of the first coil that they are designed to protect, usually the cooling coil.

    - Locate reset head on outside of plenum wall.

Freezestats’ capillary length shall provide 1 foot of capillary for each 4 square feet of coil surface (by multiple freezestat units if necessary to meet this requirement).  In all cases the coil face shall be completely crossed from corner to corner, with the freezestat control head mounted at the highest capillary point to maintain calibration.

Terminal unit and fan coil unit discharge temperature sensors shall be mounted a minimum of 36 inches downstream from the coil.

All devices shall be mounted within enclosures.  Cable trays and external cabinet surfaces shall not be used as mounting surfaces.

Proof of run for both fans and pumps shall be by current sensing devices rather than differential pressure switches.

All pressure indicating/measuring devices shall be installed with capped tee devices to permit attachment of test meters.

Except for steam valves, and space permitting, install valve bodies in the vertical plane with the actuator above the valve body.  This orientation is preferred to minimize valve packing ware.

2.17	SPECIAL DESIGN STANDARDS

- The pneumatic operator’s air supply system shall be sized and piped to operate the driven load with full stroke time not to exceed 30 seconds.

    - Operation of multiple supply boxes in a single zone presents special problems.

      - If multiple boxes must be controlled from a single sensor, mixing box discharge temperature sensors shall be used, and their closed loop control shall be reset from the zone sensor.

VAV terminal boxes used in configurations of multiple supply and/or multiple exhaust units need to have their flow rates synchronized to ensure airflow rates are appropriate and repeatable.  Control vendor shall accomplish synchronization through positive feedback of the damper position or by commanding the damper position with an analog signal (or other appropriate means).

If alternation of lead-lag motors or services is made possible by design requirements, lead-lag scheduling shall be by operator command and shall be initially set to ‘No Alternation.’

Provide a minimum 1¼-inch pressure gauge at the output of each I/P and E/P transducer.

2.18	GRAPHIC DISPLAY REQUIREMENTS

- Provide a Microsoft Windows-based software package for the preparation of system graphics.

- Include with this software a library of HVAC symbols such as fans, pumps, chillers, etc.

- This section establishes standards for graphic displays as follows:

    - All non-portable operator stations shall be programmed to display dynamic color graphic representations of the mechanical systems and floor areas for which this system has control.

    - Systems to be displayed include the air handlers, air terminal units, chillers, heat converters, pumping systems and similar mechanical devices.

    - Show the following components (if included on a project) on a single graphic:  Chilled and condenser water pumps, cooling towers, chillers, central cooling water (CCW) differential pressure control valves (header), heat exchangers between the CCW system and the condenser water, and the status indicator for whether the two systems are in their “summer” or “winter” mode of operation.

    - Displays shall automatically update with current real time data.

    - Floor plan displays are required and shall indicate the approximate positions of controlled mechanical system elements.

    - Room floor plan displays are required if rooms are served from more than one terminal unit.  Show the approximate location and orientation of the terminal units.

    - All displays shall show real time data to include temperatures, actuator positions, and motor run status.

    - All system input, output and setpoint points shall be displayed on an appropriate graphic.

2.19	SMALL PROJECTS

Designer:   Delete this section for large projects.  For small projects, use the following information to modify other specification requirements as noted in the text.  This section modifies the requirements of other sections if the scale of the project is less than 100 control or monitored points.

- The requirement for a dedicated computer (as indicated in section 2.01 D), as the point for system management does not apply.  It shall be possible to attach a portable computer to the main system controller for the purpose of system management.

- Requirements for operator stations do not apply except for the specification on portable operator stations.

- Alarm log requirements do not apply except for the current alarm log and a reduced trending requirement of 10 trend logs.

- Section 1.05 	POST INSTALLATION INSTRUCTIONS AND MATERIALS - TRAINING is modified as follows:

    - Subsection 1.05  A. 1:  Training requirement of 32 hours is reduced to 8 hours.

    - Subsection 1.05  A. 2:  Training requirement of 16 hours is reduced from 16 hours on a total of 4 occasions to 4 hours on a single occasion.

    - Subsection 1.05  A. 3:  Training requirement for 2 employees is reduced to 1 employee, and the use of a local trainer at the local facility or project is permitted.

Section 1.07 FINAL ACCEPTANCE REQUIREMENTS makes reference to a Local Operator Station.  This reference is amended to be the existing Master Operator Station.

Section 2.01 SYSTEM DESCRIPTION, GENERAL:  Paragraph A is amended to require remote communications by modem, or by local proprietary link to an existing control system, in itself already in communication to a remote site via base Ethernet, which can act as a communications relay device.  If an existing relay site is used, vendor shall pay all costs to upgrade and configure such site for support of this project.

2.20	PNEUMATIC AIR SYSTEMS

- Pneumatic air piping shall conform with the following:

    - Copper tubing:  ASTM B88, hard drawn deoxidized copper tubing, type L, with wrought copper solder joint fittings conforming to ANSI B16.22

    - Plastic tubing:  Virgin polyethylene tubing, FR rated, tested in accordance with ASTM D-1693 standards with minimum burst pressure of 600 psig and minimum working pressure of 100 psi at 75º F

Pneumatic copper tubing shall be run parallel to building lines.  Create tubing bends with formed pieces or with the use of a tubing bender.

Tubing shall be attached to the building structure at no greater than 4-foot intervals.

Copper tubing shall be ¼ inch o.d. minimum in all locations.

Polyethylene tubing is permitted inside panels and for final connection (not to exceed 6 inches) to devices that are designed with barbed fittings.

PART 3 - SEQUENCE OF OPERATION AND POINTS DESCRIPTION

3.00	DESIGN STATEMENTS

- Design Sequence of Operation appears on the mechanical design drawings.  Supplement in controls sequence of operation statements to explain how the control system programming and architecture accomplishes the design intent.

3.01	GENERAL

- Program as a minimum the following:

    - Control of equipment as described in the design sequence of operations

    - Time and holiday schedules

    - Alarm limits and histories

    - Summary of data for each zone

    - Trend logs and historical data

    - All setpoints

    - Master menu

    - Dynamic color graphic Interface

Provide all control sequences as shown on the control diagrams and described here using direct digital control.

Provide all programming as required in Section 2.08 ENERGY REDUCTION AND SPECIAL OPERATIONS SOFTWARE

3.02	SPECIFIC REQUIREMENTS

- The following Points Descriptions and Sequences of Operation shall be enhanced as necessary and included as part of the control drawings to expand and clarify information shown in the drawings.

    - Points information shall be displayed and organized by system in dynamic graphic form at the operator stations.

    - The energy reduction software and miscellaneous functions shall manage all points.

    - It shall be possible to “disconnect” any output or setpoint from the AUTOMATIC control logic and enter a MANUAL value or state from any Operator Station.

    - It shall be possible to replace any input with a MANUAL value from any Operator Station.

    - All control loop parameters for each loop shall be displayed on one display.

3.03	MINIMUM POINTS—DISPLAY AND PROGRAMMING REQUIREMENTS

- The following commands, displays and data shall be available at the operator terminal:

    - Air handling unit

      - Fan status (current sensor proof)

      - Outside air temperature

      - Mixed air temperature

      - Supply air temperature

      - Return air temperature

      - Coldest and warmest zone, all zones sampled

      - Duct and space static pressures

      - Freeze protection status

      - Alarms (temperature, airflow, pressure)

The following points, numbered 1 through 3, are only required if needed by control strategy:

    - Directly measured total supply airflow (CFM)

    - Directly measured total return airflow (CFM)

    - Directly measured minimum outside airflow (CFM)

The following points shall be displayed using calculated values based upon commanded position unless exact values, as indicated by a feedback signal, are required by control strategy:

    - Fan speed (per cent of full speed)

    - Damper positions (per cent of full open)

    - Heating and cooling valve position (per cent of full open)

Hot water steam converters and pumps

    - Status of pumps (current sensor proof)

    - Supply and return temperature

    - VFD Speed/Status

    - Valve positions (per cent of full open) (A calculated value not requiring feedback)

    - Differential pressure (if used)

Air terminals

    - Current space temperature

    - Occupied heating/ventilating setpoint

    - Unoccupied heating/ventilating setpoints

    - Current status (heating/ventilating)

    - Current mode (day/night)

    - Minimum and maximum airflow setting (CFM)

    - Current primary airflow reading (CFM)

    - Valve position (per cent of full open) (Water - a calculated value not requiring feedback)

    - High/low temperature alarm

    - Input and software capacity to add local temperature adjustment and push button timed override from the space temperature sensor

Chilled Water System

    - Supply and return temperatures

    - Entering and leaving temperatures (if different from above)

    - Supply temperature reset

    - Pump status (current sensor proof)

    - Chiller status

    - High/low temperature alarms

Central Cooling Water (CCW) System

Consultant should refer to the standard drawing under Mechanical - Central Cooling Water for more detail about control of that system.

    - Temperature and pressure of CCW supply water coming into the building at the header

    - Temperature and pressure of CCW return water leaving the building at the header

    - CCW supply pressure at the CCW header discharge

    - Summer/winter mode status

    - Entering and leaving water temperatures for the heat exchanger between the condenser water to CCW

    - CCW flow (if there’s a CCW meter)

Metering:  Steam

    - Output from condensate or steam meter

Special monitoring and control:  Provide for the following DDC I/O points:

Name					Type

a.  Fire alarm status				Binary Input

b.  Cascade Lighting Control			Binary Output

c.  Emergency Power Switch Pos.		Binary Output

Note:  Review on a project-by-project basis whether it is desirable to monitor the lighting controls.

3.04	SEQUENCE OF OPERATION

- Refer to mechanical design drawings.  Control vendor shall develop a controls version of the sequence to show how the controls programming implements the sequence provided in the mechanical design.  Include controls sequence of operations in submittals.

PART 4 – INTERFACE WITH OTHER SYSTEMS AND EQUIPMENT

4.01	INTERFACING TO FIRE ALARM SYSTEMS

The building DDC control system shall monitor the actual run status of each controlled fan and provide all air volume and static pressurization control without regard to the source of the run signal.  Fans can be called to a run state by several separate and independent means, including directly from the Fire Alarm Control Panel (FACP).

Controls vendor shall coordinate with the motor control center designer and fire alarm controls vendor in the design of the DDC interfacing to these systems.

  - INTERFACING WITH DEDICATED CONTROLS

- Coordinate with dedicated controls that interface with DDC system.

END OF GUIDE SPECIFICATION SECTION