SERIES 75 CONTROLLER

Specifications

Power 		120VAC- 240VAC, 50/60 Hz, +10/-15%, 2.5 watts    Input power is auto selected.

Inputs: 		3 switch inputs, selectable normally open or normally closed

Outputs:	RO pump 1HP* max,  Inlet solenoid 5A, 20A maximum total load   *Based on service factor of 1.0

OPERATION

When the power switch is turned ON, the center status LED will flash Green, the inlet valve will OPEN and the RO pump will START. The center LED will be solid Green for normal run.

Under normal operation the RO unit will run until: (A) the storage tank is full (left status LED Amber) or (B) Pretreat lockout has occurred (center status LED Flashing Green).  When A or B has cleared, after a time delay, the RO unit will restart, and the status LED will return to Green.  Switch setting 3 selects a 2 second or 15 minute tank full restart time delay.

Upon an alarm signal for Pressure Fault, the left status LED will flash Red, the RO pump will stop and the inlet valve will close and the RO pump will turn OFF.

If switch 1 and 2 are in the OFF Position (disabled), the left status LED will be a steady RED and the RO will not restart until the Power Switch has been manually cycled OFF then ON to reset the unit.

If switch 1 is in the ON Position (auto reset), every 60 minutes the RO will start and stop again if a pressure fault continues.

If switch 2 is in the ON Position (pressure fault retry), the RO will attempt to restart after 30 seconds, then 5 minutes, then 30 minutes.  If the pressure alarm has not cleared after the third try, the RO unit will remain off until manually reset.

If switch 1 and 2 are in the ON Position, after a pressure fault condition, the RO unit will continually attempt to restart after each 60 minute cycle, until the pressure switch input has cleared.

If switch 5 is in the OFF position, Flush is disabled, in the ON position, Flush is enabled.

If switch 6 is in the OFF position, the unit will flush on Tank Full.  In the ON position, flush is every 24 hours elapsed time.

Flush time is 5 minutes. The Amber Flush LED with flash.

Switch 4 is for switch inputs.  OFF is for N.O. contacts. ON is for N.C. contacts.

Installation

1.  The RO pump motor or motor starter and the solenoid valves must be of the same voltage 120 or 240 volt.

2.  Confirm that the (3) input signals - pressure switch, tank level switch and pretreat switch are all of the

same configuration, normally open or normally closed.

3.  Confirm the desired switch settings for your operation.  The switches are factory set to the OFF Position: Auto

Reset (disabled), Pressure Fault Retry (disabled), Tank Full restart time delay (2 seconds), Input contact

type (NC, open to operate).  If you desire to change any switch functions, move that switch to

the ON Position.  [See Table 1, Switch Selection].

4.  Wire to the controller as follows:

A. Remove the enclosure cover.

B. Mark and drill necessary electrical entry holes in the empty enclosure.

C. Terminate necessary wiring to the Quick Connect terminals as required (See Fig. 1).  Each terminal is

labeled for the proper connection.  Terminals P1-P9 are high voltage for power, motor, inlet and flush solenoid.

Utilize proper 3 conductor  wire size for the appliance.  CAUTION:  The controller is rated for maximum

20 amp total load.  Terminal strip P11is dry contact for input signals from tank full, pressure fault and pretreat

lockout.  Use small gauge 2 conductor cable for these wire connections.

5.  Position and mount the enclosure in the desired location.

6.  Connect all wiring to the appropriate appliances (Do not connect to the power source at this time).

7.  Reassemble the enclosure, be sure to coil and leave some slack wire inside the enclosure.

8.  Connect the power wire 120- 240 volt to its source.

9.  Proceed to push the power switch ON and test the completed unit as necessary.

10.  Notice the status LED to confirm system status.

R & D Specialties, Midland, TX., USA 06/2012