本文档下载自文档下载网，内容可能不完整，您可以点击以下网址继续阅读或下载：

http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949

PCS-9611_Instruction_Manual_EN

PCS9611

Management Relay

Manual

Nari-Relays Electric Co., Ltd.

[此处图片未下载成功]

PCS-9611 Feeder Management Relay

guide and the relevant operating or service manual documentation for the equipment provide full information on safe handling, commissioning and testing of this equipment.

for equipment ordered from NARI-RELAYS is dispatched separately from manufactured goods and may not be received at the same time. Therefore this guide is provided to ensure that printed information normally present on equipment is fully understood by the recipient.

carrying out any work on the equipment the user should be familiar with the contents of this manual, and read relevant chapter carefully.

chapter describes the safety precautions recommended when using the equipment. Before installing and using the equhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ipment, this chapter must be thoroughly read and understood.

and Safety

information in this chapter of the equipment documentation is intended to ensure that equipment is properly installed and handled in order to maintain it in a safe condition.

electrical equipment is in operation, dangerous voltages will be present in certain parts of the equipment. Failure to observe warning notices, incorrect use, or improper use may endanger personnel and equipment and cause personal injury or physical damage. Before working in the terminal strip area, the equipment must be isolated.

and safe operation of the equipment depends on appropriate shipping and handling, proper storage, installation and commissioning, and on careful operation, maintenance and servicing. For this reason only qualified personnel may work on or operate the equipment. Qualified personnel are individuals who:

://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 Are familiar with the installation, commissioning, and operation of the equipment and of the

to which it is being connected; z Are able to safely perform switching operations in accordance with accepted safety

practices and are authorized to energize and de-energize equipment and to isolate, ground, and label it; z Are trained in the care and use of safety apparatus in accordance with safety engineering

; z Are trained in emergency procedures (first aid).

NARI-RELAYS ELECTRIC CO., LTD i

Feeder Management Relay

[此处图片未下载成功]

and Warnings

following indicators and standard definitions are used: DANGER

that death, severe personal injury, or considerable equipment damage will occur if safety precautions are disregarded.

means that death, severe personal, or considerable equipment http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949damage could occur

safety precautions are disregarded. CAUTION means that light personal injury or equipment damage may occur if safety

are disregarded. This particularly applies to damage to the device and to resulting damage of the protected equipment.

[此处图片未下载成功]

WARNING!

firmware may be upgraded to add new features or enhance/modify existing features, please make sure that the version of this manual is compatible with the product in your hand.

[此处图片未下载成功]

WARNING!

operation of electrical equipment, certain parts of these devices are under high voltage. Severe personal injury or significant equipment damage could result from improper behavior. Only qualified personnel should work on this equipment or in the vicinity of this equipment. These personnel must be familiar with all warnings and service procedures described in this manual, as well http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949as safety regulations.

particular, the general facility and safety regulations for work with high-voltage equipment must be observed. Noncompliance may result in death, injury, or significant equipment damage.

[此处图片未下载成功]

DANGER!

allow the current transformer (CT) secondary circuit connected to this equipment to be opened while the primary system is live. Opening the CT circuit will produce a dangerously high voltage.

[此处图片未下载成功]

WARNING!

Exposed terminals

not touch the exposed terminals of this equipment while the power is on, as the high voltage generated is dangerous z Residual voltage

voltage can be present in the DC circuit just after switching off the DC power supply. It takes a few seconds for the voltage to discharge.

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

PCS-9611 Feeder Management Relayhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949

!

Earth

earthing terminal of the equipment must be securely earthed z Operating environment

equipment must only be used within the range of ambient environment detailed in the specification and in an environment free of abnormal vibration. z Ratings

applying AC voltage and current or the DC power supply to the equipment, check that they conform to the equipment ratings. z Printed circuit board

not attach and remove printed circuit boards when DC power to the equipment is on, as this may cause the equipment to malfunction. z External circuit

connecting the output contacts of the equipment to an external circuit, carefully check the supply voltage used in order to prevent the connected circuit from overheating. z Connection cable

handle the connection cable without applying excessive force.

: 1.00

://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949arP/N: EN_DYBH5301.0966.1101

&#169; NR 2008. All rights reserved

reserve all rights to this document and to the information contained herein. Improper use in particular reproduction and dissemination to third parties is strictly forbidden except where expressly authorized.

information in this manual is carefully checked periodically, and necessary corrections will be included in future editions. If nevertheless any errors are detected, suggestions for correction or improvement are greatly appreciated.

reserve the rights to make technical improvements without notice.

NARI-RELAYS ELECTRIC CO., LTD.

Suyuan Avenue. Jiangning, Nanjing 211102，China Tel: 86-25-87178185,  Fax: 86-25-87178208 Website: http://www.mianfeiwendang.com

: international@http://www.mianfeiwendang.com

NARI-RELAYS ELECTRIC CO., LTD

://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ar[此处图片未下载成功]

PCS-9611 Feeder Management Relay

[此处图片未下载成功]

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

PCS-9611 Feeder Management Relay

of Contents

...........................................................................................................................................i

............................................................................................................................i Health and Safety...................................................................................................................i Instructions and Warnings...................................................................................................ii Table of Contents..........................................................................................................................v Chapter 1 Inthttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949roduction.................................................................................................................1

.1 1.2 1.3 1.4

..................................................................................................................1 Functions....................................................................................................................1 Features.......................................................................................................................3 Ordering Options........................................................................................................3

2 Technical Data.............................................................................................................5

.1

Specification.................................................................................................5 2.1http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949.1

Specifications..................................................................................5

.1.1.1 Power Supply.............................................................................................5 2.1.1.2 Analog Current Input Ratings.....................................................................5 2.1.1.3 Analog Voltage Input Ratings.....................................................................5 2.1.1.4 Binary Input................................................................................................6 2.1.1.5 Binary Output..............................................................................................6 2.1.2 2.1.3 2.1.4 2.1.5

Specifications..............................................................................6 Ambient Temperature and Humidity...............................................................7 Communication Interhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949faces..............................................................................7 Type Test...........................................................................................................8

.1.5.1 Environmental Tests...................................................................................8 2.1.5.2 Mechanical Tests........................................................................................8 2.1.5.3 Electrical Tests............................................................................................8 2.1.5.4 Electromagnetic Compatibility....................................................................8

.2

Functions..................................................................................................9 2.2.1

Protection....................................................................................9

://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949G NARI-RELAYS ELECTRIC CO., LTD

Feeder Management Relay

[此处图片未下载成功]

.2.2 2.2.3 2.2.4 2.2.5 2.2.6 2.2.7 2.2.8 2.2.9

Control Element..................................................................................9 Phase Directional Element..............................................................................9 Inverse Time Characteristic............................................................................9 Zero Sequence Overcurrent Protection.........................................................9 Zero Sequence Directional Element.............................................................10 Thermal Overload Protection........................................................................10 Undervoltage Protection...............................................................................10 Overvoltage Protection........................................http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949..........................................10

.2.10 Under-frequency Load Shedding Protection...............................................10 2.2.11

Overcurrent Protection.......................................................................11

.2.12 Breaker Failure Initiation...............................................................................11 2.2.13 Broken Conductor Protection.......................................................................11 2.3

Functions............................................................................................11 2.3.1 2.3.2 2.3.3 2.3.4 2.3.5 2.3.6 2.4

Scope and Accuracy......................................................................11 Control Performance.....................................................................................12 Clock Performance...................................................http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949.....................................12 Disturbance Records.....................................................................................12 Telesignal........................................................................................................12 Fault Localization...........................................................................................12

...............................................................................................................12

3 Operation Theory......................................................................................................13

.1 3.2

Detectors..........................................................................................................13 Overcurrent Protection............................................................................................15 3.2.1 3.2.2 3.2.3 3.2.4 3.2.5 3http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949.3 3.4

stage Overcurrent Protection..............................................................15 Voltage Control Element for Overcurrent Protection..................................16 Directional Element for Overcurrent Protection..........................................17 Harmonic Blocking Element for Overcurrent Protection............................18 Inverse Definite Minimum Time Overcurrent Protection............................19

Overload Protection...................................................................................21 Zero Sequence Overcurrent Protection..................................................................21

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

PCS-9611 Feeder Management Relay

.4.1 3.4.2 3.4.3 3.4.4 3.5 3.6 3.7 3.8 3.9

Stage Zero Sequence Overcurrent Protection..................................21 Dihttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949rectional Element for Zero Sequence Overcurrent Protection...............23 Harmonic Blocking Element for Zero Sequence Overcurrent Protection.24 Zero Sequence IDMT Overcurrent Protection.............................................25

Earth Fault Protection..............................................................................25 Broken Conductor Protection..................................................................................26 Undervoltage Protection..........................................................................................27 Overvoltage Protection............................................................................................28 Switch Onto Fault (SOTF) Protection......................................................................29

.10 Under Frequency Load Shedding (UFLS) Protection............................................31 3.11 Breaker Failure Initiathttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ion..........................................................................................32 3.12 Three Phase Auto-recloser......................................................................................33

.12.1 Auto-reclosing Reclaim Conditions.............................................................34 3.12.2 Auto-reclosing Startup Conditions...............................................................35 3.12.3 Reclosing Check Mode..................................................................................35 3.12.4 Blocking Logic...............................................................................................36

4 Supervision, Metering and Control..........................................................................39

.1 4.2

....................................................................................................................39 Relhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ay Self-supervision.............................................................................................39 4.2.1 4.2.2 4.2.3 4.2.4 4.2.5 4.2.6 4.2.7 4.2.8 4.2.9

Hardware Supervision.........................................................................39 Setting Supervision.......................................................................................39 Control Circuit Supervision..........................................................................39 Tripped Position Contact Supervision.........................................................40 Low Pressure Binary Input Supervision......................................................40 VT Circuit Supervision...................................................................................40 CT Failure Supervision..................................................................................41 System Earth Fault Supervision................http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949...................................................42 System Frequency Supervision....................................................................42

.2.10 Digital Channel Supervision.........................................................................43 4.2.11

Overload Supervision.....................................................................43

NARI-RELAYS ELECTRIC CO., LTD

Feeder Management Relay

[此处图片未下载成功]

.2.12 Zero Sequence Overcurrent Supervision....................................................43 4.2.13 Dedicated Binary Input Supervision............................................................43 4.3 4.4 4.5

.....................................................................................................................43 Remote Control.............................................................http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949............................................43 Signaling...................................................................................................................44

5 Hardware Description...............................................................................................47

.1 5.2 5.3 5.4 5.5 5.6 5.7 5.8 5.9

....................................................................................................................47 Basic Enclosure........................................................................................................48 CPU Module (NR4102)..............................................................................................49 Digital Data Input Module (NR4201)........................................................................50 Analog Input Module (NR4402)................................................................................5http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe49490 GOOSE Module (NR4126)........................................................................................51 Binary Output Module (NR4521)..............................................................................51 Binary Input Module (NR4501).................................................................................52 Operation Circuit Module (NR4531)........................................................................53

.10 Power Supply Module (NR4301)..............................................................................57 5.11 Human Machine Interface Module (NR4851)..........................................................58 Chapter 6 HMI Operation Introduction......................................................................................59

.1

Machine Interface Overview.......................................................................59 6.1.1 6.1.2 6.1.3 6.1.4http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 6.2

.............................................................................................................59 Functionality...................................................................................................59 Keypad and Keys...........................................................................................59 LED indications..............................................................................................60

the HMI Menu Tree...............................................................................61 6.2.1 6.2.2 6.2.3 6.2.4 6.2.5 6.2.6

.........................................................................................................61 Submenu of “VALUES”.................................................................................61 Submenu of “SETTINGS”............................................................................http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949..62 Submenu of “REPORT”.................................................................................63 Submenu of “TEST_MODE”..........................................................................64 Submenu of “LOCAL_CTRL”........................................................................64

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

PCS-9611 Feeder Management Relay

.2.7 6.2.8 6.3

of “VERSION”................................................................................65 Submenu of “INTERFACE”...........................................................................65

the LCD Display...................................................................................66 6.3.1 6.3.2 6.3.3

Display under Normal Operation Condition...................................66 Display When Tripping...................................http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949...............................................66 Display under Abnormal Condition..............................................................69

.4 6.5 6.6 6.7

the Settings......................................................................................................70 View Device Status...................................................................................................70 View Software Version..............................................................................................76 View History Reports................................................................................................77 6.7.1 6.7.2

History Trip Reports..............................................................................77 View History Alarm Reports..........................................................................77

.8 Operation through Keypad.......................http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949...............................................................77 6.8.1 6.8.2 6.8.3

Protection.....................................................................................77 Change the Settings......................................................................................78 Clock Set.........................................................................................................78

.9 Understand the Alarms............................................................................................79

7 Settings......................................................................................................................81

.1 7.2 7.3 7.4 7.5 7.6

....................................................................................................................81 System Settings..................................................................http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949......................................81 Protection Settings...................................................................................................82 Communication Settings.........................................................................................95 GOOSE Parameter....................................................................................................97 VEBI Settings............................................................................................................98

8 Communication.......................................................................................................101

.1 8.2

....................................................................................................................101 Rear Communication Port Information.................................................................101 8.2.1

Interface.....http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949......................................................................................101

.2.1.1 EIA RS-485 Standardized Bus................................................................101 8.2.1.2 Bus Termination......................................................................................101

NARI-RELAYS ELECTRIC CO., LTD

PCS-9611 Feeder Management Relay

[此处图片未下载成功]

.2.1.3 Bus Connections &amp; Topologies...............................................................102 8.2.1.4 Biasing....................................................................................................102 8.2.2

Interface........................................................................................103

.2.2.1 IP Address and Equipment Address of the Equipment...........................103 8.2.2.2 Ethernet Standardized Communication Cable..http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949......................................103 8.2.2.3 Connections and Topologies...................................................................104 8.2.3 8.2.4 8.3

-5-103 Communication.................................................................104 IEC61850 Communication...........................................................................104

-5-103 Interface.......................................................................................104 8.3.1 8.3.2 8.3.3 8.3.4 8.3.5 8.3.6 8.3.7 8.3.8 8.3.9

Connection and Link Layer.........................................................105 Initialization..................................................................................................105 Time Synchronization..................................................................................105 Spontaneous Events........................................................http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949............................105 General Interrogation...................................................................................107 Cyclic Measurements..................................................................................108 General Commands.....................................................................................108 Generic Functions.......................................................................................109 Disturbance Records...................................................................................109

.4 IEC61850 Interface..................................................................................................110 8.4.1 8.4.2 8.4.3

.......................................................................................................110 Communication Profiles..............................................................................110 Serhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ver Data Organization............................................................................111

.4.3.1 Digital Status Values...............................................................................111 8.4.3.2 Analog Values.........................................................................................112 8.4.3.3 Protection Logical Nodes........................................................................112 8.4.3.4 LLN0 and Other Logical Nodes..............................................................113 8.4.4

Features and Configuration............................................................114

.4.4.1 Buffered/Unbuffered Reporting...............................................................114 8.4.4.2 File Transfer............................................................................................114 8.4.4.3 Timestamps..........................................http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949..................................................115

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

PCS-9611 Feeder Management Relay

.4.4.4 Logical Node Name Prefixes..................................................................115 8.4.4.5 GOOSE Services....................................................................................115 8.4.5

Conformance......................................................................................116

.4.5.1 ACSI Basic Conformance Statement......................................................116 8.4.5.2 ACSI Models Conformance Statement...................................................116 8.4.5.3 ACSI Services Conformance Statement.................................................118 8.4.6

Nodes..............................................................................................120

.4http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949.6.1 Logical Nodes Table...............................................................................120

9 Installation...............................................................................................................123

.1 9.2 9.3 9.4 9.5 9.6 9.7

....................................................................................................................123 Safety Instructions.................................................................................................123 Checking the Shipment..........................................................................................124 Material and Tools Required..................................................................................124 Device Location and Ambient Conditions............................................................124 Mechanical Installation.................................................http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949..........................................125 Electrical Installation and Wiring...........................................................................126 9.7.1 9.7.2 9.7.3 9.7.4 9.7.5 9.7.6 9.8

Guidelines.................................................................................126 Cubicle Grounding.......................................................................................126 Ground Connection on the Device.............................................................127 Grounding Strips and their Installation......................................................128 Guidelines for Wiring...................................................................................128 Wiring for Electrical Cables........................................................................129

Wiring of the Relay....................................................................................http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949129

10 Commissioning.....................................................................................................131

.1 General....................................................................................................................131 10.2 Safety Instructions.................................................................................................131 10.3 Commission Tools..................................................................................................132 10.4 Setting Familiarization...........................................................................................132 10.5 Product Checks......................................................................................................133

.5.1 With the Relay De-energized.......................................................................133

NARI-RELAYS ELECTRIC CO., LTD

://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949rxi

PCS-9611 Feeder Management Relay

[此处图片未下载成功]

.5.1.1 Visual Inspection...................................................................................134 10.5.1.2 Insulation Test (if required)...................................................................134 10.5.1.3 External Wiring.....................................................................................135 10.5.1.4 Auxiliary Supply....................................................................................135 10.5.2 With the Relay Energized............................................................................135

.5.2.1 Front Panel LCD Display......................................................................136 10.5.2.2 Date and Time......................................................................................136 10.5.2.3 Light Emitting Diodes (LEDs)......................................http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949..........................136 10.5.2.4 Testing the HEALTHY and ALARM LEDs.............................................136 10.5.2.5 Testing the TRIP LED...........................................................................136 10.5.2.6 Testing the RECLOSE LED..................................................................137 10.5.2.7 Testing the AC Current Inputs...............................................................137 10.5.2.8 Testing the AC Voltage Inputs...............................................................137 10.5.2.9 Testing the Binary Inputs......................................................................137 10.5.3 Protective Function Testing........................................................................138

.5.3.1 Demonstrate correct protection operation.............................................138 10.5.3.2 Overcurrent Protection Check........................................http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949......................138 10.5.3.3 IDMT Overcurrent Protection Check.....................................................139 10.5.3.4 Zero Sequence Overcurrent Protection Check.....................................139 10.5.3.5 Thermal Overload Protection Check.....................................................140 10.5.3.6 UFLS Protection Check........................................................................141 10.5.3.7 Auto-recloser Check.............................................................................141 10.5.3.8 SOTF Overcurrent Protection Check....................................................142 10.5.4 On-load Checks............................................................................................142 10.5.5 Final Checks.................................................................................................143

11 Maintenance...............................................http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949............................................................145

.1 Maintenance Schedule...........................................................................................145 11.2 Regular Testing.......................................................................................................145 11.3 Failure Tracing and Repair.....................................................................................145 11.4 Replace Failed Modules.........................................................................................145

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

PCS-9611 Feeder Management Relay

12 Decommissioning and Disposal..........................................................................147

.1 Decommissioning...................................................................................................147

.1http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949.1 Switching off................................................................................................147 12.1.2 Disconnecting cables..................................................................................147 12.1.3 Dismantling..................................................................................................147 12.2 Disposal...................................................................................................................147 Chapter 13 Manual Version History........................................................................................149

NARI-RELAYS ELECTRIC CO., LTD

PCS-9611 Feeder Management Relay

[此处图片未下载成功]

NARI-RELAYS ELECTRIC CO., LTD

Chapter 1 Introduction

1 Introduction

.1 Application

PCS-9611 relay is a directional overcurrent protection,http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 control and monitoring unit with

recloser for distribution feeders on solidly grounded, impedance grounded, Peterson coil grounded and ungrounded system. This relay is suited to be wall surface mounted indoors or outdoors or flush mounted into a control panel.

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

1.1-1 Application of PCS-9611

.2 Functions

Functions

P 51P 67P 50G 51G 67G

overcurrent protection Time overcurrent protection Directional overcurrent protection

zero sequence overcurrent protection Time zero seqhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949uence overcurrent protection Directional zero sequence overcurrent protection

protection 49 SEF

overload protection Sensitive earth fault protection

NARI-RELAYS ELECTRIC CO., LTD

Chapter 1 Introduction

protection 81U 7F BFI 79 25 SOTF 64  VTS CTS

frequency protection Frequency rate-of-change element Breaker failure initiation

pole auto-recloser (Up to 4 shots) Synchronism check function Switch-on-to fault logic Earth fault detection

and current drift auto adjustment Voltage transformer supervision Current transformer supervision

supervision

relays

Management Functions

2 TCCS

breaker status monitoring Circuit breaker control Control circuit supervision Multiple setting groups

Trip records    FR SOE

http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949Self-check alarm records 1024 Operating alarm records 1024 Handling records 64 Disturbance records

SOE records, latest records of following elements state

elements, protection elements and binary input elements. Rear communication ports: printer Rear communication ports: Ethernet

port

Testing Functions

SOE records generation Virtual measurement values generation Virtual tripping reports generation Virtual fault wave records generation

NARI-RELAYS ELECTRIC CO., LTD

Chapter 1 Introduction

.3 Features

Supports the digitalized substation functions absolutely, support the IEC60044-8 interface protocol. z Maturity protection configuration, fast speed, security performance.

On the premise of 24 samples per cycle, all data measurement, calculation and logic

could be finhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ished within one sampling period. The event recording and protection logic calculation also can be finished simultaneously. z Definite time and inverse time of overcurrent protection are both provided.

Overcurrent protection could be controlled by voltage control element and directional element. z Under frequency protection that could be controlled by rate-of-change elements would shed

before out-of-step. z This relay constantly measures and calculates a large mount of analog quantities, such as

voltage, phase-to-phase voltage, neutral voltage, phase current, neutral current, active power, reactive power, power factor and frequency. z The relay can monitor and record the operating times of opening/closing circuit breakers. z Various methods of GPS clock synchronization, including message (SNTP &amp; others), pulse

second, and IRIG-B synchronization. z The HMI interface with a 320&#21http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe49495;240-dot LCD and two buttons on the front panel is very friendly

the user. z The relay can communication with SAS or RTU, the communication protocol of this device is

: IEC60870-5-103 or IEC61850. z Flexible configuration of operation circuit to suit for various circuit breakers. z Strong function optional module to satisfy all kinds of requirements on site. z High precision 16 bits A/D converter.

Perfect fault and disturbance recording function: 64 latest fault reports and 64 fault waves, the

of a disturbance recording is configurable. z 1024 handling records of users to equipment, and 1024 records of time tagged sequence of

can be recorded.

.4 Ordering Options

relay is very flexible to configure according to the practical engineering. The following table shows the required information when ordering a PCS-9611. Information Required with Order:://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949arNARI-RELAYS ELECTRIC CO., LTD

Chapter 1 Introduction

Type:

Functions Standard

-

ABCD

2

B C D

1

AC Voltage Input; Current Input; Frequency 100V Phase-to-phase; 1A Phase; 50 Hz 100V Phase-to-phase; 1A Phase; 60 Hz 100V Phase-to-phase; 5A Phase; 50 Hz 100V Phase-to-phase; 5A Phase; 60 Hz 110V Phase-to-phase; 1A Phase; 50 Hz 110V Phase-to-phase; 1A Phase; 60 Hz 110V Phase-to-phase; 5A Phase; 50 Hz 110V Phase-to-phase; 5A Phase; 60 Hz 115V Phase-to-phase; 1A Phase; 50 Hz 115V Phase-to-phase; 1A Phase; 60 Hz 115V Phase-to-phase; 5A Phase; 50 Hz 115V Phase-to-phase; 5A Phase; 60 Hz Support of electronic/optical CT/VT Auxiliary Power Supply 110Vdc 125Vdc 220Vdc 250Vdc

Input/Output

binary inputshttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949, 8 binary outputs 21 binary inputs, 19 binary outputs Communications Ports for Automation 2 EIA RS-485 serial ports, IEC60870-5-103 2 100Base-TX Ethernet ports, IEC61850 4 100Base-TX Ethernet ports, IEC61850

100Base-TX   2 100Base-FX Ethernet ports, IEC61850 Support to GOOSE Non Available GOOSE Module Connector Type Plug In/Out Terminal Screw Terminal

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 2 Technical Data

2 Technical Data

.1 General Specification

.1.1 Electrical Specifications

.1.1.1 Power Supply Rated Voltage Variation Ripple in the DC auxiliary voltage

Vdc, 125Vdc, 220Vdc, 250Vdc 80% ~ 120%

15% of the DC value. Per IEC 60255-11:1979

IEC 61000-4-11:1994, IEC 60255-11:1979

dips and voltage

interruptions

without reset up to 100ms

://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 condition Operating condition

&lt; 15W &lt; 25W

, 3V, 65mAh

battery type

.1.1.2 Analog Current Input Ratings Rated frequency Phase rotation Rated Current (In)

/60 &#177; 5Hz ABC

&#215;In

&#215;In (for metering)

&#215;In

&#215;In (for metering) current)

for 10s

for 1s capability for half

cycle Burden

[此处图片未下载成功]

&lt; 0.05 VA/phase @ In

&lt; 0.25 VA/phase @ In

.1.1.3 Analog Voltage Input Ratings 5

NARI-RELAYS ELECTRIC CO., LTD

Chapter 2 Technical Data

[此处图片未下载成功]

.1.1.4 Binary Input Rated Voltage Pickup voltage Dropout voltage Maximum permitted voltage

time for logic input

.1.1.5 Binary Output

model Max system voltage Test voltage across open http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949contact Making Capacity Breaking capacity at 250Vdc Continuous carry Short duration current  Dropout time (Typical/Max) Bounce time

contact unloaded contact

for tripping contact Potential-free contact 250Vac/dc

Vac RMS for 1min &gt;1000W at L/R=40ms 0.4A  resistance

.2A  inductive(L/R=40ms) 8A

A for 200ms

.2A  resistance

.05A inductive (L/R=40ms) 5A

A for 200ms 10ms/15ms

for signal contact

Vdc 82.5Vdc 60.5Vdc 150Vdc

Vdc

Vdc

Vdc 175.0Vdc 125.0Vdc 300Vdc

&lt;1ms

time (Typical/Max) 5ms/10ms

ms

,000 operations minimum 10,000,000 operations minimum

ms

,000 operations minimum 10,000,000 operations minimum

.1.2 Mechanical Specifications

dimensions Trepanning dimensions Mounting Way Weight per device Local conhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949trol panel Display language Housing material Housing color Location of terminals Protection class

(per IEC60529:1989)

.00&#215;177.00&#215;223.80 (W&#215;H&#215;D, unit: mm) 226.00&#215;178.00, M5 screw (W&#215;H, unit: mm) Flush mounted Approx. 5kg

control module: 2 buttons and a 320&#215;240-dot LCD Optional: Chinese ,English Aluminum Silver grey

panel of the device

side: IP40, up to IP51

side, connection terminals: IP20 Other Sides: IP30

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 2 Technical Data

.1.3 Ambient Temperature and Humidity

temperature range

and storage temperature range Permissible humidity

&#176;C ~  55&#176;C -40&#176;C ~  70&#176;C

% ~ 95%, condensation not permissible

.1.4 Communication Interfaces

://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949m

number Baud rate

(EIA)

distance Maximal capacity Safety level Port number Connector type Transmission Rate

standard Transmission distance Safety level

number Connector type Transmission Rate Transmission standard

Fiber Type Transmission distance Safety level Port number

(EIA)

rate Printer type Safety level Port number

distance

(EIA)

capacity Timing standard Safety level

for communicating with RTU/SCADA

to 2

~ 38400bps &lt; 1000m@4800bps 32

to ELV level Up to 4 RJ-45 100Mbits/s 100Base-TX &lt; 100m

to ELV level Up to 2 SC 100Mbits/s 100Base-FX Multi-mode &lt; 1500m

to ELV level 1

~ 38400bps EPSONhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949&#174; LQ-300K Isolation to ELV level 1 &lt; 500m 32

, IRIG-B Isolation to ELV level

for communicating with a printer

for clock synchronization

NARI-RELAYS ELECTRIC CO., LTD 7

Chapter 2 Technical Data

[此处图片未下载成功]

.1.5 Type Test

.1.5.1 Environmental Tests Dry heat test Dry cold test

heat test, cyclic 2.1.5.2 Mechanical Tests Vibration Shock and bump 2.1.5.3 Electrical Tests Dielectric tests Impulse voltage tests Insulation measurement

-5:2000, test voltage: 2kV, 50Hz, 1min

-5:2000, test voltage: 5kV, unipolar impulses, waveform 1.2/50μs, source energy 0.5J

-5:2000, insulation resistance &gt;100M , 500Vdc IEC60255-21-1:1988, Class I IEC60255-21-2:1988, Class I IEC60068-2-2:1974, 16 h at  55&#176;C IEC60068-2-1:1990, 16 h at -25&#176;C

-2-30:1980, two (12 12 http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949hours) cycles, 95%RH, low temperature  25&#176;C, high temperature  55&#176;C

.1.5.4 Electromagnetic Compatibility 1MHz burst disturbance tests

Common mode - Differential mode Electrostatic discharge tests

For contact discharge  -For air discharge

frequency interference tests

sweep

Radiated amplitude-modulated     Spot frequency    -Radiated amplitude-modulated

Radiated pulse-modulated Fast transient disturbance tests

Power supply, I/O &amp; Earth terminals  - Communication terminals Surge immunity tests

Power supply, AC inputs, I/O terminals

-22-1:1988

(idt IEC61000-4-2:1995), Class III  2.5kV  1.0kV

-22-2:1996

(idt IEC 61000-4-2:1995)  Class IV  8.0kV  15.0kV

-22-3:2000  (idt IEC 61000-4-3:1995 )  class III

V/m(rms), f80…1000MHz

Vm(rms), f=80MHzhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949/160MHz

/450MHz/900MHz

Vm(rms), f=900MHz IEC60255-22-4:2002  (idt IEC 61000-4-4:1995)  Class IV, 4kV, 2.5kHz, 5/50ns  Class IV, 2kV, 5.0kHz, 5/50ns IEC60255-22-5:2002

(idt IEC 61000-4-5:1995) , Class III

.2/50us,

kV, line to earth;  1kV, line to line

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 2 Technical Data

RF electromagnetic disturbance

Power supply, AC, I/O, Comm. terminal Power frequency magnetic field immunity

-22-6:2001, Class III  10V(rms), 150kHz~80MHz IEC61000-4-8:1993, Class V  100A/m for 1min  1000A/m for 3s IEC61000-4-9:1993, Class V  6.4/16 us  1000A/m for 3s

magnetic field immunity

V  100kHz &amp; 1MHz – 100A/m

.2 Protective Functions

.2.1 Overcurrent Protection

setting Time setting

of current setting Tolerance of http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949time setting

.1&#215;In ~ 40.0&#215;In 0s ~ 100s

≤ 2.5% or 0.01&#215;In, whichever is greater ≤ 1% &#215; Setting   35 ms

.2.2 Voltage Control Element

overvoltage element setting Undervoltage element setting Operating time

of voltage setting

~ 63.5V 2 ~ 110V ≤ 35ms

≤ 2.5% or 0.10V, whichever is greater

.2.3 Phase Directional Element

Characteristic angle Block Logic

and angle accuracy Operating time

: Forward, Reverse Configurable: 0~90&#176;, step is 15&#176;

or Block selectable by setting &#177;3&#186; ≤ 35ms

.2.4 Inverse Time Characteristic

threshold setting (Ip) scope Time multiplier setting scope Tolerance of pickup threshold setting Tolerance of trip time for 1.2&lt;I/Ip&lt;20

.1&#215;In ~ 4.0&#215;In 0.05 ~ 3.20

≤ 2% or 0.01&#215;In, whichttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949h ever is greater ≤ 5% of reference (calculated) value   2% current tolerance, respectively 35ms

.2.5 Zero Sequence Overcurrent Protection

setting Time setting

NARI-RELAYS ELECTRIC CO., LTD

.02A ~ 12.0A / 40.0&#215;In 0s ~ 100s

Chapter 2 Technical Data

[此处图片未下载成功]

of current setting Tolerance of time setting

≤ 2.5% or 0.01A, whichever is greater ≤ 1% &#215; Setting   35 ms

.2.6 Zero Sequence Directional Element

Characteristic angle Block Logic

and angle accuracy Operating time

: Forward, Reverse Configurable: -90&#176;~0&#176;, step is 15&#176; Permission or Block selectable by setting &#177;3&#186; ≤ 35ms

.2.7 Thermal Overload Protection

setting Time setting

of current setting Tolerance of time setting

.1&#215;In ~ 3http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949.0&#215;In 0s ~ 100s

≤ 2.5% or 0.01&#215;In, whichever is greater ≤ 1% &#215; Setting   35 ms

.2.8 Undervoltage Protection

setting Time setting

of voltage setting Tolerance of time setting

.0 ~ 110.0V 0s ~ 100s

≤ 2.5% or 0.10V, whichever is greater ≤ 1% &#215; Setting   50 ms

.2.9 Overvoltage Protection

setting Time setting

of voltage setting Tolerance of time setting

.7 ~ 160.0V 0s ~ 100s

≤ 2.5% or 0.10V, whichever is greater ≤ 1% &#215; Setting   50 ms

.2.10 Under-frequency Load Shedding Protection

frequency setting Time setting

of frequency setting Tolerance of time setting Blocking element

blocking setting Frequency dropping rate blocking Operating time

of undervoltage blocking setting

.0 V ~ 110.0 V 0.3 Hz/s ~ 10 Hz/s ≤ 35ms://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949par

≤ 2.5% or 0.10V, whichever is greater 45.0Hz ~ 50.0Hz / 55.0Hz ~ 60.0Hz 0s ~ 100s ≤ 0.01 Hz

≤ 1% &#215; Setting   50 ms

of frequency dropping rate blocking

≤ 5.0%

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 2 Technical Data

.2.11 SOTF Overcurrent Protection

setting Time setting

of current setting Tolerance of time setting

.1&#215;In ~ 40.0&#215;In 0s ~ 100s

≤ 2.5% or 0.01&#215;In, whichever is greater ≤ 1% &#215; Setting   35 ms

.2.12 Breaker Failure Initiation

setting Time setting

of current setting Tolerance of time setting

.1&#215;In ~ 40.0&#215;In 0s ~ 100s

≤ 2.5% or 0.01&#215;In, whichever is greater ≤ 1% &#215; Setting   35 ms

.2.13 Broken Conductor Protection

/I1 Ratio setting Time setting

://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949Tolerance of current setting Tolerance of time setting

.2 ~ 1.0 0s ~ 100s ≤ 2.5%

≤ 1% &#215; Setting   35 ms

.3 Management Functions

.3.1 Metering Scope and Accuracy

Accuracy Voltage Accuracy Power (W) Accuracy

Power (Vars) Accuracy

Power (VA) Accuracy Energy (Wh) Accuracy Energy (Varh) Accuracy Phase range Accuracy Accuracy

.05 ~ 1.4&#215;In ≤ 0.2% of reading 0.05 ~ 1.4&#215;Vn ≤ 0.5% of reading

.2 ~ 1.4&#215;Vn, 0.05 ~ 1.4&#215;In

≤ 0.5% of reading at unity power factor 0.2 ~ 1.4&#215;Vn, 0.05 ~ 1.4&#215;In

≤ 0.5% of reading at zero power factor 0.2 ~ 1.4&#215;Vn, 0.05 ~ 1.4&#215;In ≤ 0.5% of reading

.2 ~ 1.4&#215;Vn, 0.05 ~ 1.4&#215;In

≤ 0.5% of reading at unity power factor 0.2 ~ 1.4&#215;Vn, 0.05 ~ 1.4&#215;In

≤ 0.5% of reading at zero power factor 0&#176; ~ 360&#176; ≤ 0.5% or &#177;1&#176; ≤ 0.http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe494901Hz

&#177; 5Hz (fn: rated frequency 50Hz or 60Hz)

NARI-RELAYS ELECTRIC CO., LTD 11

Chapter 2 Technical Data

[此处图片未下载成功]

.3.2 Control Performance

mode

of local control Accuracy of remote control

or remote ≤ 1s ≤ 3s

.3.3 Clock Performance

2000

time clock accuracy Accuracy of GPS synchronization External clock synchronization

≤ 3 seconds/day ≤ 1ms

B (200-98), SNTP protocol etc.

.3.4 Disturbance Records

and relative phases Trigger position

≤ 2.5% of applied quantities

500ms before protection pickup

.3.5 Telesignal

of telesignals Input of telesignals Resolution of SOE

≤ 1ms

free contact ≤ 2ms

.3.6 Fault Localization

≤signal-phase fault with high ground resistance://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949paris operated.)

.4 Certification

ISO9001: 2000 z ISO14001:2004 z OHSAS18001: 1999 z ISO10012:2003 z CMMI L3

EMC: 89/336/EEC, EN50263: 2000

Products safety(PS): 73/23/EEC, EN61010-1: 2001, EN60950: 2002

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 3 Operation Theory

3 Operation Theory

PCS-9611 feeder management relay is a microprocessor based relay which is designed for the protection of the overhead and underground transmission line. It can provide maturity protection for the transmission line. The following sections detail the individual protection functions in this relay.

.1 Fault Detectors

fault detector operates if any of the following conditions is satisfied.

. The discrepancy of the auxiliary normal closed contact of the circuit breaker and the post

position chttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ontact of the control circuit of this relay occurs on condition that the auto-recloser function is enabled and the auto-recloser is ready for operating. 2. Any one of phase currents is in excess of the setting of the stage 1 overcurrent protection on

that the stage 1 overcurrent protection is enabled (I &gt; [I_OC1]). 3. Any one of phase currents is in excess of the setting of the stage 2 overcurrent protection on

that the stage 2 overcurrent protection is enabled (I &gt; [I_OC2]). 4. Any one of phase currents is in excess of the setting of the stage 3 overcurrent protection on

that the stage 3 overcurrent protection is enabled (I &gt; [I_OC3]). 5. Any one of phase currents is in excess of the setting of the stage 4 overcurrent protection on

that the stage 4 overcurrent protection is enabled (I &gt; [I_OC4]). 6. Any one of phase currents is in excess of the setthttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ing of the SOTF overcurrent protection on

that the SOTF overcurrent protection is enabled (I &gt; [I_OC_SOTF]). 7. Residual current is in excess of the setting of the stage 1 earth fault overcurrent protection on

that the stage 1 earth fault overcurrent protection is enabled (I0 &gt; [I_ROC1]). 8. Residual current is in excess of the setting of the stage 2 earth fault overcurrent protection on

that the stage 2 earth fault overcurrent protection is enabled (I0 &gt; [I_ROC2]). 9. Residual current is in excess of the setting of the stage 3 earth fault overcurrent protection on

that the stage 3 earth fault overcurrent protection is enabled (I0 &gt; [I_ROC3]). 10. Residual current is in excess of the setting of the SOTF earth fault overcurrent protection on

that the SOTF earth fault overcurrent protection is enabled (I0 &gt; [I_ROC_SOTF]). 11. Sensithttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ive zero sequence current is in excess of the setting of the stage 1 sensitive earth fault

on condition that the stage 1 sensitive earth fault protection is enabled (I0S &gt; [I_SEF1]). 12. Sensitive zero sequence current is in excess of the setting of the stage 2 sensitive earth fault

on condition that the stage 2 sensitive earth fault protection is enabled (I0s &gt;

NARI-RELAYS ELECTRIC CO., LTD

Chapter 3 Operation Theory

[此处图片未下载成功]

[I_SEF2]).

. Any one of phase currents is in excess of the current setting of the overload protection on

that the overload protection is enabled (I &gt; [I_OvLd]). 14. The negative sequence current is greater than 0.01In and the ratio of negative to positive

sequence current (I2/I1) is in excess of the ratio setting of the broken conductor protection on condition thhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949at the broken conductor protection is enabled (I2/I1 &gt; [Ratio_I2/I1]). 15. Any one of phase currents is in excess of the current setting of the stage 1 breaker failure

on condition that the stage 1 breaker failure protection is enabled (I &gt; [I_OC_BFI1]). 16. Any one of phase currents is in excess of the current setting of the stage 2 breaker failure

on condition that the stage 2 breaker failure protection is enabled (I &gt; [I_OC_BFI2]). 17. The voltages are less than the setting of the stage 1 undervoltage protection on condition that

stage 1 undervoltage protection is enabled (U &lt; [V_UV1]). 18. The voltages are less than the setting of the stage 2 undervoltage protection on condition that

stage 2 undervoltage protection is enabled (U &lt; [V_UV2]). 19. The voltages are greater than the setting of the stage 1 overvoltage protection on condition

the shttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949tage 1 undervoltage protection is enabled (U &gt; [V_OV1]). 20. The voltages are greater than the setting of the stage 2 overvoltage protection on condition

the stage 2 undervoltage protection is enabled (U &gt; [V_OV2]). 21. The power system frequency is less than the setting of under frequency protection while

to-phase voltage is in excess of the low voltage setting of voltage control element on condition that the under frequency protection is enabled and reclaim timer of under frequency protection is ready. 22. The remote control operation occurs.

FD (Fault Detector) element will reset to normal operation status in 10s if the auto-recloser is in service or 500ms if the auto-recloser is disabled after the last one of the above items resets. The following figure shows the logic diagram of the fault detector of this relay.

[此处图片未下载成功]

Figure 3.1-1 Logic diagram of the http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949fault detector

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 3 Operation Theory

:

[S_CBState] is the state of the current position of the circuit breaker;

[VBI_Ready_AR] is the virtual binary input which indicates whether the AR is ready.

.2 Overcurrent Protection

.2.1 Four-stage Overcurrent Protection

overcurrent protection in this relay provides four-stage phase overcurrent protection with independent definite time delay characteristics. Each stage can be enabled or disabled by scheme logic settings independently. All overcurrent element, directional element and voltage control element settings apply to all three phases but are independent for each of the four stages. Configuring the relevant settings can enable or disable the corresponding protection. Each stage overcurrent protection can be blocked by an external binary input http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949respectively when the relevant binary input is energized and can be blocked by the second harmonic blocking element.

being set as regular definite time overcurrent protection, all the four stages of overcurrent protections have the same protective functional logic. But when the stage 1 overcurrent protection is set as inverse definite minimum time (IDMT) overcurrent protection, it has a different protective functional logic to other stages of overcurrent protections.

functional logic diagram of the stage 1 overcurrent protection is shown as bellow. The overcurrent block is a level detector that detects that the current magnitude is above the threshold.

[此处图片未下载成功]

3.2-1 Logic diagram of the stage 1 overcurrent protection

:

[I_OC1] is the current setting of the stage 1 overcurrent protection; [t_OC1] is the time-delay setting of the stage 1 overcurrent prothttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ection; [En_OC1] is the logic setting of the stage 1 overcurrent protection;

NARI-RELAYS ELECTRIC CO., LTD

Chapter 3 Operation Theory

[此处图片未下载成功]

[VEBI_OC1] is the virtual enabling binary input of the stage 1 overcurrent protection; [En_InvOC] is the logic setting for setting the OC1 with inverse time characteristics; [BI_Blk_OC1] is the binary input for blocking the stage 1 overcurrent protection;

“Flg_VCE_OC1_x (x: A, B, C)” denotes the state of the voltage control element of the stage 1 overcurrent protection, see Section 3.2.2 for more details about the voltage control element; “Flg_Dir_OC1_x (x: A, B, C)” denotes the state of the directional element of the stage 1 overcurrent protection, see Section 3.2.3 for more details about the directional element; “Flg_HarmBlk_OC1_x (x: A, B, C)” denotes the harmonic blocking element of the stage 1 overcurrent protectionhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949, see Section 3.2.4 for more details about the harmonic blocking element.

other stages of overcurrent protections have the same logic diagrams with the stage 1 overcurrent protection when the stage 1 overcurrent is set as regular overcurrent protection, but the operation thresholds are [I_OC2], [I_OC3] and [I_OC4] respectively.

.2.2 Voltage Control Element for Overcurrent Protection

the current detected by a local relay for a remote fault condition is below its overcurrent setting, a voltage controlled overcurrent (VCO) element may be used to increase the relay sensitivity to such faults. In this case, a reduction in system voltage will occur; this may then be used to reduce the pick up level of the overcurrent protection. The VCO function can be selectively enabled on the four stages of the main overcurrent element, which was described in Section 3.2.1. When the VCO is enabled, the overcurrent settihttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ng can be modified just to be in excess of the maximum value of load current.

Ia&gt; Ib&gt; Ic&gt;

for controlling Uab&lt; or Uca&lt; or U2&gt; Ubc&lt; or Uab&lt; or U2&gt; Uca&lt; or Ubc&lt; or U2&gt;

that voltage dependent overcurrent relays are more often applied in practical protection applications in order to give adequate overcurrent relay sensitivity for close up fault conditions. The fault characteristic of this protection must then coordinate with any of the downstream overcurrent relays that are responsive to the current decrement condition. It therefore follows that if this relay is to be applied on an outgoing feeder from a generator station, the use of voltage controlled overcurrent protection in the feeder relay may allow better coordination with the VCO relay on the generator.

the operation accuracy of the VCO protection, it is necessary to take the status of thhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949e voltage transformer into account. If the voltage transformer has an error, the numerical relay will issue an [Alm_VTS_Bus] signal and block all the elements that relate to the voltage measurement.

functional logic diagram of the voltage control overcurrent protection is shown in Figure 3.2-1. Each stage of the overcurrent protection can be set with voltage control by its relevant independent setting respectively. The detailed functional logic diagram for the voltage control

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 3 Operation Theory

of phase A for the stage 1 overcurrent protection is shown as bellow. The logic diagrams for voltage control element of other two phases can be gotten on the analogy of this.

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

3.2-2 Logic diagram of the voltage controlled element of phase A

:

[Vpp_UV_VCE] is the voltage setting of the undervoltage control element;

[V_NegOV_VCE] is the voltage setting of the negative sequence overvoltage control element; [En_VTS] is the logic setting of the busbar voltage transformer supervision function; [En_VCE_OC1] is the logic setting of the voltage control element for the OC1 protection; [En_BlkOC_VTS] is the logic setting of the function which can block all the protective elements that relate to the voltage measurement when the voltage transformer is failed; [Alm_VTS_Bus] is the alarm signal of the busbar voltage transformer supervision.

.2.3 Directional Element for Overcurrent Protection

phase fault elements of this relay are internally polarized by the quadrature phase-to-phase voltahttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ges, as shown in the table below:

of Protection

Phase B Phase C Phase

Current

Ib Ic

Voltage

Uca Uab

system fault conditions, the fault current vector will lag its nominal phase voltage by an angle dependent upon the system X/R ratio. It is therefore a requirement that the relay operates with maximum sensitivity for currents lying in this region. This is achieved by means of the relay characteristic angle (RCA) setting; this defines the angle by which the current applied to the relay must be displaced from the voltage applied to the relay to obtain maximum relay sensitivity. The relay characteristic angle (RCA) is configurable through the setting [phi_Char_OC] (in submenu “PROTECT_SETTING”, RCA = [phi_Char_OC]). A directional check is performed based on the following criteria: z Directional forward

&#176; &lt; (angle(I) - angle(U) -http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 RCA) &lt; 90&#176; z Directional reverse

NARI-RELAYS ELECTRIC CO., LTD 17

Chapter 3 Operation Theory

[此处图片未下载成功]

&#176; &gt; (angle(I) - angle(U) - RCA) &gt; 90&#176;

of the four overcurrent stages may be configured to be directional. When the element is selected as directional, a VTS block option is available. When the relevant setting is set to “1”, operation of the Voltage Transformer Supervision (VTS) will block the stage if the relevant directional element is in service. When the relevant setting is set to “0”, the stage will revert to non-directional upon operation of the VTS.

functional logic diagram of the phase directional overcurrent protection is shown in Figure 3.2-1. Each stage of the overcurrent protection can be set with directional element control by its relevant independent setting respectively. The detailed functional logic diagram for thttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949he phase A directional element for the OC1 protection is shown as bellow. The logic diagrams of voltage controlled element of other two phases can be gotten on the analogy of this.

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

3.2-3 Logic diagram of the phase A directional element for the OC1 protection Where:

[En_Dir_OC1] is the logic setting of the directional element for the OC1 protection;

[Opt_Dir_OC1] is the setting which is used to select the directional mode (forward, reverse) of the directional element;

[En_VTS] is the logic setting of the busbar voltage transformer supervision function;

[En_BlkOC_VTS] is the logic setting of the function which can block all the protective elements that relate to the voltage measurement when the voltage transformer ihttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949s failed; [Alm_VTS_Bus] is the alarm signal of the busbar voltage transformer supervision.

.2.4 Harmonic Blocking Element for Overcurrent Protection

prevent maloperation of the overcurrent protection when the transformer is energized without any load, this relay provides 2nd harmonic blocking function to resolve such a problem, and it can be enable or disabled by the setting [En_HarmBlkOC/ROC].

percent threshold of the 2nd harmonic blocking element to the fundamental wave can be set through the setting [K_2ndHarm].

the fundamental current is greater than the setting [I_Rls_Harm_Blk], the harmonic blocking element of the corresponding phase is released.

figure shows the logic diagram of the harmonic blocking element of phase A for the stage 1 overcurrent protection. The logic diagram of the harmonic blocking element of phase B

NARI-RELAYS ELECTRIC http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949CO., LTD

[此处图片未下载成功]

Chapter 3 Operation Theory

phase C can be gotten on the analogy of this.

3.2-4 Logic diagram of the phase A harmonic blocking element for the OC1 protection Where:

[En_HarmBlkOC/ROC] is the logic setting of the harmonic blocking element; [K_2ndHarm] is the percent setting of the harmonic blocking element;

[I_Rls_Harm_Blk] is the current setting for releasing the harmonic blocking element; [Cfg_Harm_Blk] is the output matrix setting of the harmonic blocking element; “Imax” is the maximum phase fundamental wave current; “I2a” is the second harmonic current.

.2.5 Inverse Definite Minimum Time Overcurrent Protection

stage 1 overcurrent protection also can be used as inverse definite minimum time (IDMT) overcurrent protection.

methods are available to achieve correct relay coordination on a system; by means of timehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 alone, current alone or a combination of both time and current. Grading by means of current is only possible where there is an appreciable difference in fault level between the two relay locations. Grading by time is used by some utilities but can often lead to excessive fault clearance times at or near source substations where the fault level is highest. For these reasons the most commonly applied characteristic in coordinating overcurrent relays is the IDMT type. The inverse time delayed characteristics comply with the following formula (based on IEC60255-4 standard).

=

:

β = Constant α = Constant t = Operation time  I = Measured current

β

(I/Ip) 1

α

is the current threshold setting; the current setting of the stage 1 overcurrent [I_OC1] is used as the Ip in this relay. If the stage 1 overcurrent protection is used as IDMT overcurrent protection, thehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 range of the setting [I_OC1] is 0.1&#215;In ~ 4&#215;In.

NARI-RELAYS ELECTRIC CO., LTD 19

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

Chapter 3 Operation Theory

[此处图片未下载成功]

is the time multiplier setting; the multiplier setting of the IDMT overcurrent protection [TMS_InvOC] is used as Tp in this relay. If the stage 1 overcurrent protection is used as IDMT overcurrent protection, the range of the setting [TMS_InvOC] is 0.05 ~ 3.20.

types of IDMT characteristic curves are applied in this relay. The setting [Opt_InvOC] can be used to select the expected curve (see Section 7.3 “Protection Settings”).

_InvOC

Name

β

α

://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949rse Inverse

[此处图片未下载成功]

[此处图片未下载成功]

The functional logic diagram of the IDMT overcurrent protection is shown as bellow. The

block is a level detector that detects that the current magnitude is above the threshold.

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

3.2-5 Logic diagram of the IDMT overcurrent protection

:

[I_OC1] is the current setting of the stage 1 overcurrent protection; [En_OC1] is the logic setting of the stage 1 overcurrent protection;

[VEBI_OC1] is the virtual enabling binary input of the stage 1 overcurrent protection; [En_InvOC] is the logic setting for setting the OC1 with inverse time characteristics; [BI_Blk_OC1] is the binary input for blocking the stage 1 overcurrent protection;

“Flg_VCE_OC1_x (x: A, B, C)” denotes the state of the voltage control element of the stage 1http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 overcurrent protection, see Section 3.2.2 for more details about the voltage control element; “Flg_Dir_OC1_x (x: A, B, C)” denotes the state of the directional element of the stage 1 overcurrent protection, see Section 3.2.3 for more details about the directional element; “Flg_HarmBlk_OC1_x (x: A, B, C)” denotes the harmonic blocking element of the stage 1 overcurrent protection, see Section 3.2.4 for more details about the harmonic blocking

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 3 Operation Theory

.

.3 Thermal Overload Protection

relay incorporates a current based thermal replica, using load current to model heating and cooling of the protected plant. The element can be set with both alarm and trip stages.

heat generated within an item of plant, such as a cable or a transformer, is the resistive loss (Ι2R x t). Thus, heating is dihttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949rectly proportional to current squared. The thermal time characteristic used in the relay is therefore based on current squared, integrated over time. The relay automatically uses the largest phase current for input to the thermal model.

is designed to operate continuously at a temperature corresponding to its full load rating, where heat generated is balanced with heat dissipated by radiation etc. Over-temperature conditions therefore occur when currents in excess of rating are allowed to flow for a period of time.

functional logic diagram of the thermal overload protection is shown as bellow. The overload block is a level detector that detects that the current magnitude is above the threshold.

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ar

3.3-1 Logic diagram of the overload protection

:

[I_OvLd] is the current setting of the overload protection; [t_OvLd] is the time-delay setting of the overload protection; [En_OvLd] is the logic setting of the overload protection;

[VEBI_OvLd] is the virtual enabling binary input of the overload protection.

.4 Zero Sequence Overcurrent Protection

.4.1 Three Stage Zero Sequence Overcurrent Protection

input current transformer is dedicated to the earth fault protection. The input CT is designed specially to operate at low current magnitudes.

the equipment is used in non-effective grounding or small current grounding system, the grounding zero sequence current during ground fault is basically small capacitive current. Correct selection of faulty phase in zero sequence protection could not be ensured by detection of such current. Since all protechttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949tion equipment are connected with each other via network and information

NARI-RELAYS ELECTRIC CO., LTD

Chapter 3 Operation Theory

[此处图片未下载成功]

could be shared in RCS-9000 substation automation system, so the faulty feeder could be decided firstly by related information from various feeders on same bus and then decided finally by trial tripping of the breaker of feeder having been selected. Zero sequence current has to be led from a zero sequence current transformer in this case.

the equipment is used in small resistance grounding system, the grounding zero sequence current during ground fault is larger and could be used for tripping directly. Three stages are equipped for the zero sequence current protection. The zero sequence current for tripping in this case could be calculated or directly led from a zero sequence current transformer. Whether the zehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ro sequence current uses the calculated current or the current of the real zero sequence CT is decided by the logic setting [Opt_Calc_3I0], which is contained in the menu of the system settings (see Section 7.2 “System Settings”).

following figure shows the operating process of definite time overcurrent characteristics of the three stages.

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

3.4-1 Logic diagram of the zero sequence http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949overcurrent protection

:

[I_ROC1] is the current setting of the stage 1 zero sequence overcurrent protection; [t_ROC1] is the time-delay setting of the stage 1 zero sequence overcurrent protection; [En_ROC1] is the logic setting of the stage 1 zero sequence overcurrent protection; [VEBI_ROC1] is the virtual enabling binary input of the ROC1 protection;

[En_InvROC] is the logic setting for setting the ROC1 with inverse time characteristics; [I_ROC2] is the current setting of the stage 2 zero sequence overcurrent protection; [t_ROC2] is the time-delay setting of the stage 2 zero sequence overcurrent protection; [En_ROC2] is the logic setting of the stage2 zero sequence overcurrent protection; [VEBI_ROC2] is the virtual enabling binary input of the ROC2 protection;

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 3 Operation Theory

[I_ROC3] is the current http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949setting of the stage 3 zero sequence overcurrent protection; [t_ROC3] is the time-delay setting of the stage 3 zero sequence overcurrent protection; [En_ROC3] is the logic setting of the stage 3 zero sequence overcurrent protection; [VEBI_ROC3] is the virtual enabling binary input of the ROC3 protection;

“Flg_Dir_ROCx” (x: 1~3) denotes the status of the zero sequence directional element, see Section 3.4.2 for more details about the directional element;

“Flg_HarmBlk_ROCx” (x: 1~3) denotes the status of the harmonic blocking element, see Section 3.4.3 for more details about the harmonic blocking element.

stage 3 zero sequence overcurrent protection also can issue an alarm signal [Alm_ROC3], if the setting [En_ROC3] or [VEBI_ROC3] is set as “0”.

.4.2 Directional Element for Zero Sequence Overcurrent Protection

voltage is used to polarize directional earth fault (DEF) protection. Withhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 earth fault protection, the polarizing signal requires to be representative of the earth fault condition. As residual voltage is generated during earth fault conditions, this quantity is commonly used to polarize DEF elements.

relay internally derives this voltage from the 3-phase voltage input that must be supplied from three single-phase VTs. These types of VT design allow the passage of residual flux and consequently permit the relay to derive the required residual voltage. In addition, the primary star point of the VT must be earthed.

is possible that small levels of residual voltage will be present under normal system conditions due to system imbalances, VT inaccuracies, relay tolerances etc.

zero sequence relay characteristic angle (ZS-RCA) is configurable through the setting [phi_Char_ROC] (in submenu “PROTECT_SETTINGS”, ZS-RCA  [phi_Char_ROC]). A directional check is performed based on thttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949he following criteria: z Directional forward

&#176; &lt; (angle(I0) - angle(U0 180&#176;) - ZS-RCA) &lt; 90&#176; z Directional reverse

&#176; &gt; (angle(I0) - angle(U0 180&#176;) - ZS-RCA) &gt; 90&#176;

the element is selected as directional, a VTS block option is available. When the relevant setting is set to “1”, operation of the Voltage Transformer Supervision (VTS) will block the stage if the relevant directional element is in service. When the relevant setting is set to “0”, the stage will revert to non-directional upon operation of the VTS.

detailed functional logic diagram of the zero sequence directional element of stage 1 zero sequence overcurrent protection is shown as bellow.

NARI-RELAYS ELECTRIC CO., LTD 23

Chapter 3 Operation Theory

[此处图片未下载成功]

3.4-2 Logic diagram of the zero sequence directional element for the ROC1http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 protection Where:

[Opt_Dir_ROC1] is the setting which is used to select the directional mode (forward, reverse) of the zero sequence directional element for the ROC1 protection;

[En_VTS] is the logic setting of the busbar voltage transformer supervision function;

[En_BlkOC_VTS] is the logic setting of the function which can block all the protective elements that relate to the voltage measurement when the voltage transformer is failed; [Alm_VTS_Bus] is the alarm signal of the busbar voltage transformer supervision.

.4.3 Harmonic Blocking Element for Zero Sequence Overcurrent Protection

prevent maloperation of the zero sequence overcurrent protection when the transformer is energized without any load, this relay provides 2nd harmonic blocking function to resolve such a problem, and it can be enable or disabled by the setting [En_HarmBlkOC/ROC].

percent threshold of the 2nd harmonihttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949c blocking element to the fundamental wave can be set through the setting [K_2ndHarm].

the fundamental current is greater than the setting [I_Rls_Harm_Blk], the harmonic blocking element of the corresponding phase is released.

figure shows the logic diagram of the harmonic blocking element for the stage 1 zero sequence overcurrent protection.

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

3.4-3 Logic diagram of the harmonic blocking element for the ROC1 protection Where:

[En_HarmBlkOC/ROC] is the logic setting of the harmonic blocking element;

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949下载成功]

[此处图片未下载成功]

NANJING NARI-RELAYS ELECTRIC CO., LTD

Chapter 3 Operation Theory[K_2ndHarm] is the percent setting of the harmonic blocking element; [I_Rls_Harm_Blk] is the current setting for releasing the harmonic blocking element; [Cfg_Harm_Blk] is the output matrix setting of the harmonic blocking element; “Imax” is the maximum phase fundamental wave current; “I2a, I2b, I2c” is the second harmonic current.3.4.4 Zero Sequence IDMT Overcurrent ProtectionThe stage 1 zero sequence overcurrent protection also can be used as zero sequence inverse definite minimum time (IDMT) overcurrent protection. It has the same inverse time characteristic with the IDMT overcurrent protection (see Section 3.2.5), and the setting [Opt_InvROC] can be used to select the expected curve (see Section 7.3 “Protection Settings”). The functional logic diagram of the zero sequence IDMT overcurrent protection is shown as bhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ellow. The zero sequence overcurrent block is a level detector that detects that the current magnitude is above the threshold.Io &gt; [I_ROC1] Flg_Dir_ROC1 Flg_HarmBlk_ROC1 [En_ROC1] [VEBI_ROC1] [En_InvROC]&amp; &amp;IDMT [Op_InvROC]Figure 3.4-4 Logic diagram of the IDMT overcurrent protection Where: [I_ROC1] is the current setting of the stage 1 zero sequence overcurrent protection; [En_ROC1] is the logic setting of the stage 1 zero sequence overcurrent protection; [VEBI_ROC1] is the virtual enabling binary input of the ROC1 protection; [En_InvROC] is the logic setting for setting the ROC1 with inverse time characteristics; “Flg_Dir_ROC1” denotes the status of the zero sequence directional element for the stage 1 zero sequence overcurrent protection; “Flg_HarmBlk_ROC1” denotes the status of the harmonic blocking element for the stage 1 zero sequence overcurrent protection, see Section 3.4.3 for more details about the harmhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949onic blocking element.3.5 Sensitive Earth Fault ProtectionOne current transformer input is dedicated to the sensitive earth fault (SEF) protection. The input CT is designed specially to operate at very low current magnitudes. This relay provides two stagesNANJING NARI-RELAYS ELECTRIC CO., LTD25

Chapter 3 Operation Theoryof sensitive earth fault protection. Following figure shows the stage 1 sensitive earth fault protection logic diagram.Figure 3.5-1 Logic diagram for the stage 1 sensitive earth fault protection Where: [I_SEF1] is the current setting of the stage 1 sensitive earth fault protection; [t_SEF1] is the time setting of the stage 1 sensitive earth fault protection; [EBI_SEF1] is the enabling binary input of the stage 1 sensitive earth fault protection; [VEBI_SEF1] is the virtual enabling binary input of the stage 1 sensitive earth fault protection; “Flg_HarmBlk_SEF1” denotes the status of the harmhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949onic blocking element for the stage 1 sensitive earth fault protection. Following figure shows the harmonic blocking element for the stage 1 sensitive earth fault protection.[En_HarmBlkOC/ROC] |I2a/Ia| &gt; [K_2ndHarm] Imax &gt; [I_Rls_Harm_Blk] Ia &gt; 0.06In |I2b/Ib| &gt; [K_2ndHarm] Imax &gt; [I_Rls_Harm_Blk] Ib &gt; 0.06In |I2c/Ic| &gt; [K_2ndHarm] Imax &gt; [I_Rls_Harm_Blk] Ic &gt; 0.06In [Cfg_Harm_Blk]&amp;0x0010&amp;&amp;&amp;Flg_HarmBlk_SEF1&amp;Figure 3.5-2 Logic diagram of the harmonic blocking element for the SEF1 protection The symbols in above figure are mentioned in Section 3.4.3.3.6 Broken Conductor ProtectionThe relay incorporates an element which measures the ratio of negative to positive phase sequence current (Ι2/Ι1). This will be affected to a lesser extent than the measurement of negative sequence current alone, since the ratio is approximately constant with variations in load current. Hence,http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 a more sensitive setting may be achieved. The logic diagram is as shown below. The ratio of I2/I1 is calculated and is compared with the threshold and if the threshold is exceeded then the delay timer is initiated. The CTS block signal is26NANJING NARI-RELAYS ELECTRIC CO., LTD

Chapter 3 Operation Theoryused to block the operation of the delay timer.Figure 3.6-1 Logic diagram of the broken conductor protection Where: [Ratio_I2/I1] is the ration setting of the broken conductor protection; [t_I2/I1] is the time-delay setting of the broken conductor protection; [En_I2/I1] is the logic setting of the broken conductor protection; [VEBI_I2/I1] is the virtual enabling binary input of the broken conductor protection; [En_BlkI2/I1_CTS] is the logic setting of the function which can block the broken conductor protection when the current transformer is failed; [Alm_CTS] is the alarm signal of the current transformer supehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949rvision.3.7 Undervoltage ProtectionThis relay provides two-stage undervoltage protection with definite time delay characteristics. The two stages have same protection logics. Two methods are used to check the undervoltage condition by the setting [Opt_UV_SinglePh]. If setting [Opt_UV_SinglePh] is set as “0”, when the all three voltage values are less than the voltage setting, the undervoltage protection will operates after the appointed time delay; and if the setting [Opt_UV_SinglePh] is set as “1”, when anyone of the three voltage values is less than the voltage setting, the undervoltage protection will operates after the appointed time delay. The setting [Opt_UV_VTMode] is used to decide the busbar voltage input mode. If it is set as “1”, the inputted busbar voltage is phase-to-phase voltage; and if it is set as “0”, the inputted busbar voltage is phase voltage. So the voltage setting must be set in accordance with the setthttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ing [Opt_UV_VTMode]; that is if the setting [Opt_UV_VTMode] is set as “1”, the voltage setting is set according to phase-to-phase voltage; and if the setting [Opt_UV_VTMode] is set as “0”, the voltage setting is set according to phase voltage. The circuit breaker state is taken into account in the undervoltage protection logic; when the circuit breaker is opened, the undervoltage protection is not in service. If the fast voltage transformer supervision function detects the busbar voltage transformer is failed, the undervoltage protection is blocked. And if the system voltage is lost, the undervoltage protection is also blocked. Following figure shows the logic diagram of the stage 1 undervoltage protection.NANJING NARI-RELAYS ELECTRIC CO., LTD27

Chapter 3 Operation TheoryFigure 3.7-1 Logic diagram of the stage 1 undervoltage protection Where: [V_UV1] is the voltage setting of the stage 1 undervoltage protectiohttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949n; [t_UV1] is the time-delay setting of the stage 1 undervoltage protection; [Opt_UV_SinglePh] is the logic setting for selecting the undervoltage calculation method; [Opt_UV_VTMode] is the logic setting for deciding the UV busbar voltage input mode; [En_UV1] is the logic setting of the stage 1 undervoltage protection; [VEBI_UV1] is the virtual enabling binary input of the stage 1 undervoltage protection; [EBI_UV] is the enabling binary input of the undervoltage protection; [S_CBState] is the circuit breaker present state; “Flg_FastVTS_Bus” denotes whether the fast voltage transformer supervision element is operated: if the busbar VTS conditions are satisfied (See Section 4.2.6), and none of the fault detector elements which is related to the measured current picks up at the same time; “Flg_LostVolt_Sys” denotes whether the system voltage is lost: if all the three phase voltages are less than 15V and all the three phase currentshttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 are less than 0.06In for 20ms. The stage 1 undervoltage also can issue an undervoltage alarm signal, if the setting [En_UV1] or [VEBI_UV1] is set as “0”.3.8 Overvoltage ProtectionThis relay provides two-stage overvoltage protection with definite time delay characteristics. The two stages have same protection logics.28NANJING NARI-RELAYS ELECTRIC CO., LTD

Chapter 3 Operation TheoryTwo methods are used to check the overvoltage condition by the setting [Opt_OV_SinglePh]. If setting [Opt_OV_SinglePh] is set as “0”, when the all three voltage values are greater than the voltage setting, the overvoltage protection will operates after the appointed time delay; and if the setting [Opt_OV_SinglePh] is set as “1”, when anyone of the three voltage values is greater than the voltage setting, the overvoltage protection will operates after the appointed time delay. The setting [Opt_OV_VTMode] is used to decide the busbahttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949r voltage input mode. If it is set as “1”, the inputted busbar voltage is phase-to-phase voltage; and if it is set as “0”, the inputted busbar voltage is phase voltage. So the voltage setting must be set in accordance with the setting [Opt_OV_VTMode]; that is if the setting [Opt_OV_VTMode] is set as “1”, the voltage setting is set according to phase-to-phase voltage; and if the setting [Opt_OV_VTMode] is set as “0”, the voltage setting is set according to phase voltage. Following figure shows the logic diagram of the stage 1 overvoltage protection.Figure 3.8-1 Logic diagram of the stage 1 overvoltage protection Where: [V_OV1] is the voltage setting of the stage 1 overvoltage protection; [t_OV1] is the time-delay setting of the stage 1 overvoltage protection; [Opt_OV_SinglePh] is the logic setting for selecting the overvoltage calculation method; [Opt_OV_VTMode] is the logic setting for deciding the OV busbar voltage input modehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949; [En_OV1] is the logic setting of the stage 1 overvoltage protection; [VEBI_OV1] is the virtual enabling binary input of the stage 1 overvoltage protection.3.9 Switch Onto Fault (SOTF) ProtectionIn some feeder applications, fast tripping may be required if a fault is present on the feeder when it is energized. Such faults may be due to a fault condition not having been removed from the feeder,NANJING NARI-RELAYS ELECTRIC CO., LTD29

Chapter 3 Operation Theoryor due to earthing clamps having been left on following maintenance. In either case, it may be desirable to clear the fault condition in an accelerated time, rather than waiting for the time delay associated with overcurrent protection. Switch onto fault overcurrent protection and zero sequence accelerated overcurrent protection are equipped with this equipment. Acceleration before or after tripping could be configured by setting the logic setting [Opt_http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949SOTF]. Acceleration after tripping includes accelerated tripping for manual switching-onto-fault or automatic reclosing-onto-fault. Current settings and delays of these two accelerated tripping protections could be configured independently. If acceleration after tripping is selected, the SOTF element is enabled for 3s after auto-recolser operates. And the SOTF element is enabled for 3s fixedly after manual closing signal is issued. The logic diagram of the switch onto fault protection is shown in following figure.Figure 3.9-1 Logic diagram of the SOTF protection Where: [I_OC_SOTF] is the current setting of the SOTF protection; [t_OC_SOTF] is the time-delay setting of the SOTF protection; [En_OC_SOTF] is the logic setting of the SOTF protection; [VEBI_OC_SOTF] is the virtual enabling binary input of the SOTF protection; [I_ROC_SOTF] is the current setting of the zero sequence SOTF protection; [t_ROC_SOTF] is the time-delay setthttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ing of the zero sequence SOTF protection; [En_ROC_SOTF] is the logic setting of the zero sequence SOTF protection; [VEBI_OC_SOTF] is the virtual enabling binary input of the zero sequence SOTF protection; [Opt_SOTF] is the setting for selecting the acceleration mode of the SOTF protection; [t_En_SOTF] is the enabling time setting of the SOTF protection;30NANJING NARI-RELAYS ELECTRIC CO., LTD

Chapter 3 Operation Theory[VBI_Ready_AR] is used to denote the auto-recloser is ready for operating; [Op_AR] means that the auto-recloser operates; [BI_52b] denotes the auxiliary tripping position of the circuit breaker.3.10 Under Frequency Load Shedding (UFLS) ProtectionThe feeder relay includes under frequency protection to facilitate load shedding and subsequent restoration. The logic diagram of the under frequency logic is as shown in following figure. The UFLS block is a level detector that detects that the system frhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949equency is below the threshold.Figure 3.10-1 Logic diagram of the UFLS Protection Where: [df/dt_UFLS] is the rate change blocking setting of the UFLS protection; [Vpp_UV_VCE_UFLS] is the under voltage blocking setting of the UFLS protection; [f_UF_UFLS] is the under frequency setting of the UFLS protection; [En_df/dt_UFLS] is the logic setting of rate change blocking element of the UFLS protection; [En_UFLS] is the logic setting of the UFLS protection; [EBI_UFLS] is the enabling binary input of the UFLS protection; [VEBI_UFLS] is the virtual enabling binary input of the UFLS protection. This protection could be enabled only after 100ms later when power frequency is greater than the frequency setting of under frequency protection [f_UF_UFLS] and three phase voltages are all in excess of the setting [Vpp_UV_VCE_UFLS]. In the meanwhile, the protection will be blocked when the duration of condition that the power frequency is lesshttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 than 35.0Hz or greater than 65.0Hz is longer than 200ms. Under voltage blocking and frequency dropping rate blocking functions are equipped with it. When a fault occurs in the system and the voltage is so low or the frequency drops so fast that setting of under voltage or frequency dropping rate is exceeded, this protection will be blocked. If the frequency is below the setting and the UFLS element is not blocked the DT timer is started.NANJING NARI-RELAYS ELECTRIC CO., LTD31

Chapter 3 Operation Theory3.11 Breaker Failure InitiationThe relay has two-stage breaker failure protection with definite time delay characteristics. The two stages have same protection logics. The circuit breaker failure protection is specially for re-tripping the circuit breaker, when the relay has transmitted the tripping command to the circuit breaker, but it also can detect the fault on the busbar or the circuit breaker is still clhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949osed after an appointed time-delay. It is controlled by the state of the circuit breaker or the relay operation by setting the relevant setting respectively or the external binary input which is special for triggering the breaker failure initiation. The functional logic diagram of the stage 1 circuit breaker failure initiation is shown as bellow.Figure 3.11-1 Logic diagram of the stage 1 circuit breaker failure initiation Where: [I_OC_BFI1] is the current setting of the stage 1 breaker failure protection; [t_BFI1] is the time-delay setting of the stage 1 breaker failure protection; [En_BFI1] is the logic setting of the stage 1 breaker failure protection; [VEBI_BFI1] is the virtual enabling binary input of the stage 1 breaker failure protection; [BI_Ext_BFI] is the external binary input initiation of the breaker failure protection; [En_ExtBI_Ctrl_BFI] is the logic setting of the breaker failure protection with the control of thhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949e external binary input; [En_52b_Ctrl_BFI] is the logic setting of the breaker failure protection with the control of the circuit breaker state; [S_CBState] is the present state of the circuit breaker; [En_Trip_Ctrl_BFI] is the logic setting of the breaker failure protection with the control of the relay operation; “Flg_Relay_Tripped” means that the relay already has tripped, and the tripping element is included in the setting [Cfg_IntInitBFI] (See Section 7.3) which is used to select which tripping32NANJING NARI-RELAYS ELECTRIC CO., LTD

Chapter 3 Operation Theoryelement can initiate the breaker failure protection.3.12 Three Phase Auto-recloserThis relay will initiate auto-recloser for fault clearances by the phase overcurrent, earth fault protections etc. An auto-reclosing cycle can be internally initiated by operation of a protection element or externally by a separate protection device, provided the circuihttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949t breaker (CB) is closed until the instant of protection operation. At the end of the relevant dead time, a circuit breaker close signal is given, provided system conditions are suitable. The system conditions to be met for closing are that the system voltages are in synchronism or dead line/live busbar or live line/dead busbar conditions exist, indicated by the internal check synchronism element and that the circuit breaker closing spring, or other energy source, is fully charged indicated from the binary input [BI_LowPres_Cls]. The CB close signal is cut-off when the circuit breaker closes. The logic diagram of the auto-recloser is shown as below.Figure 3.12-1 Logic diagram of the auto-recloser Where:NANJING NARI-RELAYS ELECTRIC CO., LTD33

Chapter 3 Operation Theory[t_ARx] (x:1~4) is the time-delay setting of the auto-recloser; [En_AR] is the logic setting of the auto-recloser; [VEBI_AR] is the virtual enabhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ling binary input of the auto-recloser; [N_AR] is the shot number of the auto-recloser; [t_Reclaim] is the reclaim time-delay setting of the auto-recloser; [Op_FD] means the fault detector of this relay operates; [S_CBState] is the position state of the circuit breaker; “Flg_SynCheck” is the result of the synchronism check of the auto-recloser; “Flg_DeadCheck” is the result of the line-dead check of the auto-recloser; “Flg_CBRlyTrip” denotes that the relay has issued tripping signals; “Flg_CBMalTrip” denotes that the circuit breaker is tripped unexpectedly; “Flg_Blk_AR” denotes that the state of the auto-recloser blocking logic element. When the CB is closed, the reclaim timer starts. If the circuit breaker does not trip again, the auto-reclosing function resets at the end of the reclaim time. If the protection operates during the reclaim time the relay either advances to the next shot in the programmed auto-reclosing cycle, or,http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 if all programmed reclose attempts have been made, goes to lockout. The reclosing output pulse width is configurable by setting [t_PW_Reclose].3.12.1 Auto-reclosing Reclaim ConditionsWhen auto-reclosing element is enabled, if all the following cases are ready in normal operation case, the auto-reclosing element will be in service automatically after the setting [t_Reclaim]. 1. The tripped position (BI_52b) is “0” and the post closed position (BI_PostCls) is “1”; it means that the CB is closed manually. Any operation element is not in startup status; i.e. the fault detector does not pick up. The external blocking binary input of the auto-recloser (EBI_Lockout) is “0”; i.e. there is not an external auto-recloser blocking signal. The binary input of the operation circuit status of the CB (BI_LowPres_Cls) is “0”; i.e. the CB is ready for reclosing. The [Alm_TCCS] alarm signal is not occurred; i.e. the control circuit of the CB ihttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949s healthy. If the reclosing check mode is synchronism check mode or line-dead check mode, the alarm signal [Alm_VTS_Fdr] is not occurred; i.e. the line voltage transformer is healthy.2. 3.4.5. 6.If the auto-reclosing element is in service, there is a full charged battery sign on the right bottom of LCD (see Section 6.3 “Understand the LCD Display”).34NANJING NARI-RELAYS ELECTRIC CO., LTD

Chapter 3 Operation Theory3.12.2 Auto-reclosing Startup ConditionsThe startup conditions of the auto-reclosing element include two reasons. The first reason is that one of the tripping elements (defined in the setting [Cfg_InitAR]. see Section 7.3) of this relay is operated. The second reason is that the tripped position (BI_52b) and post closed position (BI_PostCls) are in the same state “1” without any protection operating signal, it means that the circuit breaker is unexpected tripped without any system fault occurhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ring. In normal operation case of the feeder, the two relays have different states ([BI_52b] = 0 and [BI_PostCls] = 1). The auto-reclosing startup logic diagram is shown in Figure 3.12-1. To prevent the auto-reclosing startup element from undesired operation, this relay takes the current measurands into account. Only when the circuit breaker has tripped absolutely, the auto-reclosing will be put into service.3.12.3 Reclosing Check ModeThree check modes are adopted in this relay: synchronism check mode, line-dead check mode and no-check mode. Each mode can be selected through a corresponding logic setting. Synchronism check mode In synchronism check mode case, the relay checks the phase angles of the line voltage and the busbar voltage. If the phase angle difference is less than the synchronism degree setting [phi_SynChk_AR], and the line voltage value is more than the 0.7Un, reclosing the circuit breaker of the feeder is permhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949itted. The logic diagram of the synchronism check element is shown as below.Figure 3.12-2 Logic diagram of the synchronism check element Where: “θ” is the angle difference of the busbar voltage and line voltage; “Un” is the secondary rated voltage of the feeder, the setting [U2n_VT_Fdr] is used to set the secondary rated voltage of the feeder; “Ubn” is the secondary rated voltage of the busbar, the setting [U2n_VT_Bus] is used to set the secondary rated voltage of the busbar; “Ux” is the input voltage value of the feeder; [En_SynChk_AR] is the logic setting of the synchronism check mode; [phi_SynChk_AR] is the synchronism degree setting of the auto-recloser. Line-dead check mode In line-dead check mode case, the relay checks the line voltage. If the line voltage value is less than the voltage value “0.3Un”, reclosing the circuit breaker of the feeder is permitted.NANJING NARI-RELAYS ELECTRIC CO., LTD35

Chapter http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe49493 Operation TheoryThe logic diagram of the no-voltage check element is shown as below.Figure 3.12-3 Logic diagram of the no-voltage check element Where: “Un” is the secondary rated voltage of the feeder, the setting [U2n_VT_Fdr] is used to set the secondary rated voltage of the feeder; “Ux” is the input voltage value of the feeder; [En_DeadChk_AR] is the logic setting of the line-dead check mode. No-check mode In no-check mode case, the reclosing is permitted without taking the line voltage value and phase angle into account. After the reclosing delay time, this relay will issue a reclosing signal, if all the other reclosing conditions are ready. If the two settings [En_SynChk_AR] and [En_DeadChk_AR] are set as “0”, the no-check mode will be in service. If one of the two settings [En_SynChk_AR] and [En_DeadChk_AR] is set as “1”, the relevant reclosing check mode will be in service. If the two settings [En_SynChk_AR] and [En_http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949DeadChk_AR] are set as “1” together, the line-dead check mode is taken into account firstly. If the line-dead check element can operate successfully, this relay will block the synchronism check element automatically; otherwise the synchronism check element will be in service.3.12.4 Blocking LogicAfter the auto-reclosing element being put into service successfully, if anyone of the following cases occurs at anytime in normal operation case, the relay will block the auto-reclosing element automatically at once. 1. 2. 3. Open the circuit breaker by manual tripping (KKJ = 0). Open the circuit breaker by remote tripping (KKJ = 0). The line VT failure occurs and is detected by the relay (Alm_VTS_Fdr = 1), if the reclosing check mode is no-voltage check mode. The relay detects the failure of the control circuit of the CB (Alm_TCCS = 1). The external blocking binary input of the auto-recloser (EBI_Lockout) is “1”; i.e. there is an exhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ternal blocking signal. The binary input of the closing circuit status of the CB (BI_LowPres_Cls) is “1”; i.e. the CB is not ready for reclosing. The last auto-reclosing command has issued successfully. Anyone of the protective elements which are set as “1” in the setting [Cfg_BlkAR] (See Section 7.3) has operated successfully.NANJING NARI-RELAYS ELECTRIC CO., LTD4. 5.6.7. 8.36

Chapter 3 Operation TheoryIf the auto-reclosing element is not in service, there is a full uncharged battery sign on the right bottom of LCD (see Section 6.3 “Understand the LCD Display”).NANJING NARI-RELAYS ELECTRIC CO., LTD37

Chapter 3 Operation Theory38NANJING NARI-RELAYS ELECTRIC CO., LTD

Chapter 4 Supervision, Metering and ControlChapter 4 Supervision, Metering and Control4.1 OverviewThough the protection system is in non-operating state under normal conditions, it is waiting for a power shttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ystem fault to occur at any time and must operate for the fault without fail. When the equipment is in energizing process before the LED “HEALTHY” is on, the equipment needs to be checked to ensure there are no errors. Therefore, the automatic supervision function, which checks the health of the protection system when startup and during normal operation, plays an important role. The numerical relay based on the microprocessor operations is suitable for implementing this automatic supervision function of the protection system. In case a fatal fault is detected during automatic supervision, the equipment will be blocked out. It means that relay is out of service. Therefore you must re-energize the relay or even replace a module to make relay back into service. The relay also provides some auxiliary functions, such as disturbance data record, on-line data metering, real-time power calculation etc. All these make the relay meet the http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949demands of the modern power grid requirements.4.2 Relay Self-supervision4.2.1 Relay Hardware SupervisionThe MCU, RAM, ROM chips on the CPU module are monitored to ensure whether they are damaged or have some errors. If any one of them is detected damaged or having error, the equipment will be blocked and issues alarm signal [Alm_Fail]. The LED indicator “HEALTHY” will be extinguished.4.2.2 Setting SupervisionThis relay has several setting groups, while only one is active at the same time. The settings of active setting group are checked to ensure they are reasonable. If the settings are checked to be invalid, the alarm signal [Alm_Setting] and [Alm_Fail] will be issued and this equipment will be blocked at the same time. The LED indicator “HEALTHY” will be extinguished.4.2.3 Control Circuit SupervisionIf the relay detects that the tripped position (52b) and the closed position (52a) are off at the same time for longer http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949than 3 seconds, the alarm signal [Alm_TCCS] will be issued and the LED indicator “ALARM” will be lit.NANJING NARI-RELAYS ELECTRIC CO., LTD39

Chapter 4 Supervision, Metering and Control4.2.4 Tripped Position Contact SupervisionIf the relay detects that the tripped auxiliary contact position is on, i.e., the value of [BI_52b] is “1”, meanwhile any phase current is greater than 0.06In, and this condition lasts longer than 10 seconds, the alarm signal [Alm_52b] will be issued and the LED indicator “ALARM” will be lit.4.2.5 Low Pressure Binary Input SupervisionThis relay has two binary inputs which are used to indicate the state of the circuit breaker mechanism. If the binary input [BI_LowPres_Cls] is energized, this relay will issue the alarm signal [Alm_LowPres_Cls]; and if the binary input [BI_LowPres_Trp] is energized, this relay will issue the alarm signal [Alm_LowPres_Trp]. The LED indicator “ALARM” will http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949be lit at the same time. If the alarm signal [Alm_LowPres_Cls] is issued, the auto-recloser is blocked; and if the alarm signal [Alm_LowPres_Trp] is issued, the first remote control output function is blocked.4.2.6 VT Circuit SupervisionThe voltage transformer supervision (VTS) feature is used to detect failure of the AC voltage inputs to this relay. The VTS logic in the relay is designed to detect the voltage failure and automatically adjust the configuration of protective elements whose stability would otherwise be compromised. A time-delay alarm output is also available. Busbar VT supervision The busbar VTS feature within the relay operates on detection of (1) Negative phase sequence (NPS) voltage is in excess of 8V or (2) Positive phase sequence (PPS) voltage is less than 30V with the presence of current of any phase (I.e., any of the phase current is in excess of 0.06In). This gives operation for the loss of voltages. Sthttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ability of the busbar VTS function is assured during system fault conditions, by the presence of any pickup element. Repeated here, the criteria of busbar VTS Element: (1) U1 &lt; 30V and any of phase current is greater than 0.06In (2) U2 &gt; 8V That any of these two conditions is satisfied means the busbar VT is in abnormal status. Then the alarm signal [Alm_VTS_Bus] is issued 10s later and the LED “ALARM” will be lit. When the busbar VT status returns to normal condition, the alarm will restore automatically 1.25s later. In case busbar VT circuit is failed, protection elements dependent on voltage will be blocked. A fast VTS logic is applied in the undervoltage protection to block this protection element when the fast VT failure is detected. In the fast VTS element, the phase current or the negative sequence current must be taken into account.40NANJING NARI-RELAYS ELECTRIC CO., LTD

Chapter 4 Supervision, Meterihttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ng and ControlThe logic diagrams of the busbar VTS element and fast VTS element are shown as below.Ia &gt; 0.06In Ib &gt; 0.06In Ic &gt; 0.06In U1 &lt; 30V U2 &gt; 8V [En_VTS]&amp; &amp;10s[Alm_VTS_Bus]Figure 4.2-1 Logic diagram of the busbar VTS elementIa &gt; 0.06In Ib &gt; 0.06In Ic &gt; 0.06In U1 &lt; 30V U2 &gt; 8V Ia &lt; [I_FastVTS_Imax] Ib &lt; [I_FastVTS_Imax] Ic &lt; [I_FastVTS_Imax] I2 &lt; [I_FastVTS_I2] [En_VTS]&amp;&amp; &amp;&amp;Flg_FastVTS_BusFigure 4.2-2 Logic diagram of the fast busbar VTS element Where: [En_VTS] is the logic setting of the busbar VTS function; [I_FastVTS_Imax] is the phase current setting of the fast busbar VTS function; [I_FastVTS_I2] is the negative sequence current setting of the fast busbar VTS function. Line VT supervision This function is used to supervise the VT circuit of line. When the auto-reclosing function is enabled and the setting [En_SynChk_AR] or [En_DeadChttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949hk_AR] is enabled, in case the measured line voltage is 15V difference with the predetermined value for more than 10s, the alarm signal [Alm_VTS_Fdr] will be issued and the LED “ALARM” will be lit.4.2.7 CT Failure SupervisionThe main purpose of the current transformer (CT) circuit failure supervision function is to detect faults in the secondary circuits of CT and avoid influence on the operation of corresponding protection functions. This CT failure supervision (CTFS) function will be processed all the time, whether general fault detection picks up or not. The criteria of CTS element are: (1) The maximum current is greater than 4 times minimum current, (2) The maximum current is greater than the setting [I_CTS]. In normal operation program of the equipment, if a CT failure is detected, the alarm signal [Alm_CTS] will be issued and the LED indicator “ALARM” will be lit. In case the CT circuit is failure, protection elements whttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ill not be blocked.NANJING NARI-RELAYS ELECTRIC CO., LTD41

Chapter 4 Supervision, Metering and ControlThe logic diagram of the CTFS element is shown as below.Figure 4.2-3 Logic diagram of the CTS element Where: [I_CTS] is the threshold current setting of the CTS element; [En_CTS] is the logic setting of the CTS element; [Opt_CT_Prot] is the setting used to select the CT wiring form.4.2.8 System Earth Fault SupervisionThe system earth fault supervision is used to monitor whether the power gird (isolated grounded system) has an earth fault. When the relay detects that the maximum phase voltage of the system is greater than 75V; or the zero sequence voltage is greater than 30V and the negative sequence voltage is less than 8V, the LED indicator “ALARM” will be lit and the alarm signal [Alm_EF] will be issued after 15s later. The logic diagram of the earth fault supervision element is shown as below.Figure 4http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949.2-4 Logic diagram of the earth fault supervision element4.2.9 System Frequency SupervisionThe frequency of the power system is supervised continually. When the phase-to-phase voltage is greater than 40V, meanwhile the power system frequency is less than [f_Alm_UF], the LED indicator “ALARM” will be lit and the alarm signal [Alm_Freq] will be issued after 10s later. In case system is abnormal, protection elements will not be blocked. The logic diagram of the frequency supervision element is shown as below.Figure 4.2-5 Logic diagram of the frequency supervision element42NANJING NARI-RELAYS ELECTRIC CO., LTD

Chapter 4 Supervision, Metering and Control4.2.10 Digital Channel SupervisionIn a digitalized substation, the digital channels (in the module NR4201) are used to lead the voltages and currents to this relay from the merging unit. If this relay detects anyone of the digital channel is abnormal (communicathttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ion interrupt, data error or the merging unit is abnormal), the LED indicator “ALARM” will be lit and the alarm signal [Alm_Data_Ch] will be issued.4.2.11 Thermal Overload SupervisionSee Section 3.3 for the details. When the thermal overload alarm situation is occurred, the LED indicator “ALARM” will be lit and the alarm signal [Alm_OvLd] will be issued.4.2.12 Zero Sequence Overcurrent SupervisionSee Section 3.4.1 for the details. When the zero sequence overcurrent alarm situation is occurred, the LED indicator “ALARM” will be lit and the alarm signal [Alm_ROC3] will be issued.4.2.13 Dedicated Binary Input SupervisionThe relay provides 4 alarm signals which can be triggered by binary input, and the binary input is configurable. When the relay detects anyone of the four binary inputs, the LED indicator “ALARM” will be lit and the alarm signal [Alm_BI_X] (X: 1, 2, 3, 4) will be issued.4.3 MeteringThe relay produces a vhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ariety of both directly and calculated power system quantities. These measurement values are updated on a per second basis and can be viewed in the submenu “METERING” of the relay or via relay communication. The measurands include Ia_M, Ib_M, Ic_M, 3I0_M, Ua_M, Ub_M, Uc_M, Uab_M, Ubc_M, Uca_M, 3U0M_Cal, f, P, Q and COSΦ etc. These measurands are got by real-time calculation and real-time summation locally. Active and reactive power calculation eliminates error due to unbalance of the system voltage. This calculation is independent with network. All these measurands also can transmit to the SAS or RTU through communication. More information about the communication and protocols, see Chapter 8 “Communication”.4.4 Remote ControlThe relay can receive the remote control commands to trip or close the circuit breaker. Up to three groups telecontrol output relays can be configured and at least one. Before executing a telecontrol commhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949and, it is necessary to put the telecontrol switch at the “Remote” position to energize binary input [EBI_TeleCtrl]. The remote control commands include remote tripping command, remote closing command etc. More information about the communication and protocols, see Chapter 8 “Communication”.NANJING NARI-RELAYS ELECTRIC CO., LTD43

Chapter 4 Supervision, Metering and ControlIt is recommended that separate relay output contacts are allocated for remote circuit breaker control and protection tripping. This enables the control outputs to be selected via a local/remote selector switch. Where this feature is not required the same output contact(s) can be used for both protection and remote tripping.4.5 SignalingThis relay has 21 binary inputs which are used to monitor the contact positions of the corresponding bay, and all the binary inputs are configurable. Some of them are general purpose binary inputs, and otherhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949s are special purpose binary inputs. The binary input state change confirmation time of the BI_1 to BI_7 is configurable according to practical application, and the binary input state change confirmation time of the other binary inputs is 10ms. In the factory, the BI_1 to BI_8 are used as general purpose binary inputs, and BI_9 to BI_21 are use as special purpose binary inputs. The following table lists the default definition of these special inputs in the factory. Binary Input BI_9 BI_10 BI_11 BI_12 BI_13 BI_14 BI_15 BI_16 BI_17 BI_18 BI_19 BI_20 BI_21 Terminal No. 0709 0710 0711 0712 0713 0714 0715 0716 0717 0718 0719 0720 0721 Description Binary input of the enabling UV protection signal Binary input of the enabling BFI protection signal Binary input of the blocking OC1 protection signal Binary input of the blocking OC2 protection signal Binary input of the blocking OC3 protection signal Binary input of the blocking OC4 protehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ction signal Binary input of the enabling remote control function signal Binary input of the blocking auto-recloser signal Binary input of the enabling UFLS protection signal Binary input of the tripping low pressure signal Binary input of the closing low pressure signal Binary input of the signal resetting signal Binary input of the device maintenance signalThe BI_9 is used to enable/disable the undervoltage protection. If it is not energized, the relay will block the undervoltage protection. The BI_10 is used to enable/disable the BFI logic. If it is not energized, the relay will block the BFI logic. The BI_11 is used to block the stage 1 overcurrent protection. If it is energized, the stage 1 overcurrent protection will be blocked. The BI_12 is used to block the stage 2 overcurrent protection. If it is energized, the stage 2 overcurrent protection will be blocked. The BI_13 is used to block the stage 3 overcurrent protectiohttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949n. If it is energized, the stage 344NANJING NARI-RELAYS ELECTRIC CO., LTD

Chapter 4 Supervision, Metering and Controlovercurrent protection will be blocked. The BI_14 is used to block the stage 4 overcurrent protection. If it is energized, the stage 4 overcurrent protection will be blocked. The BI_15 is used to enable the remote closing control of the circuit breaker. If it is energized, this relay can accept the remote closing commands and execute these commands. The BI_16 is used to block the auto-recloser protection element. If it is energized, the auto-recloser protection will be blocked 400ms later. The BI_17 is used to enable the UFLS protective element. If it is not energized, and this relay will block the UFLS protection. The BI_18 is used to denote the tripping mechanism state of the circuit breaker. If it is energized, it means that the circuit breaker is not ready for tripping. The BI_19 is used to dehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949note the closing mechanism state of the circuit breaker. If it is energized, it means that the circuit breaker is not ready for closing. The BI_20 is used to reset the LCD and the LED indicators in the front panel of this relay. If it is energized, the LCD and LED indicators and corresponding signals will be restored. The BI_21 is used to denote whether the relay is under maintenance or commissioning. If it is energized, when the IEC60870-5-103 protocol is adopted, this relay will not transmit any message through the uplink communication interfaces; when the IEC61850 protocol is adopted, this relay will transmit the message with the “Test” bit of which is set as “1”.NANJING NARI-RELAYS ELECTRIC CO., LTD45

Chapter 4 Supervision, Metering and Control46NANJING NARI-RELAYS ELECTRIC CO., LTD

Chapter 5 Hardware DescriptionChapter 5 Hardware Description5.1 OverviewThe modular design of this relay ahttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949llows the relay to be easily upgraded or repaired by a qualified service person. The faceplate is hinged to allow easy access to the configurable modules, and back-plugging structure design makes it easy to repair or replace any modules. There are several types of hardware modules in this relay; each module takes a different part in this relay. This relay mainly consists of a CPU module, a digital data input module, an analog input module (VT and CT), a GOOSE module, a binary output module, a binary input module, an operation circuit module, a power supply module and a human machine interface (HMI) module. These modules and their codes are listed as below. Module Description CPU module Digital data input module Analog input module GOOSE module Binary output module Binary input module Operation circuit module Power supply module Human machine interface module Module Code NR4102 NR4201 NR4402 NR4126 NR4521 NR4501 NR4531 NR4301 NR4http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949851The following two figures show the front panel and the rear panel of this device.FEEDER MANAGEMENT RELAYHEALTHY ALARMFigure 5.1-1 Front panel of the this relayNANJING NARI-RELAYS ELECTRIC CO., LTD47

Chapter 5 Hardware DescriptionFigure 5.1-2 Rear panel of the this relay (fully equipped) NOTE: The voltage and current input module can be selected according to practical engineering. If the traditional CT&amp;VT are applied, the NR4402 module is selected; and if the optical CT&amp;VT are applied, the NR4201 module is selected. NOTE: If the GOOSE is applied, the NR4126 module is selected; and if practical engineering demands more binary outputs, the NR4521 module is selected.5.2 Basic EnclosureThe basic enclosure for this relay is an electronic equipment rack (see Figure 5.2-1) with an adequate number of slots for all these modules. The basic rack is equipped with a back plane (mother board), and the bahttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ck plane provides some back plane lines for distributing signals within the enclosure. The rack, back plane and the slot allocation of this relay is shown as below.Figure 5.2-1 Rack, back plane and slot allocation of this relay48NANJING NARI-RELAYS ELECTRIC CO., LTD

Chapter 5 Hardware DescriptionThere are nine slots in the rack of this relay, which can be populated with eight modules: NR4102, NR4201, NR4402, NR4126, NR4521, NR4501, NR4531 and NR4301.5.3 CPU Module (NR4102)The CPU module is the kernel part of this equipment, and contains a powerful microchip processor and some necessary electronic elements. This powerful processor performs all of the functions for the relay: the protection functions, the communication management functions. There are several A/D conversion circuits on this module, which are used to convert the AC analog signals to corresponding DC signals for fulfilling the demand of the elhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ectrical level standard. A high-accuracy clock chip is contained in this module, it provide accurate current time for this relay. The functional details of the CPU module are listed as below: Protection calculations The CPU module can calculate protective elements (such as overcurrent element, zero sequence overcurrent etc.) based on the voltage and current inputs form the analog input module/the digital data input module and binary inputs from the binary input module, and then decides that whether the device need to trip or reclose. Communication management The CPU module can effectively manage the communication procedure, and reliably send out some useful information through its various communication interfaces. These interfaces are used to communicate with a SAS or a RTU. It also can communicate with the human machine interface module. If an event is occurred (such as SOE, protective tripping event etc.), this module will senhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949d out the relevant event information through these interfaces, and make it be easily observed by the user. Auxiliary calculations Basing on the voltage and current inputs, the CPU module also can calculate out the measurement values, such as active power, reactive power and power factor etc. All these values can be sent to a SAS or a RTU through the communication interfaces. Clock Synchronization This module has a local clock chip and an interface to receive clock synchronized signals from external clock source. These signals include PPS (pulse per second) signal and IRIG-B signal. Basing on the timing message (from SAS or RTU) and the PPS signal, or basing on the IRIG-B signal, this module can make the local clock synchronize with the standard clock. The front view of the CPU module is shown in Figure 5.1-2. A 7-pin connector is fixed on the front of this module. The terminal definition of the connector is described as below. Phttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949in connections on the connector of the CPU module:NANJING NARI-RELAYS ELECTRIC CO., LTD49

Chapter 5 Hardware DescriptionPin No. 0101 0102 0103 0104 0105 0106 0107Sign SYN  SYNSHLD RTS TXD SGNDDescription EIA RS-485 standardized interface for clock synchronization, PPS and IRIG-B signals are permitted. Not used Interface for connecting with a printer, the EPSON&#174; LQ-300K printer is recommended.5.4 Digital Data Input Module (NR4201)The digital data input module is applied in a digitalized substation for leading the current and voltage from the electronic transformer through a merging unit. The communication protocol is abided by the IEC60044-8 standard protocol strictly. The digital data input module can get following values: three phase protection currents (Ia, Ib, Ic), three phase metering currents (Ia_M, Ib_M, Ic_M), three phase busbar voltages (Ua, Ub, Uc) and the line voltage (Ux). The zero sequehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949nce current also can be led through this module solely, or be calculated on the base of the three phase protection currents. The front view of the digital data input module is shown in Figure 5.1-2.5.5 Analog Input Module (NR4402)The analog input module can transform these high AC input values to relevant low AC output value, which are suited to the analog inputs of the CPU module. The transformers are used both to step-down the currents and voltages to levels appropriate to the relay’s electronic circuitry and to provide effective isolation between the relay and the power system. A low pass filter circuit is connected to each transformer (CT or VT) secondary circuit for reducing the noise of each analog AC input signal. NOTE: The rated value of the input current transformer is optional: 1A or 5A. The rated value of the CT must be definitely declared in the technical scheme and the contract. NOTE: Because the rated value of thttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949he input current transformer is optional, it is necessary to check whether the rated values of the current transformer inputs are accordant to the demand of the engineering before putting the device into operation. The front view of the analog input module is shown in Figure 5.1-2. A 24-pin connector is fixed on the front of this module. The terminal definition of the connector is described as below. Pin connections on the connector of the analog input module:50NANJING NARI-RELAYS ELECTRIC CO., LTD

Chapter 5 Hardware DescriptionPin No. 0301 0302 0303 0304 0305 0306 0307 ~ 0310 0311 0312 0313 0314 0315 0316 0317 0318 0319 0320 0321 0322 0323 0324 IaSign Ua Ub Uc Un Ux Uxn Line voltage input. Not used Ian Ib Ibn Ic Icn I0 I0n Iam Iamn I0s I0sn Icm IcmnDescription Bus voltage inputs, phase sequence is (A, B, C), star connection (Y).The input of the line current of the A phase for protection. The input of thhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949e line current of the B phase for protection. The input of the line current of the C phase for protection. The input of the zero sequence current. The input of the line current of the A phase for metering. The input of the zero sequence current for sensitive earth fault protection. The input of the line current of the C phase for metering.DANGER: Never allow the current transformer (CT) secondary circuit connected to this equipment to be opened while the primary system is live. Opening the CT circuit will produce a dangerously high voltage. If this safety precaution is disregarded, personal death, severe personal injury or considerable equipment damage will occur.5.6 GOOSE Module (NR4126)The GOOSE module is used to transmit or receive the GOOSE command. This relay can receive GOOSE tripping or closing commands through the GOOSE module, and then trip or close the corresponding circuit breaker in the bay where this relay is ehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949quipped. The GOOSE module has two FC type optical Ethernet ports for receiving or transmitting the GOOSE command. The front view of the GOOSE module is shown in Figure 5.1-2.5.7 Binary Output Module (NR4521)The binary output module consists of some necessary contact outputs, such as trip-outputs, signal outputs etc. It can receive tripping commands or reclosing commands from the CPU module, andNANJING NARI-RELAYS ELECTRIC CO., LTD51

Chapter 5 Hardware Descriptionthen act according to these commands. This module also can send out some necessary binary output signals (dry contact) to the SAS or RTU according to the relevant commands from the CPU module. All the binary outputs are configurable. The front view of the binary output module is shown in Figure 5.1-2. A 22-pin connector is fixed on the front of the binary output module. The terminal definition of the connector is described as below. Pin connections ohttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949n the 22-pin connector of the binary output module: Pin No. 0601 0602 0603 0604 0605 0606 0607 0608 0609 0610 0611 0612 0613 0614 0615 0616 0617 0618 0619 0620 0621 0622 Sign BO_ROC1_Trp BO_ROC2_Trp BO_ROC3_Trp BO_BFI1_Trp BO_BFI2_Trp BO_SEF1_Trp BO_SEF2_Trp BO_OC1_Trp BO_OC2_Trp BO_OC3_Trp BO_OC4_Trp Description The stage 1 zero sequence overcurrent protection tripping output The stage 2 zero sequence overcurrent protection tripping output The stage 3 zero sequence overcurrent protection tripping output The stage 1 breaker failure protection tripping output The stage 2 breaker failure protection tripping output The stage 1 sensitive earth fault protection tripping output The stage 2 sensitive earth fault protection tripping output The stage 1 overcurrent protection tripping output The stage 2 overcurrent protection tripping output The stage 3 overcurrent protection tripping output The stage 4 overcurrent protection tripping outhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949putNOTE: Above table lists the default definition of all the binary outputs of this module in the factory, they can be configured according to the practical demand through the relevant settings, see Section 7.3 for more details.5.8 Binary Input Module (NR4501)The binary input module contains 21 binary inputs which are used to monitor the contact positions of the corresponding bay, and all the binary inputs are configurable. Some of them are used as general purpose binary inputs, and others are used as special purpose binary inputs. These binary inputs are all optical insulation binary inputs.52NANJING NARI-RELAYS ELECTRIC CO., LTD

Chapter 5 Hardware DescriptionThe regular optical insulation binary inputs are used to monitor the position of the regular binary signals; the special optical insulation binary inputs are used to monitor the position of the special binary signals, which must be taken into account http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949in the protection calculations and communication management of the CPU module. The front view of the binary input module is shown in Figure 5.1-2. A 22-pin connector is fixed on the front of the binary input module. The terminal definition of the connector is described as below. Pin connections on the 22-pin connector of the binary input module: Pin No. 0701 0702 0703 0704 0705 0706 0707 0708 0709 0710 0711 0712 0713 0714 0715 0716 0717 0718 0719 0720 0721 0722 BI_1 BI_2 BI_3 BI_4 BI_5 BI_6 BI_7 BI_8 EBI_UV BI_Ext_BFI BI_Blk_OC1 BI_Blk_OC2 BI_Blk_OC3 BI_Blk_OC4 EBI_TeleCtrl EBI_Lockout EBI_UFLS BI_LowPres_Trp BI_LowPres_Cls BI_RstTarg BI_BlkComm OptoSign Binary input 1 Binary input 2 Binary input 3 Binary input 4 Binary input 5 Binary input 6 Binary input 7 Binary input 8 Binary input of the enabling UV protection signal Binary input of the BFI protection initiation signal Binary input of the blocking OC1 protection signal Binarhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949y input of the blocking OC2 protection signal Binary input of the blocking OC3 protection signal Binary input of the blocking OC4 protection signal Binary input of the enabling remote control function signal Binary input of the blocking auto-recloser signal Binary input of the enabling UFLS protection signal Binary input of the tripping low pressure signal Binary input of the closing low pressure signal Binary input of the signal resetting signal Binary input of the device maintenance signal Common negative connection of the all binary inputs DescriptionNOTE: Above table lists the default definition of all the binary inputs in the factory, they can be configured according to the practical demand through PCS-PC configuration tool.5.9 Operation Circuit Module (NR4531)The operation circuit module consists of some necessary contact outputs, such as trip-outputs, signal outputs etc. It can receive tripping commands or reclosing http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949commands from the CPU module, and then execute these commands. This module also can send out some necessary binary output signals (dry contact) to the SAS or RTU according to the relevant commands from the CPUNANJING NARI-RELAYS ELECTRIC CO., LTD53

Chapter 5 Hardware Descriptionmodule. Figure 5.9-1 shows schematic diagram of the operation circuit in this module. Here, each abbreviation implicates a relevant functional relay. All the abbreviation and their implications are listed in following table. Abbreviation TWJ HWJ TBJ HBJ BTJ BHJ TBJV KKJ YHJ YTJ0801 AUX Implication Open position relay, 52b Closed position relay, 52a Tripping seal-in relay Closing seal-in relay Protection tripping relay AR closing relay Anti-pump relay Post closed position relay Remote closing relay Remote tripping relay0810 AUX0807 to 52b TWJ HBJ TBJV 0806 to closing coil HBJ TBJ BHJ 0808 0018 0019 TBJV TBJV anti-pumpControl Panelhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949To 0809 Closing Button Local Control Control Switch Remote Control Tripping Button To 08030014 YHJ 0015 YTJ 0012 BTJ 0016 0017 001308090803KKJ0802 TBJ 0805 to tripping coilTBJ 0804 to 52a HWJFigure 5.9-1 Schematic diagram of the operation circuit in this module Circuit Breaker Open State Supervision The relays TWJ is applied to supervise the open state of circuit breaker when terminal 0807 is connected to the negative pole of power supply in series with normal closed auxiliary contact of circuit breaker (52b). In addition, if terminal 0807 is connected with terminal 0806, i.e. connected with normal closed auxiliary contact of circuit breaker (52b) and its close coil (CC), the relay TWJ can provide supervision on health of close coil (CC) as well.54NANJING NARI-RELAYS ELECTRIC CO., LTD

Chapter 5 Hardware DescriptionThe LED indicator “CB OPEN” in green lighting shows the open state of the circuit brehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949aker. Circuit Breaker Closed State Supervision The relays HWJ is applied to supervise the open state of circuit breaker when terminal 0804 is connected to the negative pole of power supply in series with normal open auxiliary contact of circuit breaker (52a). In addition, if terminal 0804 is connected with terminal 0805, i.e. connected with normal open auxiliary contact of circuit breaker (52a) and its trip coil (TC), the relay HWJ can provide supervision on health of trip coil (TC) as well. A normal closed contact of HWJ serials with a normal closed contact of TWJ can initiate a control circuit failure annunciation by the terminal 0811 and 0812. The LED indicator “CB CLOSE” in red lighting shows the open state of the circuit breaker. Closing Circuit Protection closing signal arrives at terminal 0808 from the BHJ relay (terminal 0018 and 0019); manual closing signal arrives at terminal 0809 from the “Closing Button”; and the remhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ote closing signal arrives at terminal 0809 from the YHJ relay (terminal 0014 and 0015). Terminal 0806 shall be connected to close coil (CC) in series with normal open auxiliary contact of circuit breaker (52b). Terminal 0019 shall be connected with terminal 0808 via a metallic link; and terminal 0015 shall be connected with terminal 0809 via a metallic link too. HBJ is a seal-in auxiliary relay, whose pickup current is adaptive to the closing current in the range of 0.5A-4.0A. Even if closing signal disappears, the normal open contact of relay HBJ will keep closing to maintain closing circuits working until circuit breaker is closed successfully and the auxiliary contact of circuit breaker (52b) is open. TBJV is the anti-pump relay; the details of the TBJV relay are described in following section. Tripping Circuit Protection tripping signal arrives at terminal 0802 from the BTJ relay (terminal 0016 and 0017); manual tripping sihttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949gnal arrives at terminal 0803 from the “Tripping Button”; and the remote tripping signal arrives at terminal 0803 from the YTJ relay (terminal 0012 and 0013). Terminal 0805 shall be connected to trip coil (TC) in series with normal open auxiliary contact of circuit breaker (52a). Terminal 0017 shall be connected with terminal 0802 via a metallic link; and terminal 0013 shall be connected with terminal 0803 via a metallic link too. TBJ is a seal-in auxiliary relay, whose pickup current is adaptive to the trip current in the range of 0.5A-4.0A. Even if tripping signal disappears, the normal open contact of relay TBJ will keep closing to maintain trip circuits working until circuit breaker is tripped successfully and normal open auxiliary contact of circuit breaker (52a) is open. TBJ is also used in anti-pump circuit; the details of the TBJ relay are described in following section.NANJING NARI-RELAYS ELECTRIC CO., LTD55://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949

Chapter 5 Hardware DescriptionKKJ KKJ is a bi-stable auxiliary relay. When circuit breaker is closed manually, the relay KKJ will pick up and latch, when circuit breaker is tripped manually, the relay KKJ will reset. The normal open contact of KKJ can be used together with normal closed auxiliary contact of circuit breaker (52b), to initiate auto-recloser in case that circuit breaker trips especially without any trip commands from protection and manual switch. A normal open contact is provided to denote the position of the KKJ relay via terminals 813 and 814. Anti-pump Anti-pump function is achieved via auxiliary relay TBJV. In the event that a breaker is closed onto a fault, while the operator is applying a close signal via a closed control switch, the circuit breaker will trip and prevent further closing again until the closing circuit has been de-energized by the operator releasing the control switch. When trip signalhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 comes and at the same time close signal persists, the normal open contact of TBJ will close and TBJV will operate and keep sealed with its own normal open contact. The normal closed contact of TBJV will cut off closing circuit to prevent any further closing. The front view of the binary input module is shown in Figure 5.1-2. A 22-pin connector is fixed on the front of the operation circuit module. The terminal definition of the connector is described as below. Pin connections on the 22-pin connector of the operation circuit module:Pin No. 0801 0802 0803 0804 0805 0806 0807 0808 0809 0810 0811 0812 0813 0814 0815 0816 0817 0818 AUX  In_ProtTrp In_ManTrp 52a_PwrCC TC 52b_PwrIn_ProtCls In_ManCls AUX-SignDescription DC( ) input for operation circuit Protection tripping input Manual tripping input To negative pole of 52a contact To closing coil To tripping coil To negative pole of 52b contact Protection closing input Manual clhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949osing input DC(-) input for operation circuit TCCS alarm signal output Post closed position signal output The CB closing position output The CB opening position output 1BO_Alm_TCCS BO_PostCls BO_52a BO_52b_156NANJING NARI-RELAYS ELECTRIC CO., LTD

Chapter 5 Hardware Description0819 0820 0821 0822BO_52b_2 BO_Alm_FaultThe CB opening position output 2 General fault signal output5.10 Power Supply Module (NR4301)The power supply module is a DC/DC converter with electrical insulation between input and output, and an output power of 30W. The power supply module has an input voltage range as described in Chapter 2 “Technical Data”. The standardized output voltages are  3.3V,  5V, &#177;12V and  24V DC. The tolerances of the output voltages are continuously monitored. The  3.3V DC output provides power supply for the microchip processors, and the  5V DC output provides power supply for all the electrical elemenhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ts that need  5V DC power supply in this relay. The &#177;12V DC output provides power supply for A/D conversion circuits in this device, and the  24V DC output provides power supply for the static relays of this device. The use of an external miniature circuit breaker is recommended. The miniature circuit breaker must be in the on position when the device is in operation and in the off position when the device is in cold reserve. The power supply module also provides binary outputs which are used to send out some necessary binary output signals according to the relevant commands from the CPU module. The last six binary outputs (Terminal 0008~0019) are configurable. The front view of the binary input module is shown in Figure 5.1-2. A 22-pin connector is fixed on the front of the power supply module. The terminal definition of the connector is described as below. Pin connections on the 22-pin connector of the power supply modulehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949: Pin No. 0001 0002 0003 0004 0005 0006 0007 0008 0009 0010 0011 0012 0013 SIG_COM BO_Alm_Fail BO_Alm_Abnor BO_LatchTrp BO_LatchCls BO_UnlatTrp BO_UnlatCls BO_CtrlTrp Sign Description Signal common output terminal Failure signal output Alarming signal output Tripping latched signal output Closing latched signal output Tripping unlatched signal output Closing unlatched signal output Remote tripping outputNANJING NARI-RELAYS ELECTRIC CO., LTD57

Chapter 5 Hardware Description0014 0015 0016 0017 0018 0019 0020 0021 0022BO_CtrlCls BO_ProtTrp BO_ProtCls PSW  PSWGNDRemote closing output Protection tripping output Protection closing output DC power supply positive input DC power supply negative input Grounded terminalNOTE: Above table lists the default definition of the last six binary outputs of this module in the factory, they can be configured according to the practical demand through the relevant settings, shttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ee Section 7.3 for more details.5.11 Human Machine Interface Module (NR4851)The human machine interface (HMI) module is installed on the front panel of this device. It is used to observe the running status and event information on the LCD, and configure the protection settings and device operation mode. It can help the user to know the status of this device and detailed event information easily, and provide convenient and friendly access interface for the user. For further details, see Chapter 6 “HMI Operation Introduction”.58NANJING NARI-RELAYS ELECTRIC CO., LTD

Chapter 6 HMI Operation IntroductionChapter 6 HMI Operation IntroductionHuman machine interface (HMI) is an important component of the equipment. It is a convenient facility to access the relay from the front local control panel of the device to view desired information, such as measurement quantity or binary inputs’ state or program version, etc,http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 or modify some system settings or protection settings. This function is very helpful during commissioning before putting the equipment into service. Furthermore, all above functions can be realized in a remote terminal with special software through a communication bus via a RS-485 port or an Ethernet port. This chapter will describe human machine interface (HMI), menu tree and LCD display of the equipment. In addition, how to input settings using keypad is described in detail.6.1 Human Machine Interface Overview6.1.1 DesignThe human machine interface consists of a human machine interface (HMI) module which allows a communication as simple as possible for the user. The HMI module includes: A 320&#215;240-dot matrix backlight LCD visible in dim lighting conditions for monitoring status, fault diagnostics and setting, etc. Twenty LED indicators on the front panel of this relay for denoting the status of this protection operatihttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949on. A 2-multifunction-key keypad on the front panel of the device for full access to the device. The front panel of the device is shown in Figure 5.1-1.6.1.2 FunctionalityThe HMI module helps to draw your attention to something that has occurred which may activate a LED or a report display on the LCD. You as the operator may have own interest to view a certain data. Use menus navigate through menu commands and to locate the data of interest.6.1.3 Keypad and KeysThe keypad and keys on the front panel of the equipment provide convenience to the operator to view a certain data or change the device’s setting. The keypad contains two multifunction keys, and each key can be pressed and turned. Pressing the upper key “ENT” can confirm present operation or enter the next level menu; and pressing the lower key “ESC” can cancel present operation or back to the upper level menu. Turning the upper key “MENU” can choose an expected subhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949menu or data; and turning the lower upper keyNANJING NARI-RELAYS ELECTRIC CO., LTD59

Chapter 6 HMI Operation Introduction“ADJUST” can modify the selected data. Following figure shows the keypad and keys.Figure 6.1-1 Keypad on the front panel6.1.4 LED indicationsThere are twenty LED indicators, which can indicate the operation state of the device. Following figure shows the LED indicators on the front panel of the device.Figure 6.1-2 LED indicators Label HEALTHY Off Steady Green ALARM TRIP RECLOSE CB OPEN CB CLOSE Off Steady Yellow Off Steady Red Off Steady Red Off Steady Red Off Steady Red Display Remarks When the equipment is not energized or any hardware defect is detected during self-supervision. Lit when the equipment is in service and ready for operation. When the equipment is in normal operating condition. Lit when any abnormality alarm is issued. When the equipment is in normal operating conditionhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949. Lit when any protection element trips. When the equipment is in normal operating condition. Lit when reclosing operating. When the circuit breaker is closed state. When the circuit breaker is opened state. When the circuit breaker is opened state. When the circuit breaker is closed state.NOTE:60NANJING NARI-RELAYS ELECTRIC CO., LTD

Chapter 6 HMI Operation IntroductionThe “HEALTHY” LED can only be turned on by supplying DC to equipment again or rebooting the relay. The “ALARM” LED is turned on as long as alarm exists. When alarm signals disappear, it will be turned off. The “TRIP” LED is turned on once any protection element operates and remains lit even after the trip command goes off. The “RECLOSE” LED is turned on once auto-reclosing elements operates and remains lit even after the auto-reclosing command goes off. The “CB OPEN” LED is turned on once when the circuit breaker is in open position. The “CB Chttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949LOSE” LED is turned on once when the circuit breaker is in closing position. The “TRIP” and “RECLOSE” LEDs and relevant latched binary outputs can be reset by energizing the binary input [BI_RstTarg].6.2 Understand the HMI Menu Tree6.2.1 OverviewIn this section, the main layout of the menu which is shown on the LCD of the local human machine interface (HMI) will be described in detail. Under normal operating condition, press down the upper key “ENT” can enter the main menu of this device. The following figure shows the menu tree structure of this device.Figure 6.2-1 Tree diagram of total command menu6.2.2 Submenu of “VALUES”Purpose: This menu is used to view the measured value including current, voltage, phase angle, binaryNANJING NARI-RELAYS ELECTRIC CO., LTD61

Chapter 6 HMI Operation Introductioninput state and other calculated quantities. It also can view the operation state of this relay. Access Aphttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949proach: Move cursor to the item “VALUES” and press key “ENT” to enter its submenu after entering the main menu of this device. Submenu Tree:1.VALUES1.MEASUREMENT 2.ANGLE_MEASURE 3.ENABLING_BI 4.METERING 5.TELE_BI_STATE 6.ALM_STATE 7.OPTIC_COMM_STATE 8.GOOSE_BI_STATE 9.RELAY_STATE A.OPTIC_ALM_STAT B.MEASUREMENT_PRI_VAL C.METERING_PRI_VAL http://www.mianfeiwendang.comM_STATEFigure 6.2-2 Tree diagram of “VALUES” menu “VALUES” has following submenus. No.1 2 3 4 5 6 7 8 9 A B C DItemMEASUREMENT ANGLE_MEASURE ENABLING_BI METERING TELE_BI_STATE ALM_STATE OPTIC_COMM_STATE GOOSE_BI_STATE RELAY_STATE OPTIC_ALM_STAT MEASUREMENT_PRI_VAL METERING_PRI_VAL COMM_STATEDescriptionTo display magnitudes of the AC voltage and current and calculated values sampled by protection circuit To display the angles of the AC voltage and current To display the states of the enabling binary inputs To display magnitudes of the AC voltage and current http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949and calculated values sampled by metering circuit To display the states of the binary inputs To display the states of the self supervision information To display the states of the optical channel To display the states of the GOOSE information To display the states of the binary output To display the statistical information of the optical channel To display the primary protection value To display the primary metering value To display the communication state6.2.3 Submenu of “SETTINGS”Purpose: The menu is used to view and modify the settings and parameters of this device. Access Approach:NANJING NARI-RELAYS ELECTRIC CO., LTD62

Chapter 6 HMI Operation IntroductionMove cursor to the item “SETTINGS” and press key “ENT” to enter its submenu after entering the main menu of this device. Submenu Tree:Figure 6.2-3 Tree diagram of “SETTINGS” menu “SETTINGS” has following submenus. No.1 2 3 4 5 6 7ItemSYSTEM_SETTINhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949G PROTECT_SETTING Virtual_Enabling_BI Equip_Parameter GOOSE_SETTING MANUAL_SETTING COPY_SETTINGDescriptionTo view and modify system settings To view and modify protection settings To view and modify the virtual enabling binary inputs To view and modify communication settings To view and modify GOOSE settings To view and modify metering accuracy coefficient manually To copy a group of setting to other group6.2.4 Submenu of “REPORT”Purpose: This menu is used to view all kinds of report including trip report, alarm report and so on. Access Approach: Move cursor to the item “REPORT” and press key “ENT” to enter its submenu after entering the main menu of this device. Submenu Tree:3.REPORT1.TRP_REPORT 2.ALM_REPORT 3.BI_CHG_REPORT http://www.mianfeiwendang.comER_OPR_REPORT 5.Figure 6.2-4 Tree diagram of “REPORT” menu “REPORT” has following submenus. No. 1 2 ItemTRP_REPORT ALM_REPORTDescription To display the trip reports http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949To display the self supervision report63NANJING NARI-RELAYS ELECTRIC CO., LTD

Chapter 6 HMI Operation Introduction3 4 5BI_CHG_REPORT USER_OPR_REPORT TELE_CTRL_REPORTTo display the report of binary input change To display the device operation reports To display the local/remote control reports6.2.5 Submenu of “TEST_MODE”Purpose: This menu is used to test particular functions of the device, such as testing binary signals, tripping output circuit or telemetering. Access Approach: Move cursor to the item “TEST_MODE” and press key “ENT” to enter its submenu after entering the main menu of this device. Submenu Tree:Figure 6.2-5 Tree diagram of “TEST_MODE” menu “TEST_MODE” has following submenus. No. 1 ItemCOMM_TESTDescription To send all virtual messages of binary signals including tripping information, alarm, BI state changes, etc. only for the signal test and communication commissioning. To send messagehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949s of a selected measurement as a set value To modify metering accuracy coefficient automatically To display the protection trip reports without waveform2 3 4FORCE_METERING AUTO_CALBR ITEM_TRP_REPORT6.2.6 Submenu of “LOCAL_CTRL”Purpose: This menu is used to configure the device locally: setting clock, closing or tripping circuit breaker, clearing history report etc. Access Approach: Move cursor to the item “LOCAL_CTRL” and press key “ENT” to enter its submenu after entering the main menu of this device. Submenu Tree:64NANJING NARI-RELAYS ELECTRIC CO., LTD

Chapter 6 HMI Operation Introduction

6.2-6 Tree diagram of “LOCAL_CTRL” menu

“LOCAL_CTRL” has following submenus.

.

2 3 4 5 6 7 8

TELE_CTRL

[此处图片未下载成功]

CLR_REPORT TRIG_OSCILLOG CLR_STAT RESET_TARGET CLR_ENERGY

_ACTIVE_GRP

set the clock

://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949

switch the setting group

control the circuit breaker To clear the history reports

record present measurements as oscillogram To clear the statistical information of the optical channel To restore all the signals on the LCD and binary outputs To clear the energy accumulation of this relay

.2.7 Submenu of “VERSION”

:

menu is used to check program version and module information of this relay. Access Approach:

cursor to the item “VERSION” and press key “ENT” to enter its submenu after entering the

menu of this device. Submenu Tree:

6.2-7 Tree diagram of “VERSION” menu

“VERSION” has following submenus.

.

2

BOARD_INFO

check the program version of this relay To check the module information of this relay

.2.8 Submenu of “INTERFACE”

:://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949parNARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

Chapter 6 HMI Operation Introduction

menu is used to configure the environment parameter (display language etc.) of this relay. Access Approach:

cursor to the item “INTERFACE” and press key “ENT” to enter its submenu after entering the main menu of this device. Submenu Tree:

[此处图片未下载成功]

[此处图片未下载成功]

Figure 6.2-8 Tree diagram of “INTERFACE” menu

“INTERFACE” has following submenus.

.

2

DOWNLOAD

select the display language

enable downloading the interlock file

.3

[此处图片未下载成功]

Understand the LCD Display

.3.1

[此处图片未下载成功]

Default Display under Normal Operation Condition

default display on the LChttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949D is shown as below when the device is in normal situation.

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

Figure 6.3-1 Default display in normal situation

first line shows the current time of this relay, and it shows the measurement for the protection

the middle part of the LCD. The last line shows the device address and the setting group number. The battery sign on the left-bottom is used to indicate the ready state of the auto-recloser. When the battery sign is solid, it means that the auto-recloser is ready; when the battery sign is empty, it means that the auto-recloser is blocked; and when the battery sign is half solid, it means that the auto-recloser is in reclaiming procedure.

.3.2 Display When Tripping

there is any protection element operating, a brief tripping report will appear on the LCD, and the backlight of the LCD and the LED “TRIP” will be lit simultahttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949neously.

NARI-RELAYS ELECTRIC CO., LTD

Chapter 6 HMI Operation Introduction

format of the fault report is shown as following figure.

[此处图片未下载成功]

Figure 6.3-2 LCD display of trip report

first line shows the sequence number and the start time of the current trip report, and then

the operation elements and fault information one by one according to the time sequence. The fault information includes fault phase, maximum fault value and minimum fault value.

[此处图片未下载成功]

NOTE: In case more than one protection element has operated, the relevant report will be displayed one by one according to time sequence on the LCD. And the fault information is listed after all the operation elements.

trip report will keep being displayed on LCD until an acknowledgement by pressing the key “ENT” or energizing the binary input [BI_RstTarg]. Thehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 default display then appears on LCD and LED “TRIP” is turned off.

elements listed below may be displayed.

. 1 2 3 4 5 6 7 8 9 11

Element Op_FD Op_OC1 Op_OC2 Op_OC3 Op_OC4 Op_InvOC Op_OC_SOTF Op_OvLd Op_SEF1 Op_ROC1

least one of the fault detectors operates Stage 1 overcurrent protection operates Stage 2 overcurrent protection operates Stage 3 overcurrent protection operates Stage 4 overcurrent protection operates Inverse time overcurrent protection operates SOTF overcurrent protection operates Overload protection operates

1 sensitive earth fault protection operates Stage 2 sensitive earth fault protection operates Stage 1 zero sequence overcurrent protection operates Stage 2 zero sequence overcurrent protection operates Stage 3 zero sequence overcurrent protection operates Inverse time zero sequence overcurrent protection operates Zero sequenhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ce SOTF overcurrent protection operates UFLS protection operates The 1st shot auto-recloser operates The 2nd shot auto-recloser operates The 3rd shot auto-recloser operates

Op_SEF2 12 Op_ROC2 13 Op_ROC3 14 Op_InvROC 15 Op_ROC_SOTF 16 Op_UFLS NANJING NARI-RELAYS ELECTRIC CO., LTD

Chapter 6 HMI Operation Introduction

Op_BFI1 22 Op_BFI2 23 Op_UV1 24 Op_UV2 25 Op_OV1 26 Op_OV2 27 Op_I2/I1 28 Trip 29 30 31 32 33 34 35 36 37 38 39 40 41 42 43 44 45 46

_GOOSE_Trp1 Op_GOOSE_Cls1 Op_GOOSE_Trp2 Op_GOOSE_Cls2 Op_GOOSE_Trp3 Op_GOOSE_Cls3 Op_GOOSE_Trp4 Op_GOOSE_Cls4 Op_GOOSE_Trp5 Op_GOOSE_Cls5 Op_GOOSE_Trp6 Op_GOOSE_Cls6 Op_GOOSE_Trp7 Op_GOOSE_Cls7 Op_GOOSE_Trp8 Op_GOOSE_Cls8 Op_GOOSE_Trp9 Op_GOOSE_Cls9

4th shot auto-recloser operates Stage 1 Breaker failure protection operates Stage 2 Breaker failure protection operates Stage 1 undervoltage protection operates Stage 2 undervoltage phttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949rotection operates Stage 1 overvoltage protection operates Stage 2 overvoltage protection operates Broken conductor protection operates Protection is tripped

No.1 GOOSE Trip operates The No.1 GOOSE Close operates The No.2 GOOSE Trip operates The No.2 GOOSE Close operates The No.3 GOOSE Trip operates The No.3 GOOSE Close operates The No.4 GOOSE Trip operates The No.4 GOOSE Close operates The No.5 GOOSE Trip operates The No.5 GOOSE Close operates The No.6 GOOSE Trip operates The No.6 GOOSE Close operates The No.7 GOOSE Trip operates The No.7 GOOSE Close operates The No.8 GOOSE Trip operates The No.8 GOOSE Close operates The No.9 GOOSE Trip operates The No.9 GOOSE Close operates

information listed below may be displayed.

. 1 2 3 4 5 6 7 8 9 11

Information Ipmax I0max I2/I1max Uppmin Uppmax Upmin Upmax U2max fmin Uxmin

maximum phase current The maximum zero http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949sequence current The maximum ratio of I2/I1

minimum phase-to-phase voltage The maximum phase-to-phase voltage The minimum phase voltage The maximum phase voltage

maximum negative sequence voltage The minimum system frequency The maximum line voltage The minimum line voltage The fault localization result

Uxmax 12 Fault_Distance

NARI-RELAYS ELECTRIC CO., LTD

Chapter 6 HMI Operation Introduction

.3.3 Display under Abnormal Condition

there is any abnormality in the operating or firmware error detected by equipment self-diagnostic,

report will be displayed instantaneously on the LCD. Therefore, default display will be replaced by the alarm report.

format of the alarm report is shown as following figure.

[此处图片未下载成功]

Figure 6.3-3 Information of alarm report on the LCD

first line shows the alarm report thttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949itle, and then shows the alarm elements one by one according to the time sequence.

alarm report will keep being displayed on LCD until the relevant alarm situation is restored to normal state. It means that this relay does not detect any alarm situation. The default display then appears on LCD and LED “ALARM” is turned off. The LED “ALARM” will not be lit if the alarm signal [Alm_Fail] or [Alm_Setting] is issued. Alarm elements listed below may be displayed.

.

Element

least one alarm event occurs.

operates and the CB change status from close to open, this relay issues this signal 3s latter. All protection functions of the equipment are blocked. breaker is abnormal.

line voltage transformer fails. The busbar voltage transformer fails. The system frequency is abnormal. The control operation circuit is abnormal. The earth fault occurs. The ovhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949erload occurs.

stage 3 residual overcurrent alarms. The pressure of the tripping circuit is low. The pressure of the closing circuit is low. The current transformer fails. The digital data channel is abnormal. The undervoltage occurs.

input to trigger an alarm signal [Alm_BI_1] Binary input to trigger an alarm signal [Alm_BI_2]

_Fail

6 7 8 9 11 12 13

_VTS_Fdr Alm_VTS_Bus Alm_Freq Alm_TCCS Alm_EF Alm_ROC3 Alm_LowPres_Trp Alm_LowPres_Cls

Alm_OvLd

Alm_CTS 15 Alm_Data_Ch 16 Alm_UV1 17 Alm_BI_1 18 Alm_BI_2

NARI-RELAYS ELECTRIC CO., LTD 69

Chapter 6 HMI Operation Introduction

Alm_BI_3 20 Alm_BI_4 21 Goose_BJ 22 Alm_Setting

input to trigger an alarm signal [Alm_BI_3] Binary input to trigger an alarm signal [Alm_BI_4] The GOOSE element alarms. There is a mistake in the settings.

.4 View the Settings://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949partake viewing protection settings as an example to introduce the operating steps of viewing setting for operators. Operating steps:

. Turn key “MENU” to enter the main menu.

. Turn key “MENU

[此处图片未下载成功]

” to locate the cursor on the submenu “SETTINGS” and press key “ENT” to

this submenu. 3. Turn key “

[此处图片未下载成功]

MENU” to locate the cursor on the submenu “PROTECT_SETTING” and press key

[此处图片未下载成功]

“ENT” to enter this submenu. 4. Turn key “MENU

[此处图片未下载成功]

” to view the expected settings.

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

70http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949

NARI-RELAYS ELECTRIC CO., LTD

Chapter 6 HMI Operation Introduction

. Turn key “MENU” to view the expected measured values.

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

Figure 6.5-1 LCD display of the protection measurement

tables show all the state data of this relay. z Protection measurement data No. 1 2 3 4 5 6 8 9 10 12 13 14 15 16 17

Ib Ic 3I0 I1 I2 Ua Ub Uc Uab Ubc Uca 3U0 U1 U2

value of the phase A from protection CT Current value of the phase B from protection CT Current value of the phase C from protection CT Zero sequence current value Positive sequence current value Negative sequence current value Sensitive zero sequence cuhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949rrent value Voltage value of phase A from busbar VT Voltage value of phase B from busbar VT Voltage value of phase C from busbar VT Line voltage value

value of phase A to phase B Voltage value of phase B to phase C Voltage value of phase C to phase A Zero sequence voltage value Positive sequence voltage value Negative sequence voltage value System frequency

Metering data No. 1 2 3 4 5 6 7

_M Ib_M Ic_M 3I0_M Ua_M Ub_M Uc_M

value of the phase A from metering CT Current value of the phase B by self-calculation Current value of the phase C from metering CT Zero sequence current value

value of phase A from busbar VT Voltage value of phase B from busbar VT Voltage value of phase C from busbar VT

NARI-RELAYS ELECTRIC CO., LTD

Chapter 6 HMI Operation Introduction

9 10 11

_M Ubc_M Uca_M 3U0_http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949M

value of phase A to phase B Voltage value of phase B to phase C Voltage value of phase C to phase A Zero sequence voltage value System frequency Active power Reactive power Output active energy Incoming active energy Output reactive energy Incoming reactive energy

17 18 19

_Out KWH_In KVAH_Out KVAH_In

Φfactor

Phase angle data No. 1 2 3 4 5 6 7 8 9 10 11 12 13 14

(Ia-Ib) Ang(Ib-Ic) Ang(Ic-Ia) Ang(Ua-Ia) Ang(Ub_Ib) Ang(Uc-Ic) Ang(Ua-Ub) Ang(Ub-Uc) Ang(Uc-Uc) Ang(Uab-Ux) Ang(U0-I0) Ang(Ua-IaM) Ang(Ub-IbM) Ang(Uc-IcM)

of phase A current and phase B current Angle of phase B current and phase C current Angle of phase C current and phase A current Angle of phase A voltage and phase A current Angle of phase B voltage and phase B current Angle of phase C voltage and phase C current Angle of phase A voltage and phase B voltage Anglhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949e of phase B voltage and phase C voltage Angle of phase C voltage and phase A voltage Angle of phase-to-phase voltage Uab and line voltage Angle of the zero sequence voltage and current Angle of phase A voltage and metering phase A current Angle of phase B voltage and metering phase B current Angle of phase C voltage and metering phase C current

Primary protection measurement data No. 1 2 3 4 5 6 8 9 10

Ib Ic 3I0 I1 I2 Ua Ub Uc

value of the phase A from protection CT Current value of the phase B from protection CT Current value of the phase C from protection CT Zero sequence current value Positive sequence current value Negative sequence current value Sensitive zero sequence current value Voltage value of phase A from busbar VT Voltage value of phase B from busbar VT Voltage value of phase C from busbar VT Line voltage value

NARI-RELAYS ELECTRIC COhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949., LTD

Chapter 6 HMI Operation Introduction

13 14 15 16 17

Ubc Uca 3U0 U1 U2

value of phase A to phase B Voltage value of phase B to phase C Voltage value of phase C to phase A Zero sequence voltage value Positive sequence voltage value Negative sequence voltage value System frequency

Primary metering data No. 1 2 3 4 5 6 7 8 9 10 11

_M Ib_M Ic_M 3I0_M Ua_M Ub_M Uc_M Uab_M Ubc_M Uca_M 3U0_M

value of the phase A from metering CT Current value of the phase B by self-calculation Current value of the phase C from metering CT Zero sequence current value

value of phase A from busbar VT Voltage value of phase B from busbar VT Voltage value of phase C from busbar VT Voltage value of phase A to phase B Voltage value of phase B to phase C Voltage value of phase C to phase A Zero sequence voltage value Syshttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949tem frequency Active power Reactive power Output active energy Incoming active energy Output reactive energy Incoming reactive energy

17 18 19

_Out KWH_In KVAH_Out KVAH_In

Φfactor

Regular Binary input state No.

input 1 Binary input 2 Binary input 3 Binary input 4 Binary input 5 Binary input 6 Binary input 7 Binary input 8 Binary input 9 Binary input 10 Binary input 11

NARI-RELAYS ELECTRIC CO., LTD

Chapter 6 HMI Operation Introduction

input 12 Binary input 13 Binary input 14 Binary input 15 Binary input 16 Binary input 17 Binary input 18 Binary input 19 Binary input 20 Binary input 21

Protection binary input state No.

position of the circuit breaker.

output contact indicating CB is in open status. An output contact indicating CB is in closhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949e status. An output contact indicating CB is closed manually. Binary input of the enabling UV protection signal. Binary input of the BFI protection external initiation signal. Binary input of the blocking OC1 protection signal. Binary input of the blocking OC2 protection signal. Binary input of the blocking OC3 protection signal. Binary input of the blocking OC4 protection signal. Binary input of the enabling remote control function signal. Binary input of the blocking auto-recloser signal. Binary input of the enabling UFLS protection signal. Binary input of the tripping low pressure signal. Binary input of the closing low pressure signal. Binary input of the signal resetting signal. Binary input of the device maintenance signal.

virtual binary input indicating protection tripping which will

until it is acknowledged manually.

virtual binary input indicating protection reclosing which will hold untilhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 it is acknowledged manually.

virtual binary input indicating the auto-recloser is ready. A signal issued when the device can not receive GPS signal. Binary input of the triggering oscillography signal.

signal indicates the interlock conditions of the No.1 remote opening output.

signal indicates the interlock conditions of the No.1 remote closing output.

signal indicates the interlock conditions of the No.2 remote opening output.

NARI-RELAYS ELECTRIC CO., LTD

7 8 9 10 11 12 13

_UV BI_Blk_OC1 BI_Blk_OC2 BI_Blk_OC3 BI_Blk_OC4 EBI_TeleCtrl EBI_Lockout EBI_UFLS 20 21 22

_Ready_AR BI_LossGPS BI_TrigOscillog

Chapter 6 HMI Operation Introduction

30 31 32 A signal indicates the interlock conditions of the No.2 remote

[此处图片未下载成功]

closing output.

signal indicates the interlock conditions of the No.3 remote http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949opening output.

signal indicates the interlock conditions of the No.3 remote closing output.

signal indicates the No.1 programmable logic element output.A signal indicates the No.2 programmable logic element output.A signal indicates the No.3 programmable logic element output.A signal indicates the No.4 programmable logic element output.

_ProgBO1 Input_ProgBO2 Input_ProgBO3 Input_ProgBO4

: The programmable element is provided to program a logic element (tripping element, alarm element or blocking element etc.) according to the practical engineering demand. All the four programmable logic elements can be configured through the PCS-PC configuration tool.

Self supervision state

Section 6.3.3, “1” means the alarm signal exists, “0” means the alarm signal disappears. z Output relay state No. 1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20

_Relay NRhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe49494301_04n05 NR4301_06n07 NR4301_08n09 NR4301_10n11 NR4301_12n13 NR4301_14n15 NR4301_16n17 NR4301_18n19 NR4521_01n02 NR4521_03n04 NR4521_05n06 NR4521_07n08 NR4521_09n10 NR4521_11n12 NR4521_13n14 NR4521_15n16 NR4521_17n18 NR4521_19n20 NR4521_21n22

state of the fault detector output relay.

state of the 04&amp;05 output relay on the NR4301 module. The state of the 06&amp;07 output relay on the NR4301 module. The state of the 08&amp;09 output relay on the NR4301 module. The state of the 10&amp;11 output relay on the NR4301 module. The state of the 12&amp;13 output relay on the NR4301 module. The state of the 14&amp;15 output relay on the NR4301 module. The state of the 16&amp;17 output relay on the NR4301 module. The state of the 18&amp;19 output relay on the NR4301 module. The state of the 01&amp;02 output relay on the NR4521 module. The state of the 03&amp;04 output relay on the NR4521 modulehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949. The state of the 05&amp;06 output relay on the NR4521 module. The state of the 07&amp;08 output relay on the NR4521 module. The state of the 09&amp;20 output relay on the NR4521 module. The state of the 11&amp;12 output relay on the NR4521 module. The state of the 13&amp;14 output relay on the NR4521 module. The state of the 15&amp;16 output relay on the NR4521 module. The state of the 17&amp;18 output relay on the NR4521 module. The state of the 19&amp;20 output relay on the NR4521 module. The state of the 21&amp;22 output relay on the NR4521 module.

NARI-RELAYS ELECTRIC CO., LTD 75

Chapter 6 HMI Operation Introduction

GOOSE state No. 1 3 5

_goose_in1 close_goose_in1 goose_iloc1

state of the No.1 GOOSE tripping input. The state of the No.1 GOOSE closing input. The state of No.1 GOOSE interlocking input Whether the No.1 GOOSE interlocking ihttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949nput is valid. ……

state of No.10 GOOSE interlocking input Whether the No.10 GOOSE interlocking input is valid. The GOOSE element alarms.

link of GOOSE port A is broken down. The link of GOOSE port B is broken down.

the No.1 GOOSE tripping input is valid. Whether the No.1 GOOSE closing input is valid. 23 25 26 27

_iloc10 Goose_BJ

_a_link_down Goose_b_link_down 6.6 View Software Version

program version of this relay and all the module information can be known through this menu. Take viewing the program version data as an example. Operating steps:

. Turn key “MENU” to enter the main menu.

. Turn key “MENU” to locate the cursor on the submenu “VERSION” and press key “ENT” to

this submenu.

[此处图片未下载成功]

3. Turn key “MENU” to locate the cursor on the submenu “VERSION” and press key “ENT” to

[此处图片未下载成功]

enthttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949er this submenu. 4. Turn key “MENU” to view the software version information.

6.6-1 LCD display of the software version

：It is only a sample which is used to explain the indication of the software version menu. The software version of the device of the practical engineering should be taken as

NARI-RELAYS ELECTRIC CO., LTD

Chapter 6 HMI Operation Introduction

and binding.

.7 View History Reports

device can record and store the history reports which include the protection tripping reports,

self supervision reports and the binary input change reports etc. It provides convenience for viewing the history reports at any time.

.7.1 View History Trip Reports

history trip report stores the trip elements, trip time and waveform of a selected trip report. Operating steps:

. Turn key “MENU” to enter the main menuhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949.

. Turn key “MENU” to locate the cursor on the submenu “REPORT” and press key “ENT” to

this submenu. 3. Turn key “MENU” to locate the cursor on the submenu “TRP_REPORT” and press key “ENT”

enter this selected submenu, If there is no report in the selected submenu, it will show “No Valid Report!” on the LCD. 4. Turn key “MENU” to view the expected history trip report and press key “ENT” to show details

the selected trip report. 5. Press key “ENT” again to show the waveform of the selected trip report.

.7.2 View History Alarm Reports

history alarm report stores the alarm elements and alarm time. Operating steps:

. Turn key “MENU” to enter the main menu.

. Turn key “MENU” to locate the cursor on the submenu “REPORT” and press key “ENT” to

this submenu. 3. Turn key “MENU” to locate the cursor on the submenu “ALM_REPORT” and press key “ENT”

://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949parto enter this selected submenu, If there is no report in the selected submenu, it will show “No Valid Report!” on the LCD. 4. Turn key “MENU” to view the expected history alarm report.

.8 Operation through Keypad

.8.1 Password Protection

the safety purpose, this device provides password protection function for modifying the configuration (settings and parameters) and deleting the history reports. Only the inputted

NARI-RELAYS ELECTRIC CO., LTD

Chapter 6 HMI Operation Introduction

is correct, the relevant operation can be done.

password is fixed, and it is “111”. If the inputted password is correct, the relevant operation can be done; otherwise, it will show the input interface on the LCD to prompt the user to input the password again.

.8.2 Change the Settings

settings can be modified through the local HMI to meet the demhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949and of practical engineering. Operating steps:

. Refer the Section 6.4 to locate the cursor on the expected setting, and then press key “ENT”

enter the setting modification state. 2. Turn key “MENU” to locate the cursor on the expected digital place, and then turn key

“ADJUST” to change the number to an expected number, and press key “ENT” to finish a single selected setting. Do it again and again to modify other settings. 3. After finishing the setting modification, press key “ESC” to prompt the user whether to save

settings. Select “Yes” to confirm to save the modified settings. Then a password input interface is shown on the LCD. Input the correct password and press key “ENT” to confirm the modification. If the modification is given up, press key “ESC” to exit the modification operation. 4. After confirming the setting modification, it will show “Saving Settings…” on the LCD. Then the

://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ar[此处图片未下载成功]

device will restart, and the new settings will be in service.

: It is necessary to certify the entered settings are correct absolutely before confirming the setting modification.

.8.3 Clock Set

the clock of this relay as following steps. Operating steps:

. Turn key “MENU” to enter the main menu.

. Turn key “MENU” to locate the cursor on the submenu “LOCAL_CTRL” and press key “ENT”

enter this submenu. 3. Turn key “MENU” to locate the cursor on the submenu “CLOCK” and press key “ENT” to enter

selected submenu. 4. Turn key “MENU” to locate the cursor on the expected digital place, and then turn key

“ADJUST” to change the number to an expected number. 5. After finishing the clock modification, press key “ENT” to confirm the modification. The clock modification interface is shown as below.

NARI-RELAYS ELECTRIC COhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949., LTD

Chapter 6 HMI Operation Introduction

6.8-1 Clock modification interface

.9 Understand the Alarms

circuit and operation condition of the equipment are self-supervised continuously. If any

condition is detected, information or report will be displayed and a corresponding alarm will be issued.

common abnormality may block a certain number of protection functions while other functions can still work.

, if serious hardware failure or abnormality were detected, all protection functions will be blocked and the LED “HEALTHY” will be turned off.

hardware failure is detected, all protection functions will be blocked and corresponding alarm signal will be issued. The equipment then cannot work normally in this case and manual maintenance is required to fix the failure.

[此处图片未下载成功]

NOTE: If the equipment is blocked or alahttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949rm signal is issued during operation, do please find out its reason by help of the history reports. If the reason can not be found on site, please inform the manufacturer NARI-RELAYS.

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

79

Chapter 6 HMI Operation Introduction

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 7 Settings

7 Settings

.1 Overview

settings are used to determine the characteristic of each protective element and operation mode of the relay. It is necessary to configure the settings of this relay according to engineering demands before putting this relay into service. If the settings are not configured correctly, the relay maybe work abnormally (such as communication interrupted, printing out unexpected codes etc.), even sometimes much more serious accident will occur (such as unwanhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ted operation, missing operation).

settings of this relay include system settings, protection settings, communication settings and miscellaneous settings. The user can configure these settings or parameters manually (see Section 6.8.2 “Change the Settings”). Remote modification is also supported (IEC60870-5-103 interface or IEC61850 interface, see Chapter 8 “Communication”).

[此处图片未下载成功]

NOTE: If a CPU module is replaced, it is necessary to configure all the settings again according to the configuration of the CPU module which is replaced.

.2 System Settings

system settings (in submenu “SYSTEM_SETTING”) are mainly used to set the rated value of VT and CT.

following table lists all the system parameters. No.

text

information of the setting file Rated primary value of protection CT Rated secondary value of http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949protection CT Rated primary value of metering CT Rated secondary value of metering CT Rated primary value of neutral CT Rated secondary value of neutral CT Rated primary value of sensitive neutral CT Rated secondary value of sensitive neutral CT Rated primary value of VT of busbar Rated secondary value of VT of busbar Rated primary value of VT of line Rated secondary value of VT of line

sequence line reactance of secondary side Positive sequence line resistance of secondary side

&lt; 16 Characters 1~6000A 1/5A 1~6000A 1/5A 1~6000A 1/5A 1~6000A 1/5A 0~121.0kV 57.7~110V 0~121.0kV 57.7~110V 0.01~600  0.01~600

5

n_CT_Meter I2n_CT_Meter

n_CT_NP

n_CT_SEF

12 13 14 15

n_VT_Bus U1n_VT_Fdr U2n_VT_Fdr X1L R1L

NARI-RELAYS ELECTRIC CO., LTD 81

Chapter 7 Settings

[此处图片未下载成功]

17 18://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949rL R0L LineLength

sequence line reactance of secondary side Zero sequence line resistance of secondary side Total length of the line

sequence current is self calculated 0:from neutral CT  1:self calculated 0: traditional CT&amp;VT; 1: electronic CT&amp;VT CT wiring form

: three-phase CT  1: two-phase CT (A &amp; C) Select the rated system frequency 0: 50Hz  1: 60Hz

.01~600

[此处图片未下载成功]

0.01~600  0~600km 0/1 0/1 0/1 0/1

_Mode

:

. System settings is related to the protection activities, thus it is necessary to configure theses

according to actual conditions. 2. Of calculated zero sequence current (Opt_Calc_3I0): calculated zero sequence current is

for tripping and alarm and can not be used for selecting earthed line. Set the value of [Opt_Calc_3I0] as “1” means that zero sequence current is calhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949culated by equipment, and set the value as 0 means that zero sequence current is derived from specific CT (incoming from terminal 0317~0318). The default value is “0” when the equipment delivered. 3. Of CT wiring form (Opt_CT_Prot): Two methods are used to calculate the real time power in

relay. The first method is based on the three-phase current and the three-phase voltage, and the second method is based on the A and C phase current and the three-phase voltage. Set the setting [Opt_CT_Prot] as “0” means the first method is adopted, and set the setting [Opt_CT_Prot] as “1” means the second method is adopted. The default value is “0” when the equipment delivered.

.3 Protection Settings

are up to 10 groups of protection settings in this relay. The protection settings (in submenu “PROTECT_SETTING”) are used to determine the characteristic of each protection. All the protection settings of this relahttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949y are listed in following table. No.

text

of the negative sequence voltage blocking overcurrent element (phase voltage)

of the low voltage blocking overcurrent element (phase-to-phase voltage)

of the stage 1 overcurrent protection Setting of the stage 2 overcurrent protection Setting of the stage 3 overcurrent protection Setting of the stage 4 overcurrent protection

Step

4 5 6

_OC1 I_OC2 I_OC3 I_OC4

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 7 Settings

8

_OC_SOTF I_OvLd

of the SOTF overcurrent protection Setting of the overload protection

of the stage 1 zero sequence overcurrent protection

of the stage 2 zero sequence overcurrent protection

of the stage 3 zero sequhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ence overcurrent protection

of the zero sequence SOTF overcurrent protection

of the frequency alarm element Setting of the UFLS protection

of low voltage blocking element of UFLS (phase-to-phase voltage)

of frequency rate change blocking element of the UFLS protection

for the overcurrent of the stage 2 BFI protection

of the stage 1 undervoltage protection Setting of the stage 2 undervoltage protection Setting of the stage 1 overvoltage protection Setting of the stage 2 overvoltage protection Setting of the broken conductor protection Setting of the CT supervision threshold

of phase current

of negative sequence current

of the synchronism check angle of the auto-recloser

OC protection

.1In~3In 0.01In ~1In 0.01In ~1http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949In

.01A 0.01A 0.01A

16

_Alm_UF f_UF_UFLS

~60Hz 45~60Hz

.01Hz 0.01Hz

22 23 24 25 26

_UV1 V_UV2 V_OV1 V_OV2 Ratio_I2/I1 I_CTS

~110V 2~110V 57.7~160V 57.7~160V 0.1~1.0 0.01In~40In

.01V 0.01V 0.01V 0.01V 0.2 0.1A

_OC2

.01s

~100s

NARI-RELAYS ELECTRIC CO., LTD 83

Chapter 7 Settings

[此处图片未下载成功]

_OvLd

delay setting of the overload protection Time delay setting of the stage 1 sensitive earth fault protection

delay setting of the stage 2 sensitive earth fault protection

delay setting of the stage 1 zero sequence overcurrent protection

delay setting of the stage 2 zero sequence overcurrent protection

delay setting of the stage 3 zero sequencehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 overcurrent protection

delay setting of the zero sequence SOTF overcurrent protection

delay setting of the UFLS protection Time delay setting of the 1st shot auto-recloser Time delay setting of the 2nd shot auto-recloser Time delay setting of the 3rd shot auto-recloser Time delay setting of the 4th shot auto-recloser Reclaim time setting of the auto-recloser

~100s

.01s

45 46 47 48 49

_UFLS t_AR1 t_AR2 t_AR3 t_AR4 t_Reclaim

~100s 0~9s 0~600s 0~600s 0~600s 0-600s

.01s 0.01s 0.01s 0.01s 0.01s 0.01s

52

_BFI1 t_BFI2

width of Time delay setting of the stage 1 BFI protection Time delay setting of the stage 2 BFI protection Time delay setting of the stage 1 undervoltage protection

delay setting of the stage 2 undervoltage protection

time settihttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ng of the SOTF protection The minimum time for wave recorder IDMT overcurrent protection

~100s 0~100s

.01s 0.01s

59

_En_SOTF t_MinRecWave

-100s 0-6000ms 1:standard

.0s 1ms 1

a inverse curve when the OC3 is used as 1~3

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 7 Settings

_2ndHarm

a inverse curve when the ROC2 is used as 2:very zero sequence IDMT overcurrent protection Time multiplier setting for the IDMT overcurrent protection

protection

Ratio of second harmonic in foundation current or fault current

shot number setting of the auto-recloser. influenced by second harmonic

matrix setting to configure which element can initiate the breaker failure protection

matrix setting to configure which element can initiate the auto-reclohttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ser

matrix setting to configure which element can block the auto-recloser

matrix setting to configure which element can be blocked after the shot 1 auto-recloser operatesThe matrix setting to configure which element can be blocked after the shot 2 auto-recloser operatesThe matrix setting to configure which element can be blocked after the shot 3 auto-recloser operatesThe matrix setting to configure which element can be blocked after the shot 4 auto-recloser operatesThe matrix setting 1 of the output NR4521_01n02 The matrix setting 1 of the output NR4521_03n04 The matrix setting 1 of the output NR4521_05n06 The matrix setting 1 of the output NR4521_07n08 The matrix setting 1 of the output NR4521_09n10 The matrix setting 1 of the output NR4521_11n12 The matrix setting 1 of the output NR4521_13n14 The matrix setting 1 of the output NR4521_15n16 The matrix setting 1 of the output NR4521_17n18 The matrix settinghttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 1 of the output NR4521_19n20 The matrix setting 1 of the output NR4521_21n22 The matrix setting 2 of the output NR4521_01n02 The matrix setting 2 of the output NR4521_03n04 The matrix setting 2 of the output NR4521_05n06 The matrix setting 2 of the output NR4521_07n08 The matrix setting 2 of the output NR4521_09n10 The matrix setting 2 of the output NR4521_11n12

:extremely

.01~1

.01

_AR

~ 4 0xFFFF 0x00000000 ~0xFFFFFFFF 0x00000000 ~0xFFFFFFFF 0x00000000 ~0xFFFFFFFF 0x00000000 ~0xFFFFFFFF 0x00000000 ~0xFFFFFFFF 0x00000000 ~0xFFFFFFFF 0x00000000 ~0xFFFFFFFF 0x00000000

~ 0xFFFFFFFF

1 1 1 1 1 1 1 1 1

76 77 78 79 80 81 82 83 84 85 86 87 88 89 90 91

_NR4521_01n02_1 Cfg_NR4521_03n04_1 Cfg_NR4521_05n06_1 Cfg_NR4521_07n08_1 Cfg_NR4521_09n10_1 Cfg_NR4521_11n12_1 Cfg_NR4521_13n14_1 Cfg_NR4521_15n16_1 Cfg_NR4521_17n18_1 Cfg_NR4521_19n20_1 Cfg_NRhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe49494521_21n22_1 Cfg_NR4521_01n02_2 Cfg_NR4521_03n04_2 Cfg_NR4521_05n06_2 Cfg_NR4521_07n08_2 Cfg_NR4521_09n10_2 Cfg_NR4521_11n12_2

X0000~

NARI-RELAYS ELECTRIC CO., LTD 85

Chapter 7 Settings

[此处图片未下载成功]

93 94 95 96 97 98 99 100 101 102 103 104 105 106 107 108

_NR4521_13n14_2 Cfg_NR4521_15n16_2 Cfg_NR4521_17n18_2 Cfg_NR4521_19n20_2 Cfg_NR4521_21n22_2 Cfg_NR4301_08n09_1 Cfg_NR4301_10n11_1 Cfg_NR4301_12n13_1 Cfg_NR4301_14n15_1 Cfg_NR4301_16n17_1 Cfg_NR4301_18n19_1 Cfg_NR4301_08n09_2 Cfg_NR4301_10n11_2 Cfg_NR4301_12n13_2 Cfg_NR4301_14n15_2 Cfg_NR4301_16n17_2 Cfg_NR4301_18n19_2

matrix setting 2 of the output NR4521_13n14 The matrix setting 2 of the output NR4521_15n16 The matrix setting 2 of the output NR4521_17n18 The matrix setting 2 of the output NR4521_19n20 The matrix setting 2 of the output NR4521_21n22 The matrix setting 1 of the output NR4301_08n09 Thhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949e matrix setting 1 of the output NR4301_10n11 The matrix setting 1 of the output NR4301_12n13 The matrix setting 1 of the output NR4301_14n15 The matrix setting 1 of the output NR4301_16n17 The matrix setting 1 of the output NR4301_18n19 The matrix setting 2 of the output NR4301_08n09 The matrix setting 2 of the output NR4301_10n11 The matrix setting 2 of the output NR4301_12n13 The matrix setting 2 of the output NR4301_14n15 The matrix setting 2 of the output NR4301_16n17 The matrix setting 2 of the output NR4301_18n19 The holding time of the output NR4521_01n02 The holding time of the output NR4521_03n04 The holding time of the output NR4521_05n06 The holding time of the output NR4521_07n08 The holding time of the output NR4521_09n10 The holding time of the output NR4521_11n12 The holding time of the output NR4521_13n14 The holding time of the output NR4521_15n16 The holding time of the output NR4521_17n18 The holding time of http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949the output NR4521_19n20 The holding time of the output NR4521_21n22 The holding time of the output NR4301_08n09 The holding time of the output NR4301_10n11 The holding time of the output NR4301_12n13 The holding time of the output NR4301_14n15 The holding time of the output NR4301_16n17 The holding time of the output NR4301_18n19 The pick-up time of binary input 1 The pick-up time of binary input 2 The pick-up time of binary input 3 The pick-up time of binary input 4 The pick-up time of binary input 5 The pick-up time of binary input 6 The pick-up time of binary input 7 The drop-off time of binary input 1 The drop-off time of binary input 2

~ 10000ms

ms

~ 10000ms

ms

~999ms 999: latched

ms

~999ms 999: latched

ms

111 112 113 114 115 116 117 118 119

_PW_NR4521_03n04 t_PW_NR4521_05n06 t_PW_NR4521_07n08 t_PW_NR4521_09n10 t_PW_NR4521_11n12 t_http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949PW_NR4521_13n14 t_PW_NR4521_15n16 t_PW_NR4521_17n18 t_PW_NR4521_19n20 t_PW_NR4521_21n22

127 128 129 130 131 132 133 134 86

_BI1_PU t_BI2_PU t_BI3_PU t_BI4_PU t_BI5_PU t_BI6_PU t_BI7_PU t_BI1_DO t_BI2_DO

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 7 Settings

136 137 138 139

_BI3_DO t_BI4_DO t_BI5_DO t_BI6_DO t_BI7_DO

drop-off time of binary input 3 The drop-off time of binary input 4 The drop-off time of binary input 5 The drop-off time of binary input 6 The drop-off time of binary input 7

logical settings are used to enable or disable the relevant protection.

* 2* 3* 4* 6 7 8 9

_OC1 En_OC2 En_OC3 En_OC4

/disable the stage 1 overcurrent protection Enable/disable the stage 2 overcurrent protection Enable/disable the stage 3 overcurrent protection Enable/disable the stage 4 overcurrent protection Enhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949able/disable the IDMT overcurrent protection

/disable the VCE of the stage 1 overcurrent protection Enable/disable the VCE of the stage 2 overcurrent protection Enable/disable the VCE of the stage 3 overcurrent protection Enable/disable the VCE of the stage 4 overcurrent protection Enable/disable the directional element for the stage 1 overcurrent protection

/disable the directional element for the stage 2 overcurrent protection

/disable the directional element for the stage 3 overcurrent protection

/disable the directional element for the stage 4 overcurrent protection

/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1

the directional mode of the DOCx (x: 1~4) protection 1: forward direction; 0: reverse direction

/1 0/1 0/1

/disable VT circuit supervision function

/disable the overcurrent elements which are dependent http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949on voltage when VT is failed.

/disable CT circuit supervision function

/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1

_VCE_OC1 En_VCE_OC2 En_VCE_OC3 En_VCE_OC4

_VTS

21* 22*

_CTS

SOTF overcurrent protection En_ROC_SOTF

/disable the zero sequence SOTF overcurrent protection Select the acceleration tripping mode of the SOTF protection. 1: accelerated tripping before auto-reclosing 0: accelerated tripping after auto-reclosing Enable/disable overload protection

/disable the stage 1 sensitive earth fault protection Enable/disable the stage 2 sensitive earth fault protection Enable/disable the stage 1 zero sequence overcurrent protection Enable/disable the stage 2 zero sequence overcurrent protection Enable/disable the stage 3 zero sequence overcurrent protection Enable/disable the zero sequence IDMT overcurrent protection

://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ar24* 25* 26* 27* 28* 29* 30

_OvLd En_SEF1 En_SEF2 En_ROC1 En_ROC2 En_ROC3 En_InvROC

NARI-RELAYS ELECTRIC CO., LTD 87

Chapter 7 Settings

[此处图片未下载成功]

*

_UFLS

overcurrent protection

[此处图片未下载成功]

sequence overcurrent protection

overcurrent protection

the directional mode of the DROCx (x:1~3) protection 1: forward direction; 0: reverse direction Enable/disable the UFLS protection

/disable frequency rate-change blocking element of the UFLS protection

/disable the auto-recloser

/disable the synchronism check function Enable/disable the line-dead check function Enable/disable the stage 1 BFI protection Enable/disable the stage 2 BFI protection

/disable the breaker failure protection with the control of the circuit breaker state

/disable the brehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949aker failure protection with the control of the relay operation

/disable the breaker failure protection with the control of the external binary input

/disable the stage 1 undervoltage protection Enable/disable the stage 2 undervoltage protection Select the undervoltage calculation method

the busbar voltage input mode for the UV protection Enable/disable the stage 1 overvoltage protection Enable/disable the stage 2 overvoltage protection Select the overvoltage calculation method

the busbar voltage input mode for the OV protection

/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1

* 41 42* 43

_AR

_DeadChk_AR En_BFI1 En_BFI2

* 48* 49 50 51* 52* 53 54 55*

_UV1 En_UV2

_UV_SinglePh Opt_UV_VTMode En_OV1 En_OV2

_OV_SinglePh Opt_OV_VTMode

broken conductor protechttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949tion

/disable blocking the broken conductor protection when the current transformer is failed

/disable the harmonic blocking OCEF function

_HarmBlkOC/ROC

:

. Before configuring the settings, setting group must be configured first.

. When a certain setting is of no use, in case of over-elements (such as overcurrent, residual

), set the value as upper limit; in case of under-elements (such as under frequency, under voltage), set the value as lower limit; set the corresponding time as 100s and disable corresponding protection element and de-energize the corresponding binary input.

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 7 Settings

. In general, for switch onto fault protection and accelerated protection, it is necessary to set a

delay from decades to 100 milliseconds. Thahttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949nks to there is no 100ms time-delay in the numerical protection equipment as there in the traditional protection equipment in the past, thus it can not avoid surge current when CB is closing if the time is set as 0.00s. For residual overcurrent when switch-onto-fault and residual accelerate protection, there is zero sequence surge current when CB is closing. 4. The tripping matrix settings [Cfg_NR4521_01n02_1] to [Cfg_NR4521_21n22_1] and

[Cfg_NR4521_01n02_2] to [Cfg_NR4521_21n22_2] are used to program the output matrix of board NR4521. Each setting of them is a 32-bit binary number, and each bit can configure a protective, alarm or remote control output. They must be set according to the practical engineering demand. At the same time, the settings [Cfg_NR4301_08n09_1] to [Cfg_NR4301_18n19_1] and [Cfg_NR4301_08n09_2] to [Cfg_NR4301_18n19_2] are used for board NR4301. Take an example as below.

[此处图片未下载成功]

Fihttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949gure 7.3-1 Binary structure of the output matrix

relationship table of each bit and relevant output element of [Cfg_NR4521_xxnxx_1] and [Cfg_NR4301_xxnxx_1] is shown as below.

No.

1 2 3 4 5 6 7 8 9 10 11 12 13 14

element for output

auto-recloser closing output

stage 1 overcurrent protection tripping output The stage 2 overcurrent protection tripping output The stage 3 overcurrent protection tripping output The stage 4 overcurrent protection tripping output The IDMT overcurrent protection tripping output The SOTF overcurrent protection tripping output The overload protection tripping output

stage 1 sensitive earth fault protection tripping output The stage 2 sensitive earth fault protection tripping output The stage 1 zero sequence overcurrent protection tripping output The stage 2 zero sequence overcurrent protection tripping output The stage 3 zero http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949sequence overcurrent protection tripping output The zero sequence IDMT overcurrent protection tripping output The zero sequence SOTF overcurrent protection tripping output

NARI-RELAYS ELECTRIC CO., LTD 89

Chapter 7 Settings

[此处图片未下载成功]

16 17 18 19 20 21 22

UFLS protection tripping output The stage 1 BFI protection tripping output The stage 2 BFI protection tripping output

stage 1 undervoltage protection tripping output The stage 2 undervoltage protection tripping output The stage 1 overvoltage protection tripping output The stage 2 overvoltage protection tripping output The broken conductor protection tripping output

st remote tripping output 1st remote closing output 2nd remote tripping output 2nd remote closing output 3rd remote tripping output 3rd remote closing output

relationship table of each bit and relevant output elemenhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949t in [Cfg_NR4521_xxnxx_2] is

as below.

No.

1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 21 22 23 24

element for output

auto-recloser operating pickup output The stage 1 overcurrent protection pickup output The stage 2 overcurrent protection pickup output The stage 3 overcurrent protection pickup output The stage 4 overcurrent protection pickup output The IDMT overcurrent protection pickup output The SOTF overcurrent protection pickup output The overload protection pickup output

stage 1 sensitive earth fault protection tripping output The stage 2 sensitive earth fault protection tripping output The stage 1 zero sequence overcurrent protection pickup output The stage 2 zero sequence overcurrent protection pickup output The stage 3 zero sequence overcurrent protection pickup output The zero sequence IDMT overcurrent protection pickup output The zero sequenhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ce SOTF overcurrent protection pickup output The UFLS protection pickup output The stage 1 BFI protection pickup output The stage 2 BFI protection pickup output

stage 1 undervoltage protection pickup output The stage 2 undervoltage protection pickup output The stage 1 overvoltage protection pickup output The stage 2 overvoltage protection pickup output The broken conductor protection pickup output The GOOSE tripping output The GOOSE closing output

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 7 Settings

relationship table of each bit and relevant output element in [Cfg_NR4301_xxnxx_2] is shown as below.

No.

1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 21 22 23 24 25 26 27 28

element for output

[此处图片未下载成功]

The auto-recloser operating pickup output The stage 1 overcurrent protection pickup output The stagehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 2 overcurrent protection pickup output The stage 3 overcurrent protection pickup output The stage 4 overcurrent protection pickup output The IDMT overcurrent protection pickup output The SOTF overcurrent protection pickup output The overload protection pickup output

stage 1 sensitive earth fault protection tripping output The stage 2 sensitive earth fault protection tripping output The stage 1 zero sequence overcurrent protection pickup output The stage 2 zero sequence overcurrent protection pickup output The stage 3 zero sequence overcurrent protection pickup output The zero sequence IDMT overcurrent protection pickup output The zero sequence SOTF overcurrent protection pickup output The UFLS protection pickup output The stage 1 BFI protection pickup output The stage 2 BFI protection pickup output

stage 1 undervoltage protection pickup output The stage 2 undervoltage protection pickup output The stage 1 ohttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949vervoltage protection pickup output The stage 2 overvoltage protection pickup output The broken conductor protection pickup output The GOOSE tripping output The GOOSE closing output

No.1 programmable logic element output The No.2 programmable logic element output The No.3 programmable logic element output The No.4 programmable logic element output

: The programmable logic elements can be configured through the PCS-PC configuration tool. If a programmable logic element is not used for signal output through anyone of the binary outputs, the corresponding bit should be set as “0”; and if a programmable logic element is configured for outputting a signal which is not for tripping through the power supply module (NR4301), it is strongly recommended other tripping outputs should not be configured on the same module.

method: If a certain element output at a certain group of output contacts, sehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949t the blank as “1” at the cross between the operation element (column) and the tripping out relay (row) in Figure 7.3-1.

NARI-RELAYS ELECTRIC CO., LTD

Chapter 7 Settings

[此处图片未下载成功]

example, if the stage 2 overcurrent element tripping output signal is sent out through the output “NR4521_05n06”, set the black as “1” at the cross between the No.3 row (starting with “1”) and the No.2 column (starting with “0”). So the setting “Cfg_NR4521_05n06_1” set as “0x00000003”.

. The matrix setting [Cfg_Harm_Blk] is used to select which element is controlled by the second

blocking element. Following table shows the relationship of each bit and relevant element.

No.

1 2 3 4 5 6 7 8

element with control of second harmonic blocking element

stage 1 overcurrent protection, including DT &amp; IDMT OC protection Thehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 stage 2 overcurrent protection The stage 3 overcurrent protection The stage 4 overcurrent protection The stage 1 sensitive earth fault protection The stage 2 sensitive earth fault protection

stage 1 zero sequence overcurrent protection, including DT &amp; IDMT ROC protectionThe stage 2 zero sequence overcurrent protection The stage 3 zero sequence overcurrent protection

. The matrix setting [Cfg_IntInitBFI] is used to select which element can initiate the breaker

protection. Following table shows the relationship of each bit and relevant element.

No.

1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19

element for BFI internal initiation

stage 1 overcurrent protection tripping element The stage 2 overcurrent protection tripping element The stage 3 overcurrent protection tripping element The stage 4 overcurrent protection tripping element The IDMT overhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949current protection tripping element The SOTF overcurrent protection tripping element The overload protection tripping element The stage 1 sensitive earth fault protection The stage 2 sensitive earth fault protection

stage 1 zero sequence overcurrent protection tripping element The stage 2 zero sequence overcurrent protection tripping element The stage 3 zero sequence overcurrent protection tripping element The zero sequence IDMT overcurrent protection tripping element The zero sequence SOTF overcurrent protection tripping element The UFLS protection tripping element

stage 1 undervoltage protection tripping element The stage 2 undervoltage protection tripping element The stage 1 overvoltage protection tripping element The stage 2 overvoltage protection tripping element The broken conductor protection tripping element

. The matrix setting [Cfg_InitAR] is used to select which element can initiate the ahttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949uto-recloser.

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 7 Settings

table shows the relationship of each bit and relevant element. Bit No.

1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 21

element for auto-recloser initiation

stage 1 overcurrent protection tripping element The stage 2 overcurrent protection tripping element The stage 3 overcurrent protection tripping element The stage 4 overcurrent protection tripping element The IDMT overcurrent protection tripping element The SOTF overcurrent protection tripping element The overload protection tripping element The stage 1 sensitive earth fault protection The stage 2 sensitive earth fault protection

stage 1 zero sequence overcurrent protection tripping element The stage 2 zero sequence overcurrent protection tripping element The stage 3 zero sequence overcurrehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949nt protection tripping element The zero sequence IDMT overcurrent protection tripping element The zero sequence SOTF overcurrent protection tripping element The UFLS protection tripping element

stage 1 breaker failure protection tripping element The stage 2 breaker failure protection tripping element The stage 1 undervoltage protection tripping element The stage 2 undervoltage protection tripping element The stage 1 overvoltage protection tripping element The stage 2 overvoltage protection tripping element The broken conductor protection tripping element

. The matrix setting [Cfg_BlkAR] is used to select which element can block the auto-recloser.

table shows the relationship of each bit and relevant element.

No.

1 2 3 4 5 6 7 8 9 10 11 12 13

element for blocking auto-recloser

stage 1 overcurrent protection tripping element The stage 2 overcurrenhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949t protection tripping element The stage 3 overcurrent protection tripping element The stage 4 overcurrent protection tripping element The IDMT overcurrent protection tripping element The SOTF overcurrent protection tripping element The overload protection tripping element The stage 1 sensitive earth fault protection The stage 2 sensitive earth fault protection

stage 1 zero sequence overcurrent protection tripping element The stage 2 zero sequence overcurrent protection tripping element The stage 3 zero sequence overcurrent protection tripping element The zero sequence IDMT overcurrent protection tripping element The zero sequence SOTF overcurrent protection tripping element

NARI-RELAYS ELECTRIC CO., LTD 93

Chapter 7 Settings

[此处图片未下载成功]

15 16 17 18 19 20 21

UFLS protection tripping element

stage 1 breaker failure protection tripping element The http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949stage 2 breaker failure protection tripping element The stage 1 undervoltage protection tripping element The stage 2 undervoltage protection tripping element The stage 1 overvoltage protection tripping element The stage 2 overvoltage protection tripping element The broken conductor protection tripping element

. The matrix setting [Cfg_ARxBlkProt] (x: 1~4) is used to select which element can be blocked

the shot x (x: 1~4) auto-recloser. Following table shows the relationship of each bit and relevant element.

No.

1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 21

element can be blocked by the auto-recloser

stage 1 overcurrent protection tripping element The stage 2 overcurrent protection tripping element The stage 3 overcurrent protection tripping element The stage 4 overcurrent protection tripping element The IDMT overcurrent protection tripping elemenhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949t The SOTF overcurrent protection tripping element The overload protection tripping element The stage 1 sensitive earth fault protection The stage 2 sensitive earth fault protection

stage 1 zero sequence overcurrent protection tripping element The stage 2 zero sequence overcurrent protection tripping element The stage 3 zero sequence overcurrent protection tripping element The zero sequence IDMT overcurrent protection tripping element The zero sequence SOTF overcurrent protection tripping element The UFLS protection tripping element

stage 1 breaker failure protection tripping element The stage 2 breaker failure protection tripping element The stage 1 undervoltage protection tripping element The stage 2 undervoltage protection tripping element The stage 1 overvoltage protection tripping element The stage 2 overvoltage protection tripping element The broken conductor protection tripping element

. Thehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 settings [t_PW_NR4521_01n02] to [t_PW_NR4521_21n22] and [t_PW_NR4301_08n09]

[t_PW_NR4301_18n19] are used to set the holding time of the output of the NR4521 module and NR4301 module. The range is 0ms to 999ms, and if the setting of a certain output is set as “999ms”, the corresponding output is a self-latched output. Especially, if a certain output is configured as remote control (tripping or closing) output, the holding time is 1000ms fixedly; no matter what the holding time setting of the corresponding output is. 11. See Section 3.7 and Section 3.8 for more details about the settings [Opt_UV_SinglePh],

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 7 Settings

[Opt_UV_VTMode], [Opt_OV_SinglePh] and [Opt_OV_VTMode].

. When the settings [En_SynChk_AR] and [En_DeadChk_AR] are both set as “0”, it means that

check when auto-reclosing. 13. The settingshttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 marked with “*” means that they have corresponding virtual enabling binary

. Virtual binary inputs can be modified on the remote terminal via communication. On the local control panel, all virtual enabling binary inputs can be set as “1” through the

“Virtual_Enabling_BI”.

. Only when the logic setting (such as listed in above table), the state of virtual enabling binary

and the state of enabling binary input are “1” at the same time, the corresponding protection element is valid, otherwise it is invalid.

.4 Communication Settings

communication settings (in submenu “Equip_Parameter”) are used for communication with substation monitoring system, substation controlling system or remote SCADA. The following table lists all the communication settings. No.

3 4 5 6 7 8 9

text

_ip portA_mask portB_ip portB_mask portC_ip portC_mask porthttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949D_ip portD_mask

address Ethernet port A IP Ethernet port A mask code Ethernet port B IP Ethernet port B mask code Ethernet port C IP Ethernet port C mask code Ethernet port D IP Ethernet port D mask code

-5-103 protocol

voltage value of the binary input Time synchronization mode

metering change differentiate percent for IEC61850 protocol The SNTP server address

binary input for IEC61850 protocol SCADA system for IEC60870-5-103 protocol IEC60870-5-103 protocol The time zone code

~65535

.000.000.000 ~255.255.255.255

12

_voltage IS_IRIG_B

~ 3000s

, 48, 110 or 220V 0: PPS 1: IRIG-B % 0~65535 1: related 1: permitted 1: blocked 0 ~ 23

_server_addr

_zone

the remote control object is related to 0: Unrelated Whether perhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949mit to modify the settings through 0: not permitted 0: not blocked

NARI-RELAYS ELECTRIC CO., LTD

Chapter 7 Settings

[此处图片未下载成功]

_Alm_TCCS

for pulse-width for the first telecontrol tripping relay

[此处图片未下载成功]

Setting for pulse-width for the first telecontrol closing relay

tripping relay

closing relay

for pulse-width for the third telecontrol tripping relay

for pulse-width for the third telecontrol closing relay

whether supervise the control circuit

.1~1000.0s 0.1~1000.0s 0.1~1000.0s 0.1~1000.0s 0.1~1000.0s 0.1~1000.0s 0/1

:

. Communication parameters may be determined by test engineer according to the actual field

. 2. The standard arrangement of Ethernet port is two, at most four (predetermined when

://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949rdering). Set the IP address according to actual arrangement of Ethernet numbers and the un-useful port/ports can not be configured. 3. When the IEC61850 protocol is adopted in substations, the setting [sntp_server_addr] can be

to appoint the address of the SNTP service provider in the same LAN. If the SNTP server provides unicast clock synchronization service, this setting can get from the SNTP server IP address; for example, the SNTP server IP address is “198.120.A.B”, then the setting is equal to A&#215;256 B. If the SNTP server provides broadcast clock synchronization service, this setting must be set as “65535”. If there is no SNTP service provided in the same LAN, this setting can be set as “0”. 4. Of circle time for sending telemetering (comm_telemeter_period): It represents the time

when the equipment sends metering data forwardly. When this setting is set as “0” means that the equipment will nothttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 send metering data at fixed time forwardly (at this time inquiry issued by SCADA still being responded). This setting may be set according to actual field condition and can be set as “0” when the communication function is un-useful. The default value is “0” when the equipment is delivered. 5. When the IEC61850 protocol is adopted in substations, if the time tags of communication

are required according to Greenwich Mean Time (GMT), the time zone code is used to set the current time zone that the relay stays in; for example, if a relay is applied in China, the time zone code of China is east 8th time zone, so this setting is set as “8”. If there does not have such a requirement, the time zone code must be set as “0”.

zone Setting

zone

1st

2nd

3rd

4th

5th

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949

Chapter 7 Settings

zone Setting Time zone Setting Time zone Setting

6th East/West 12th

6th East 7th West 1st West 7th

8th West 2ndWest 8th

9th West 3rd West 9th

10th West 4th West 10th

11th West 5th West 11th

.5 GOOSE Parameter

GOOSE parameters (in submenu “GOOSE_SETTING”) are used to set the GOOSE function

parameters.

following table lists all the GOOSE parameters. No.

2

text

[此处图片未下载成功]

goose_neta_ena goose_netb_ena

the Ethernet A of GOOSE module Enable the Ethernet B of GOOSE module Enable the No.1 GOOSE reception block Enable the No.2 GOOSE reception block Enable the No.3 GOOSE reception block Enable the No.4 GOOSE reception block Enable the No.5 GOOSE reception block Enable the No.6 GOOSE reception block Enable the No.7 GOhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949OSE reception block Enable the No.8 GOOSE reception block Enable the No.9 GOOSE reception block Enable the No.1 GOOSE transmission block Enable the No.2 GOOSE transmission block Enable the No.3 GOOSE transmission block Enable the No.4 GOOSE transmission block Enable the No.5 GOOSE transmission block Enable the No.6 GOOSE transmission block Enable the No.7 GOOSE transmission block Enable the No.8 GOOSE transmission block

/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1

:

. The settings [goose_neta_ena] and [goose_netb_ena] are used to enable the Ethernet

port A and port B of the GOOSE module respectively. 2. The setting [Goose_rx1_enable] is used to enable the GOOSE module to receive the No.1

block, and the No.1 data block includes the GOOSE tripping or closing information which are configured through a special configuration softwarhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949e tool. 3. The setting [Goose_tx1_enable] is used to enable the GOOSE module to transmit the No.1

NARI-RELAYS ELECTRIC CO., LTD

Chapter 7 Settings

[此处图片未下载成功]

block, and the No.1 data block includes the GOOSE tripping or closing information which are configured through a special configuration software tool.

.6 VEBI Settings

virtual enabling binary input (VEBI) setting (in submenu “Virtual_Enabling_BI”) is one of the conditions that decide whether the relevant protection is in service, when this relay is energized. Each virtual enabling binary input is an “AND” condition of the relevant protective element. Through SAS or RTU, the virtual enabling binary input can be set as “1” or “0”; and it means that the relevant protection can be in service or out of service through remote command. It provides convenience for operation management. The followinghttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 table lists all the VEBI settings. No.

2 3 4 5

Text

_OC1 VEBI_OC2 VEBI_OC3 VEBI_OC4 VEBI_OC_SOTF

setting of the stage 1 overcurrent protection. VEBI setting of the stage 2 overcurrent protection. VEBI setting of the stage 3 overcurrent protection. VEBI setting of the stage 4 overcurrent protection. VEBI setting of the SOTF overcurrent protection.

.

setting of the overload protection.

setting of the stage 1 sensitive earth fault protection. VEBI setting of the stage 2 sensitive earth fault protection. protection.

.

.

setting of the UFLS protection. VEBI setting of the auto-recloser. VEBI setting of the stage 1 BFI function. VEBI setting of the stage 2 BFI function.

setting of the stage 1 undervoltage protection. VEBI setting of the stage 2 undervoltage protection. VEBI http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949setting of the stage 1 overvoltage protection. VEBI setting of the stage 2 overvoltage protection. VEBI setting of the broken conductor protection. VEBI setting of the blocking No.1 remote tripping output. VEBI setting of the blocking No.2 remote tripping output. VEBI setting of the blocking No.3 remote tripping output. VEBI setting of the blocking No.1 remote closing output.

/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1 0/1

8 9

_OvLd VEBI_OC1 VEBI_OC2

14 15 16 17 18 19 20 21 22 23 24 25 98

_UFLS VEBI_AR VEBI_BFI1 VEBI_BFI2 VEBI_UV1 VEBI_UV2 VEBI_OV1 VEBI_OV2 VEBI_I2/I1 VEBI_Trip01_Block VEBI_Trip02_Block VEBI_Trip03_Block VEBI_Close01_Block

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 7 Settings

VEBI_Close01_Block VEBI setting of the blocking No.2 remote closing output. 0http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949/1 27

_Close01_Block

setting of the blocking No.3 remote closing output.

/1

NARI-RELAYS ELECTRIC CO., LTD

Chapter 7 Settings

[此处图片未下载成功]

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 8 Communication

8 Communication

.1 General

section outlines the remote data communication interfaces of this relay. The relay only supports two protocols at present: IEC60870-5-103 or IEC61850. Setting the relevant communication parameter can select the expected protocol (see Section 7.4 “Communication Settings”).

EIA RS-485 standardized interfaces are isolated, as well as the Ethernet interfaces, and are suitable for permanent connection whichever protocol is selected. The advantage of this type of connection is that up to 32 relays can be “daisy chained” together uhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949sing a simple twisted pair electrical connection.

should be noted that the descriptions contained within this section do not aim to fully detail the protocol itself. The relevant documentation for the protocol should be referred to for this information. This section serves to describe the specific implementation of the protocol in the relay.

.2 Rear Communication Port Information

.2.1 RS-485 Interface

relay provides some rear RS-485 communication ports, and each port has two terminals in the screw connector located on the back of the relay. This port has a common ground terminal for the earth shield of the communication cable. See Section 5.3 for details of the connection terminals. The rear ports provide RS-485 serial data communication and they are intended for use with a permanently wired connection to a remote control center.

protocol provided by the relay is indicated in the http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949relay’s “Equip_Parameter” submenu. Using the keypad and LCD, configure the relevant communication protocol parameters, the corresponding protocol and will be selected. 8.2.1.1 EIA RS-485 Standardized Bus

EIA RS-485 two-wire connection provides a half-duplex fully isolated serial connection to the product. The connection is polarized and whilst the product’s connection diagrams indicate the polarization of the connection terminals it should be borne in mind that there is no agreed definition of which terminal is which. If the master is unable to communicate with the product, and the communication parameters match, then it is possible that the two-wire connection is reversed. 8.2.1.2 Bus Termination

EIA RS-485 bus must have 120  (Ohm) &#189; Watt terminating resistors fitted at either end across the signal wires (see Figure 8.2-1). Some devices may be able to provide the bus terminating resistors by differenthttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 connection or configuration arrangements, in which case separate external components will not be required. However, this product does not provide such a

NARI-RELAYS ELECTRIC CO., LTD

Chapter 8 Communication

[此处图片未下载成功]

, so if it is located at the bus terminus then an external termination resistor will be required.

[此处图片未下载成功]

Figure 8.2-1 EIA RS-485 bus connection arrangements

.2.1.3 Bus Connections &amp; Topologies

EIA RS-485 standard requires that each device is directly connected to the physical cable that is the communications bus. Stubs and tees are expressly forbidden, such as star topologies. Loop bus topologies are not part of the EIA RS-485 standard and are forbidden by it also.

core screened cable is recommended. The specification of the cable will be dependent on the application, although a multi-strand http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe49490.5mm2 per core is normally adequate. Total cable length must not exceed 500m. The screen must be continuous and connected to ground at one end, normally at the master connection point; it is important to avoid circulating currents, especially when the cable runs between buildings, for both safety and noise reasons.

product does not provide a signal ground connection. If a signal ground connection is present in the bus cable then it must be ignored, although it must have continuity for the benefit of other devices connected to the bus. At no stage must the signal ground be connected to the cables screen or to the product’s chassis. This is for both safety and noise reasons. 8.2.1.4 Biasing

may also be necessary to bias the signal wires to prevent jabber. Jabber occurs when the signal level has an indeterminate state because the bus is not being actively driven. This can occur when all the slaves are in recehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ive mode and the master is slow to turn from receive mode to transmit mode. This may be because the master purposefully waits in receive mode, or even in a high impedance state, until it has something to transmit. Jabber causes the receiving device(s) to miss the first bits of the first character in the packet, which results in the slave rejecting the message and consequentially not responding. Symptoms of these are poor response times (due to retries), increasing message error counters, erratic communications, and even a complete failure to communicate.

requires that the signal lines be weakly pulled to a defined voltage level of about 1V. There should only be one bias point on the bus, which is best situated at the master connection point. The DC source used for the bias must be clean; otherwise noise will be injected. Note that some devices may (optionally) be able to provide the bus bias, in which case externahttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949l components will not be required.

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 8 Communication

:

It is extremely important that the 120  termination resistors are fitted. Failure to do so will

in an excessive bias voltage that may damage the devices connected to the bus. z As the field voltage is much higher than that required, NARI-RELAYS cannot assume

for any damage that may occur to a device connected to the network as a result of incorrect application of this voltage. z Ensure that the field voltage is not being used for other purposes (i.e. powering logic inputs)

this may cause noise to be passed to the communication network.

.2.2 Ethernet Interface

relay provides some rear Ethernet interfaces and they are unattached each other. Parameters of each Ethernet port can be configured in the submhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949enu “Equip_Parameter” except for the protocol, and protocol is a uniform parameter for these Ethernet ports. 8.2.2.1 IP Address and Equipment Address of the Equipment

brief explanation of IP and network submask is made as bellow. There are four sections for an IP address.

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

8.2-2 Format of IP and submask address

:

Section 3 and section 2 can be set separately

Section 1 &#215; 256   section 0 = device address (device_addr)

address has above relationship described as an equation with section 1 and section 0 of IP address.

.2.2.2 Ethernet http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949Standardized Communication Cable

is recommended to use 4-pair screened twisted category 5E cable as the communication cable.

[此处图片未下载成功]

A picture is shown bellow.

8.2-3 Ethernet communication cable

NARI-RELAYS ELECTRIC CO., LTD 103

[此处图片未下载成功]

Chapter 8 Communication

[此处图片未下载成功]

.2.2.3 Connections and Topologies

device is connected to an exchanger via communication cable and thereby to form a star structure network. Dual-network is recommended in order to increase reliability. SCADA is also connected to the exchanger and will play a role of master station, so the every equipment which has been connected to the exchanger will play a role of slave unit.

[此处图片未下载成功]

Figure 8.2-4 Ethernet communication structure

.2.3 IEC60870-5-103 Communication

IEC specification IEC60870-5-103: http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949Telecontrol Equipment and Systems, Part 5: Transmission Protocols Section 103 defines the use of standards IEC60870-5-1 to IEC60870-5-5 to perform communication with protection equipment. The standard configuration for the IEC60870-5-103 protocol is to use a twisted pair EIA RS-485 connection over distances up to 500m. It also supports to use an Ethernet connection. The relay operates as a slave in the system, responding to commands from a master station.

.2.4 IEC61850 Communication

IEC specification IEC61850: Communication Networks and Systems in Substations, a new protocol defines the communication standards in substations. The standard configuration for the IEC61850 protocol is based on the Ethernet.

.3 IEC60870-5-103 Interface

IEC60870-5-103 interface is a master/slave interface with the relay as the slave device. The relay conforms to compatibility level 2; compatibility level 3 is not http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949supported. The following IEC60870-5-103 facilities are supported by this interface:

Initialization (reset)

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 8 Communication

Time synchronization z Event record extraction z General interrogation z Cyclic measurements z General commands z Disturbance records

.3.1 Physical Connection and Link Layer

EIA RS-485 standardized ports are available for IEC60870-5-103 in this relay. The baudrate is optional: 4800bps, 9600bps, 19200bps, 38400bps, 57600bps or 115200bps.

unattached Ethernet ports are available for IEC60870-5-103 in this relay. The transmission speed is 100Mbit/s.

link layer strictly abides by the rules defined in the IEC60870-5-103.

.3.2 Initialization

the relay has been powered up, or if the communication parameters have been changed, a reset command http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949is required to initialize the communications. The relay will respond to either of the two reset commands (Reset CU or Reset FCB), the difference is that the Reset CU will clear any unsent messages in the relay’s transmit buffer.

relay will respond to the reset command with an identification message ASDU 5, the COT (Cause Of Transmission) of this response will be either Reset CU or Reset FCB depending on the nature of the reset command.

addition to the above identification message, if the relay has been powered up it will also produce a power up event.

.3.3 Time Synchronization

relay time and date can be set using the time synchronization feature of the IEC60870-5-103 protocol. The relay will correct for the transmission delay as specified in IEC60870-5-103. If the time synchronization message is sent as a send/confirm message then the relay will respond with a confirmation. Whether the timhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949e-synchronization message is sent as a send confirmation or a broadcast (send/no reply) message, a time synchronization Class 1 event will be generated/produced.

the relay clock is synchronized using the IRIG-B input then it will not be possible to set the relay time using the IEC60870-5-103 interface. An attempt to set the time via the interface will cause the relay to create an event with the current date and time taken from the IRIG-B synchronized internal clock.

.3.4 Spontaneous Events

are categorized using the following information:

NARI-RELAYS ELECTRIC CO., LTD

Chapter 8 Communication

[此处图片未下载成功]

Type identification (TYP) z Function type (FUN) z Information number (INF)

following table contains a complete listing of all events produced by the relay. For the details about this events, see relevant sections in Chapter 6 “http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949Human Interface Operation Introduction”.

ASDU 1

_Abnor Alm_Fault Alm_Fail Alm_52b Alm_VTS_Fdr Alm_VTS_Bus Alm_Freq Alm_TCCS Alm_EF Alm_OvLd Alm_ROC3 Alm_LowPres_Trp Alm_LowPres_Cls Alm_CTS Alm_Data_Ch Alm_UV1 Alm_Setting BI_52b BI_52a BI_PostCls EBI_UV BI_Ext_BFI BI_Blk_OC1 BI_Blk_OC2 BI_Blk_OC3 BI_Blk_OC4 EBI_TeleCtrl EBI_Lockout EBI_UFLS BI_LowPres_Trp BI_LowPres_Cls BI_RstTarg BI_BlkComm VBI_52bLock VBI_52aLock

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 8 Communication

_Ready_AR BI_LossGPS Op_FD Op_OC1 Op_OC2 Op_OC3 Op_OC4 Op_SEF1 Op_SEF2 Op_InvOC Op_OC_SOTF Op_OvLd Op_ROC1 Op_ROC2 Op_ROC3 Op_InvROC

2

_ROC_SOTF Op_UFLS Op_AR1 Op_AR2 Op_AR3 Op_AR4 Op_BFI1 Op_BFI2 Op_UV1 Op_UV2 Op_OV1 Op_OV2 Op_I2/I1 Trip

_GOOSE_Trp Op_GOOSE_Cls S_CBState BI_1

40

_2 BIhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949_3 BI_4

.3.5 General Interrogation

GI can be used to read the status of the relay, the function numbers, and information numbers

will be returned during the GI cycle. The GI cycle strictly abides by the rules defined in the IEC60870-5-103.

NARI-RELAYS ELECTRIC CO., LTD 107

Chapter 8 Communication

[此处图片未下载成功]

relay will respond to this GI command with an ASDU 44 message, the cause of transmission (COT) of this response is 9.

the IEC60870-5-103 standard can get the enough details about general interrogation.

.3.6 Cyclic Measurements

relay will produce measured values using ASDU 50 on a cyclical basis, this can be read from the relay using a Class 2 poll (note ADSU 3 and ASDU 9 are not used).

cause of transmission is 2. The rate at which the relay produces new measured values is fixed (about one second)http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949. It should be noted that the measurands transmitted by the relay are sent as a proportion of corresponding times the rated value of the analog value. The following table shows all the measurands and the proportion relationship between the measurands and the rated value.

[此处图片未下载成功]

Here, the sign “In” denotes the rated current of the AC current input, the sign “Un” denotes the

phase voltage of the AC voltage input.

.3.7 General Commands

list of the supported commands (in control direction) is contained in the following table. The relay will not respond to other commands, and short-term communication interrupt will occur.

ASDU 64 ASDU 64 ASDU 64 ASDU 64 ASDU 64 ASDU 64

1 1 1 1 1 1

48 48 48 48 48 48

0x81 0x82 0x01 0x02 0xC1 0xC2

trip with confirmation Remote close with confirmation Remote trip with execution Remhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ote close with execution Remote trip with abortion Remote close with abortion

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 8 Communication

the relay receives one of the command messages correctly, it will respond an ACK message, and then respond a message which has the same ASDU data with the control direction message in next communication turn.

.3.8 Generic Functions

generic functions can be used to read the setting and protection measurement of the relay, and modify the setting. Two supported type identifications are ASDU 21 and ASDU 10. For more details about generic functions, see the IEC60870-5-103 standard. 1. Generic functions in control direction

240 241 243 244 245 249 250 251

headings of all defined groups

values or attributes of all entries in one group Read directory of a single entry Readhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 value or attribute of a single entry General interrogation of generic data Write entry with confirmation Write entry with execution Write entry abort

. Generic functions in monitor direction

240 241 243 244 245 249 250 251

headings of all defined groups

values or attributes of all entries of one group Read directory of a single entry Read value or attribute of a single entry End of general interrogation of generic data Write entry with confirmation Write entry with execution Write entry aborted

.3.9 Disturbance Records

relay can store up to eight disturbance records in its memory. A pickup of the fault detector or an operation of the relay can make the relay store the disturbance records.

disturbance records are stored in uncompressed format and can be extracted using the standard mechanisms described in IEC60870-5-103.

://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949arNANJING NARI-RELAYS ELECTRIC CO., LTD 109

Chapter 8 Communication

[此处图片未下载成功]

.4 IEC61850 Interface

.4.1 Overview

IEC 61850 standard is the result of years of work by electric utilities and vendors of electronic equipment to produce standardized communications systems. IEC 61850 is a series of standards describing client/server and peer-to-peer communications, substation design and configuration, testing, environmental and project standards. The complete set includes: IEC 61850-1: IEC 61850-2: IEC 61850-3: IEC 61850-4: IEC 61850-5: IEC 61850-6: IEC 61850-7-1: IEC 61850-7-2: IEC 61850-7-3: IEC 61850-7-4: IEC 61850-8-1: IEC 61850-9-1: IEC 61850-9-2: IEC 61850-10:

and overview Glossary

requirements

and project management

and requirements for functions and device models

description languhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949age for communication in electrical substations related to IEDs

communication structure for substation and feeder equipment - Principles and models

communication structure for substation and feeder equipment - Abstract communication service interface (ACSI)

communication structure for substation and feeder equipment – Common data classes

communication structure for substation and feeder equipment – Compatible logical node classes and data classes

Communication Service Mapping (SCSM) – Mappings to MMS (ISO 9506-1 and ISO 9506-2) and to ISO/IEC 8802-3

Communication Service Mapping (SCSM) – Sampled values over serial unidirectional multi-drop point to point link

Communication Service Mapping (SCSM) – Sampled values over ISO/IEC 8802-3 Conformance testing

documents can be obtained from the IEC (). It is strongly recommendhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ed that all those involved with any IEC 61850 implementation obtain this document set.

.4.2 Communication Profiles

PCS-9600 series relay supports IEC 61850 server services over TCP/IP communication protocol stacks. The TCP/IP profile requires the PCS-9600 series relay to have an IP address to establish communications. These addresses are located in the submenu “Equip_Parameter”. See Section 7.4 for further details. MMS Protocol

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 8 Communication

61850 specifies the use of the Manufacturing Message Specification (MMS) at the upper (application) layer for transfer of real-time data. This protocol has been in existence for a number of years and provides a set of services suitable for the transfer of data within a substation LAN environment. Actual MMS protocol services are mapped to IEC 61850 abstract services ihttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949n IEC61850-8-1. Client/server

is a connection-oriented type of communication. The connection is initiated by the client, and communication activity is controlled by the client. IEC61850 clients are often substation computers running HMI programs or SOE logging software. Servers are usually substation equipment such as protection relays, meters, RTUs, transformer, tap changers, or bay controllers. Peer-to-peer

is a non-connection-oriented, high speed type of communication usually between substation equipment, such as protection relays. GOOSE is the method of peer-to-peer communication. Substation configuration language (SCL)

substation configuration language is a number of files used to describe the configuration of substation equipment. Each configured device has an IEC Capability Description (ICD) file and a Configured IED Description (CID) file. The substation single line information is stored http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949in a System Specification Description (SSD) file. The entire substation configuration is stored in a Substation Configuration Description (SCD) file. The SCD file is the combination of the individual ICD files and the SSD file.

.4.3 Server Data Organization

defines an object-oriented approach to data and services. An IEC61850 physical device can contain one or more logical device(s) (for proxy). Each logical device can contain many logical nodes. Each logical node can contain many data objects. Each data object is composed of data attributes and data attribute components. Services are available at each level for performing various functions, such as reading, writing, control commands, and reporting.

IED represents one IEC61850 physical device. The physical device contains one logical device, and the logical device contains many logical nodes. The logical node LPHD contains information about thhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949e IED physical device. The logical node LLN0 contains information about the IED logical device.

.4.3.1 Digital Status Values

GGIO logical node is available in the PCS-9600 series relays to provide access to digital status points (including general I/O inputs and warnings) and associated timestamps and quality flags. The data content must be configured before the data can be used. GGIO provides digital status points for access by clients. It is intended that clients use GGIO in order to access digital status values from the PCS-9600 series relays. Clients can utilize the IEC61850 buffered reporting features available from GGIO in order to build sequence of events (SOE) logs and HMI display screens. Buffered reporting should generally be used for SOE logs since the buffering capability reduces the chances of missing data state changes. All needed status data objects are transmitted

NARI-RELAYS ELEhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949CTRIC CO., LTD

Chapter 8 Communication

[此处图片未下载成功]

HMI clients via buffered reporting, and the corresponding buffered reporting control block (BRCB) is defined in LLN0. 8.4.3.2 Analog Values

of analog measured values are available through the MMXU logical nodes, and metering values in MMTR, the others in MMXN, MSQI and so on. Each MMXU logical node provides data from a IED current/voltage “source”. There is one MMXU available for each configurable source. MMXU1 provides data from CT/VT source 1(usually for protection purpose), and MMXU2 provides data from CT/VT source 2 (usually for monitor and display purpose). All these analog data objects are transmitted to HMI clients via unbuffered reporting periodically, and the corresponding unbuffered reporting control block (URCB) is defined in LLN0. MMXUx logical nodes provide the following data for each source: MMXU.ST.TotW: http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949MMXU.ST.TotVAr: MMXU.ST.TotPF: MMXU.ST.Hz: MMXU.ST.PPV.phsAB: MMXU.ST.PPV.phsBC: MMXU.ST.PPV.phsCA: MMXU.ST.PhV.phsA: MMXU.ST.PhV.phsB: MMXU.ST.PhV.phsC: MMXU.ST.A.phsA: MMXU.ST.A.phsB: MMXU.ST.A.phsC: MMXU.ST.A.neut:

phase real power three-phase reactive power three-phase power factor frequency

AB voltage magnitude and angle phase BC voltage magnitude and angle Phase CA voltage magnitude and angle phase AG voltage magnitude and angle phase BG voltage magnitude and angle phase CG voltage magnitude and angle phase A current magnitude and angle phase B current magnitude and angle phase C current magnitude and angle ground current magnitude and angle

.4.3.3 Protection Logical Nodes

following list describes the protection elements for all PCS-9600 series relays. The specified relay will contain a subset of protection elements from this list.

: transformer instantaneous differenhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949tial, transformer percent differential PDIS: phase distance, ground distance

: phase instantaneous overcurrent, neutral instantaneous overcurrent, ground

overcurrent, negative-sequence instantaneous overcurrent.

: phase time overcurrent, neutral time overcurrent, ground time overcurrent,

sequence time overcurrent, neutral directional overcurrent, negative-sequence directional overcurrent

: phase undervoltage, auxiliary undervoltage, third harmonic neutral undervoltage PTUF: underfrequency

: phase overvoltage, neutral overvoltage, auxiliary overvoltage, negative sequence

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 8 Communication

: breaker failure RREC: autoreclosure

protection elements listed above contain start (pickup) and operate flags, instead of any elemehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949nt has its own start (pickup) flag separately, all the elements share a common start (pickup) flags “PTRC.ST.Str.general” in a PCS-9600 series relay. The operate flag for PTOC1 is “PTOC1.ST.Op.general”. For the PCS-9600 series relay protection elements, these flags take their values from related module for the corresponding element. Similar to digital status values, the protection trip information is reported via BRCB, and it also locates in LLN0. 8.4.3.4 LLN0 and Other Logical Nodes

node LLN0 is essential for an IEC61850 based IED. This LN shall be used to address common issues for Logical Devices. In PCS-9600 series relays, most of the public services, the common settings, control values and some device oriented data objects are available here. The public services may be BRCB, URCB and GSE control blocks and similar global defines for the whole device; the common settings (the logic nodes LPHD、PTRC also contain http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949some related common settings) include all the setting items of communication settings. System settings and some of the protection setting items, which can be configured to two or more protection elements (logical nodes). In LLN0, the item Loc is a device control object, this Do item indicates the local operation for complete logical device, when it is true, all the remote control commands to the IED will be blocked and those commands make effective until the item Loc is changed to false. Besides the logical nodes we describe above, there are some other logical nodes below in the IEDs: Physical device information, the logical node to model common issues for physical device.

: Protection trip conditioning, it shall be used to connect the “operate” outputs of one or

protection functions to a common “trip” to be transmitted to XCBR. In addition or alternatively, any combination of “operate” outputs of protectihttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949on functions may be combined to a new “operate” of PTRC.

: Disturbance recorder function. It triggers the fault wave recorder and its output refers to

“IEEE Standard Format for Transient Data Exchange (COMTRADE) for Power System” (IEC 60255-24). All enabled channels are included in the recording, independently of the trigger mode.

: Generic automatic process control, it is used to model in a generic way the

/automation of functions, for example the sequence control functions for RCS-9600C series relays.

: Switch controller. This class is used to control all switching conditions of XCBR and

. A remote switching command (for example select-before-operate) arrives here firstly.

: breaker control. The XCBR logical node is directly associated with the breaker control

.

.ST.Pos: This is the position of the breaker. If the breakhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949er control logic

that the breaker, or any single pole of the breaker, is closed, then the breaker position state is “on”. If the breaker

NARI-RELAYS ELECTRIC CO., LTD

:

Chapter 8 Communication

[此处图片未下载成功]

logic indicates that the breaker is open, then the breaker position state is “off”.

.ST.BlkOpn: This is the state of the block open command logic. When true,

open commands from IEC61850 clients will be rejected.

.ST.BlkCls: This is the state of the block close command logic. When true,

close commands from IEC61850 clients will be rejected.

.CO.Pos: This is where IEC61850 clients can issue open or close

to the breaker. SBO control with normal security is the only supported IEC61850 control model.

.4.4 Server Features and Configuration

.4.http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe49494.1 Buffered/Unbuffered Reporting

buffered and unbuffered reporting control blocks locate in LLN0, they can be configured to transmit information of protection trip information (in the Protection logical nodes), binary status values (in GGIO) and analog measured/calculated values (in MMXU, MMTR and MSQI). The reporting control blocks can be configured in CID files, and then be sent to the IED via an IEC61850 client. The following items can be configured.

: Trigger options. The following bits are supported by the PCS-9600 series relays:

－ Bit 1: Data-change － Bit 4: Integrity

－ Bit 5: General interrogation

: Option Fields. The following bits are supported by the PCS-9600 series relays:

－ Bit 1: Sequence-number － Bit 2: Report-time-stamp － Bit 3: Reason-for-inclusion － Bit 4: Data-set-name － Bit 5: Data-reference

－ Bit 6: Buffer-overflow (for buffered reports ohttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949nly) － Bit 7: EntryID (for buffered reports only) － Bit 8: Conf-revision － Bit 9: Segmentation IntgPd: Integrity period. BufTm: Buffer time. 8.4.4.2 File Transfer

file services are supported to allow transfer of oscillography, event record or other files from

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 8 Communication

PCS-9600 series relay. 8.4.4.3 Timestamps

timestamp values associated with all IEC61850 data items represent the time of the last change of either the value or quality flags of the data item. 8.4.4.4 Logical Node Name Prefixes

specifies that each logical node can have a name with a total length of 11 characters. The name is composed of: a five or six-character name prefix; a four-character standard name (for example, MMXU, GGIO, PIOC, etc.); a one or two-character instantiation index.

names are of the fohttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949rm xxxxxxPTOC1, where the xxxxxx character string is configurable. Details regarding the logical node naming rules are given in IEC61850 parts 6 and 7-2. It is recommended that a consistent naming convention be used for an entire substation project. 8.4.4.5 GOOSE Services

specifies the type of peer-to-peer data transfer services: Generic Object Oriented Substation Events (GOOSE). IEC61850 GOOSE services provide virtual LAN (VLAN) support, Ethernet priority tagging, and Ether-type Application ID configuration. The support for VLANs and priority tagging allows for the optimization of Ethernet network traffic. GOOSE messages can be given a higher priority than standard Ethernet traffic, and they can be separated onto specific VLANs. Devices that transmit GOOSE messages also Devices that transmit GOOSE messages also function as servers. Each GOOSE publisher contains a “GOOSE control block” to configure and control thhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949e transmission.

transmission is also controlled via the hidden setting [MMS_multi_cast_addr]. The setting [MMS_multi_cast_addr] defines a definite IED group in which the IED can communicate with each other via GOOSE protocol, and if the setting [MMS_multi_cast_addr] is configured to “0”, GOOSE service is blocked in this IED. IEC61850 recommends a default priority value of 4 for GOOSE. Ethernet traffic that does not contain a priority tag has a default priority of 1. More details are specified in IEC61850 part 8-1. IEC61850 recommends that the Ether-type Application ID number be configured according to the GOOSE source.

PCS-9600 series delays support IEC61850 Generic Object Oriented Substation Event (GOOSE) communication. All GOOSE messages contain IEC61850 data collected into a dataset. It is this dataset that is transferred using GOOSE message services. The GOOSE related dataset is configured in the CID fihttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949le and it is recommended that the fixed GOOSE be used for implementations that require GOOSE data transfer between PCS-9600 series relays.

GOOSE messaging contains a number of configurable parameters, all of which must be correct to achieve the successful transfer of data. It is critical that the configured datasets at the transmission and reception devices are an exact match in terms of data structure, and that the GOOSE addresses and name strings match exactly.

general steps required for transmission configuration are: 1. Configure the transmission dataset.

NARI-RELAYS ELECTRIC CO., LTD

Chapter 8 Communication

[此处图片未下载成功]

. Configure the GOOSE service settings. 3. Configure the data.

general steps required for reception configuration are: 1. Configure the reception dataset. 2. Configure the GOOSE service settings. 3. Configure thhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949e data.

.4.5 ACSI Conformance

.4.5.1 ACSI Basic Conformance Statement

Server Roles B11 B12

Association) Application-Association) SCSM: IEC 61850-8-1 usedSCSM: IEC 61850-9-1 usedSCSM: IEC 61850-9-2 usedSCSM: other Publisher side Subscriber side Publisher side Subscriber side

－ C1

－

[此处图片未下载成功]

PCS-9600 Series

Supported B21 B22 B23 B24 B31 B32 B41 B42

N N N － O － O

N N N

N N N

Substation Event Model (GSE)

－

Of Sampled Value Model (SVC)

－

:

: Shall be &quot;M&quot; if support for LOGICAL-DEVICE model has been declared O: Optional M: Mandatory

: Supported by PCS-9600 series relays

: Currently not supported by PCS-9600 series relays

.4.5.2 ACSI Models Confhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ormance Statement

M2 M3

device Logical node

C2 C3

C2 C3

Series

Y

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 8 Communication

M5 M6 M7 M7-1 M7-2 M7-3 M7-4 M7-5 M7-6 M7-7 M7-8 M7-9 M7-10 M8 M8-1 M8-2 M8-3 M8-4 M8-5 M8-6 M8-7 Logging M9 M9-1 M10 GSE M12 M13 M14 M15 M16 M17

set

group control Buffered report control  data-set-name  data-reference  buffer-overflow  entryID  BufTm  IntgPd  GI

report control data-set-name  data-reference  BufTm  IntgPd Log control  IntgPd

O O Y Y Y Y Y Y Y N Y Y M Y Y Y Y Y N N O N

[此处图片未下载成功]

O O Y Y Y Y Y Y Y N Y Y M Y Y Y Y Y N Y O N

Y Y Y Y Y Y Y Y Y N Y Y Y Y Y Y Y Y N Y N N

SVC Unicast SVC File transfer

O O

://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 O O

N Y

:

: Shall be &quot;M&quot; if support for LOGICAL-NODE model has been declared

: Shall be &quot;M&quot; if support for DATA model has been declared

: Shall be &quot;M&quot; if support for DATA-SET, Substitution, Report, Log Control, or Time

has been declared

: Shall be &quot;M&quot; if support for Report, GSE, or SMV models has been declared M: Mandatory

NARI-RELAYS ELECTRIC CO., LTD 117

Chapter 8 Communication

[此处图片未下载成功]

: Supported by PCS-9600 series relays

: Currently not supported by PCS-9600 series relays

.4.5.3 ACSI Services Conformance Statement

S1 S2 S3 S4 S5 S6 S7 Data S8 S9 S10 S11 S12 S13 S14 S15 S16 S17 S18 S19 S20 S21 S22 S23

association

/Publisher

Series://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949device Logical node

set

group control

report control block S24

-1  data-change  S24-2  qchg-change  S24-3  data-update

Y Y

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 8 Communication

S26 S27

report control block S27-1  data-change S27-2  qchg-change S27-3  data-update S28 S29

Y Y

Log control block S30 S31 Log S32 QueryLogByTime

S34

substation event model (GSE) GOOSE control block S35 S36 S37 S38 S39

Of Sample Value Model (SVC) Multicast SVC S45 S46 S47 Unicast SVC

S49 S50 Control

S52 S53 S54 S55 S56 File transfer

NARI-RELAYS ELECTRIC CO., LTD

Chapter 8 Communication

://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ar[此处图片未下载成功]

S59 S60 Time

[此处图片未下载成功]

SNTP

:

: Shall declare support for at least one (BRCB or URCB)

: Shall declare support for at least one (QueryLogByTime or QueryLogAfter) C8: Shall declare support for at least one (SendGOOSEMessage or

)

: Shall declare support if TP association is available

: Shall declare support for at least one (SendMSVMessage or SendUSVMessage)

.4.6 Logical Nodes

.4.6.1 Logical Nodes Table

PCS-9600 series relays support IEC61850 logical nodes as indicated in the following table. Note that the actual instantiation of each logical node is determined by the product order code.

: System Logical Nodes

Series

: Physical device informationP: Logical Nodes For Protection Functions

: Logical node zeroPDhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949IF: DifferentialPDIR: Direction comparisonPDOP: Directional overpower PDUP: Directional underpower PFRC: Rate of change of frequency PHAR: Harmonic restraint

－ － － －

: DistancePHIZ: Ground detector PMRI Motor restart inhibition

: Motor starting time supervision POPF: Over power factor PPAM: Phase angle measuring PSCH: Protection scheme

: Sensitive directional earth fault PTEF: Transient earth fault PTOF: Overfrequency

: Instantaneous overcurrent－ － － － － － － －

NARI-RELAYS ELECTRIC CO., LTD

: Time overcurrent

[此处图片未下载成功]

Chapter 8 Communication

: Overvoltage PTTR: Thermal overload PTUC: Undercurrent PUPF: Underpower factor

－ － －

: Protection trip conditioningPTUV: UndervoltagePTUF: UnderfrequencyPVOC: Voltage controlled time overcurrent PVPH: Volts per Hz

－ PZSU: Zero speed or underspeed://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949r

－

: Logical Nodes For Protection Related Functions

: Disturbance recorder function RADR: Disturbance recorder channel analogue － RBDR: Disturbance recorder channel binary － RDRS: Disturbance record handling － RBRF: Breaker failure

: Directional element － RFLO: Fault locator

－ RPSB: Power swing detection/blocking

－ RREC: AutoreclosingRSYN: Synchronism-check or synchronizingC: Logical Nodes For Control CALH: Alarm handling － CCGR: Cooling group control － CILO: InterlockingCPOW: Point-on-wave switching

－

: Switch controllerG: Logical Nodes For Generic References

: Generic automatic process controlGGIO: Generic process I/OGSAL: Generic security application

－ I: Logical Nodes For Interfacing And Archiving IARC: Archiving

－ IHMI: Human machine interface － ITCI: Telecontrol interface － ITMI: Telemonitoring interface

－ A: Logical Nodes Forhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 Automatic Control ANCR: Neutral current regulator － ARCO: Reactive power control － ATCC: Automatic tap changer controllerAVCO: Voltage control

－ NANJING NARI-RELAYS ELECTRIC CO., LTD 121

Chapter 8 Communication

[此处图片未下载成功]

: Logical Nodes For Metering And Measurement

: Differential measurementsMHAN: Non phase related harmonics or interharmonicMMXN: Non phase related measurementMHAI: Harmonics or interharmonicsMMTR: MeteringMMXU: MeasurementMSTA: Metering statistics

: Logical Nodes For Sensors And Monitoring SARC: Monitoring and diagnostics for arcs SIMG: Insulation medium supervision (gas) SIML: Insulation medium supervision (liquid)

: Monitoring and diagnostics for partial discharges X: Logical Nodes For Switchgear TCTR: Current transformer TVTR: Voltage transformer

: Logical Nodes For Power Transformers YEFN: Earth fault neutralizer (Peterson coilhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949) YPSH: Power shunt

: Logical Nodes For Further Power System Equipment ZAXN: Auxiliary network ZBAT: Battery ZBSH: Bushing ZCAB: Power cable ZCAP: Capacitor bank ZCON: Converter ZGEN: Generator ZGIL: Gas insulated line ZLIN: Power overhead line ZMOT: Motor ZREA: Reactor

: Rotating reactive component ZSAR: Surge arrestor

: Thyristor controlled frequency converter ZTRC: Thyristor controlled reactive component

－ － － － － － － － － － － － － － － － － － － － － － － －

: Sequence and imbalanceYLTC: Tap changerYPTR: Power transformer122

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 9 Installation

9 Installation

.1 General

equipment must be shipped, stored and installed with the greatest care.

the place of installation such that the communication interface and the controls on the front of the device are eahttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949sily accessible.

must circulate freely around the equipment. Observe all the requirements regarding place of installation and ambient conditions given in this instruction manual.

care that the external wiring is properly brought into the equipment and terminated correctly and pay special attention to grounding. Strictly observe the corresponding guidelines contained in this section.

.2 Safety Instructions

and units may only be replaced by correspondingly trained personnel. Always observe the basic precautions to avoid damage due to electrostatic discharge when handling the equipment.

certain cases, the settings have to be configured according to the demands of the engineering configuration after replacement. It is therefore assumed that the personnel who replace modules and units are familiar with the use of the operator program on the service PC.

[此处图片未下载成功]

://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949DANGER: Only insert or withdraw the PWR module while the power supply is switched off. To this end, disconnect the power supply cable that connects with the PWR module.

[此处图片未下载成功]

WARNING: Only insert or withdraw the other boards while the power supply is switched off.

[此处图片未下载成功]

WARNING: The modules of this relay may only be inserted in the slots designated in Section 5.2. Components can be damaged or destroyed by inserting boards in the wrong slots.

[此处图片未下载成功]

DANGER: Improper handling of the equipment can cause damage or an incorrect response of the equipment itself or the primary plant.

[此处图片未下载成功]

WARNING: Industry packs and ribbon cables may only be replaced or the positions of jumpers be changed on a workbench appropriately designed for working on electronic

NARI-RELAYS ELECTRIC CO., LTD 123

Chapter 9 Installation

[此处图片未下载成http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949功]

. The modules, bus backplanes are sensitive to electrostatic discharge when not in the unit's housing.

basic precautions to guard against electrostatic discharge are as follows:

Should boards have to be removed from this relay installed in a grounded cubicle in an HV

installation, please discharge yourself by touching station ground (the cubicle) beforehand. z Only hold electronic boards at the edges, taking care not to touch the components.

Only works on boards that have been removed from the cubicle on a workbench designed for

equipment and wear a grounded wristband. Do not wear a grounded wristband, however, while inserting or withdrawing units. z Always store and ship the electronic boards in their original packing. Place electronic parts in

screened packing materials.

.3 Checking the Shipment

://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949eck that the consignment is complete immediately upon receipt. Notify the nearest NARI-RELAYS Company or agent, should departures from the delivery note, the shipping papers or the order be found.

inspect all the material when unpacking it. When there is evidence of transport damage, lodge a claim immediately in writing with the last carrier and notify the nearest NARI-RELAYS Company or agent.

the equipment is not going to be installed immediately, store all the parts in their original packing in a clean dry place at a moderate temperature. The humidity should not exceed 90% at a maximum temperature of  55&#176;C; the permissible storage temperature range in dry air is -40&#176;C to  70&#176;C.

.4 Material and Tools Required

necessary mounting kits will be provided, including screws, pincers and assembly instructions.

suitable drill and spanners are required to secure the cubhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949icles to the floor using the plugs provided (if this relay is mounted in cubicles).

.5 Device Location and Ambient Conditions

place of installation should permit easy access especially to front of the device, i.e. to the human machine interface of the equipment.

should also be free access at the rear of the equipment for additions and replacement of

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 9 Installation

boards.

every piece of technical equipment can be damaged or destroyed by inadmissible ambient conditions, such as:

) The location should not be exposed to excessive air pollution (dust, aggressive substances). 2) Severe vibration, extreme changes of temperature, high levels of humidity, surge voltages of

amplitude and short rise time and strong induced magnetic fields should be avoided as far ahttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949s possible. 3) Air must not be allowed to circulate freely around the equipment.

equipment can in principle be mounted in any attitude, but it is normally mounted vertically (visibility of markings).

[此处图片未下载成功]

WARNING: Excessively high temperature can appreciably reduce the operating life of this relay.

.6 Mechanical Installation

relay is made of a single layer 4U height 9.5” chassis with 8 connectors on its rear panel (See Figure 5.1-2). Following figure shows the dimensions of this relay for reference in mounting.

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

9.6-1 Dimensions of this relay and the cut-out in the cubicle (unit: mm)://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949rNARI-RELAYS ELECTRIC CO., LTD

Chapter 9 Installation

[此处图片未下载成功]

: It is necessary to leave enough space top and bottom of the cut-out in the cubicle for heat emission of this relay.

mentioned former (Chapter 5 “Hardware Description”), up to eight modules are installed in the enclosure of this relay, and these modules must be plugged into the proper slots of this relay respectively. The safety instructions must be abided by when installing the boards, see Section 9.2 “Safety Instructions”. Figure 9.6-2 shows the installation way that a module is being plugged into a

[此处图片未下载成功]

corresponding slot.

9.6-2 Demonstration of plugging a board into its corresponding slot

the case of equipment supplied in cubicles, place the cubicles on the foundations that have been prepared. Take care while doing so not to jam or othttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949herwise damage any of the cables that have already been installed. Secure the cubicles to the foundations.

.7 Electrical Installation and Wiring

.7.1 Grounding Guidelines

operations in HV installations generate transient over voltages on control signal cables. There is also a background of electromagnetic RF fields in electrical installations that can induce spurious currents in the devices themselves or the leads connected to them. All these influences can influence the operation of electronic apparatus.

the other hand, electronic apparatus can transmit interference that can disrupt the operation of other apparatus.

order to minimize these influences as far as possible, certain standards have to be observed with respect to grounding, wiring and screening.

[此处图片未下载成功]

NOTE: All these precautions can only be effective if the station ground is of good quality.://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949r

.7.2 Cubicle Grounding

cubicle must be designed and fitted out such that the impedance for RF interference of the

[此处图片未下载成功]

NANJING NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 9 Installation

path from the electronic device to the cubicle ground terminal is as low as possible. Metal accessories such as side plates, blanking plates etc., must be effectively connected surface-to-surface to the grounded frame to ensure a low-impedance path to ground for RF interference. The contact surfaces must not only conduct well, they must also be non-corroding.

[此处图片未下载成功]

NOTE: If the above conditions are not fulfilled, there is a possibility of the cubicle or parts of it forming a resonant circuit at certain frequencies that would amplify the transmission of interference by the devices installed and also reduce their immunity to induced interfhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949erence.

parts of the cubicle such as doors (front and back) or hinged equipment frames must be effectively grounded to the frame by three braided copper strips (see Figure 9.7-1).

metal parts of the cubicle housing and the ground rail are interconnected electrically conducting and corrosion proof. The contact surfaces shall be as large as possible.

[此处图片未下载成功]

NOTE: For metallic connections please observe the voltage difference of both materials according to the electrochemical code.

cubicle ground rail must be effectively connected to the station ground rail by a grounding strip

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949此处图片未下载成功]

[此处图片未下载成功]

(braided copper).

9.7-1 Cubicle grounding system

.7.3 Ground Connection on the Device

is a ground terminal on the rear panel (see Figure 9.7-2), and the ground braided copper strip can be connected with it. Take care that the grounding strip is always as short as possible. The main thing is that the device is only grounded at one point. Grounding loops from unit to unit are not allowed.

are some ground terminals on some connectors of this relay, and the sign is “GND”. All the ground terminals are connected in the cabinet of this relay. So, the ground terminal on the rear

NARI-RELAYS ELECTRIC CO., LTD

Chapter 9 Installation

[此处图片未下载成功]

(see Figure 9.7-2) is the only ground terminal of this device.

9.7-2 Ground terminal of this relay

.7.4 http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949Grounding Strips and their Installation

frequency currents are produced by interference in the ground connections and because of skin effect at these frequencies, only the surface region of the grounding strips is of consequence. The grounding strips must therefore be of (preferably tinned) braided copper and not round copper conductors, as the cross-section of round copper would have to be too large. Data of braided copper strip: threaded M4, 2.5mm2.

terminations must be fitted to both ends (press/pinch fit and tinned) with a hole for bolting them firmly to the items to be connected.

surfaces to which the grounding strips are bolted must be electrically conducting and non-corroding.

following figure shows the ground strip and termination.

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

9.7-3 Ground strip and termination

.7.5 Guidelines for Wiring

are several types of cables that are used in the connection of this relay: braided copper cable, serial communication cable. Recommendation of each cable:

Grounding: braided copper cable, threaded M4, 2.5mm2 z Serial communication: 4-core shielded braided cable

DC Power supply, Binary Output: brained copper cable, 1.5mm2

[此处图片未下载成功]

NANJING NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 9 Installation

.7.6 Wiring for Electrical Cables

female connector is used for connecting the wires with it, and then a female connector plugs into a corresponding male connector that is in thehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 front of one board. For further details about the pin defines of these connectors, see Chapter 5 “Hardware Description”.

following figure shows the glancing demo about the wiring for the electrical cables.

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

Figure 9.7-4 Glancing demo about the wiring for electrical cables

: Never allow the current transformer (CT) secondary circuit connected to this equipment to be opened while the primary system is live. Opening the CT circuit will produce a dangerously high voltage.

.8 Typical Wiring of the Relay

information and sections about the modules and the connectors of the relay are described in Chapter 5 “Hardware Description”. Referring the relevant sections can help to wire correctly and effectively.

figure shows the metallic links, control switch and local operation buttons (mahttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949nual closing button and manual tripping button) on the control panel.

9.8-1 Metallic links, control switch and local operation button on the control panel The typical wiring of this relay is shown as below, all the configurable binary inputs and binary output adopt the default definition in the factory.

NARI-RELAYS ELECTRIC CO., LTD 129

Chapter 9 Installation

[此处图片未下载成功]

9.8-2 Typical wiring diagram of this relay

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

NANJING NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 10 Commissioning

10 Commissioning

.1 General

relay is fully numerical in their design, implementing all protection and non-protection functions in software. The relay employ a high degree ofhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 self-checking and in the unlikely event of a failure, will give an alarm. As a result of this, the commissioning test does not need to be as extensive as with non-numeric electronic or electro-mechanical relays.

commission numerical relays, it is only necessary to verify that the hardware is functioning correctly and the application-specific software settings have been applied to the relay.

commissioning test and setting records are provided at the end of this manual for completion as required.

carrying out any work on the equipment, the user should be familiar with the contents of the safety and technical data sections and the ratings on the equipment’s rating label.

.2 Safety Instructions

[此处图片未下载成功]

WARNING: Hazardous voltages are present in this electrical equipment during operation. Non-observance of the safety rules can result in severe personal injury or propehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949rty damage.

[此处图片未下载成功]

WARNING: Only qualified personnel shall work on and around this equipment after becoming thoroughly familiar with all warnings and safety notices of this manual as well as with the applicable safety regulations.

attention must be drawn to the following:

The earthing screw of the device must be connected solidly to the protective earth conductor

any other electrical connection is made. z Hazardous voltages can be present on all circuits and components connected to the supply

or to the measuring and test quantities. z Hazardous voltages can be present in the device even after disconnection of the supply

(storage capacitors!) z The limit values stated in the technical data (Chapter 2) must not be exceeded at all, not even

testing and commissioning. z When testing the device with secondary test equipment, makehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 sure that no other

quantities are connected. Take also into consideration that the trip circuits and maybe also close commands to the circuit breakers and other primary switches are

NARI-RELAYS ELECTRIC CO., LTD

Chapter 10 Commissioning

[此处图片未下载成功]

from the device unless expressly stated.

[此处图片未下载成功]

DANGER: Current transformer secondary circuits must have been short-circuited before the current leads to the device are disconnected.

[此处图片未下载成功]

WARNING: Primary test may only be carried out by qualified personnel, who are familiar with the commissioning of protection system, the operation of the plant and safety rules and regulations (switching, earthing, etc.)

.3 Commission Tools

equipment required:

Multifunctional dynamic current and voltage injection test set with intervahttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949l timer.

Multimeter with suitable AC current range and AC/DC voltage ranges of 0~440V and 0~250V

. z Continuity tester (if not included in the multimeter). z Phase angle meter. z

[此处图片未下载成功]

Phase rotation meter.

: Modern test set may contain many of the above features in one unit.

equipment:

An electronic or brushless insulation tester with a DC output not exceeding 500V (for

resistance test when required). z A portable PC, with appropriate software (this enables the rear communications port to be

, if this is to be used, and will also save considerable time during commissioning). z EIA RS-485 to EIA RS-232 converter (if EIA RS-485 IEC60870-5-103 port is being tested). z PCS-9600 serials relay dedicated protection tester HELP-2000A.

.4 Setting Familiarization

commissioning a PCS-9611 relay for the http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949first time, sufficient time should be allowed to become familiar with the method by which the settings are applied. The Chapter 6 contains a detailed description of the menu structure of this relay.

the front cover in place all keys are accessible. All menu cells can be read. LED indicators and alarms can be reset. Protection or configuration settings can be changed, or fault and event records cleared. However, menu cells will require the appropriate password to be entered before

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 10 Commissioning

can be made.

, if a portable PC is available together with suitable setting software (such as RCS-9700 SAS software), the menu can be viewed a page at a time to display a full column of data and text. This PC software also allows settings to be entered more easily, saved to a file on disk for futurhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949e reference or printed to produce a setting record. Refer to the PC software user manual for details. If the software is being used for the first time, allow sufficient time to become familiar with its operation.

.5 Product Checks

product checks cover all aspects of the relay which should be checked to ensure that it has not been physically damaged prior to commissioning, is functioning correctly and all input quantity measurements are within the stated tolerances.

the application-specific settings have been applied to the relay prior to commissioning, it is advisable to make a copy of the settings so as to allow them restoration later. This could be done by extracting the settings from the relay itself via printer or manually creating a setting record.

.5.1 With the Relay De-energized

relay is fully numerical and the hardware is continuously monitored. Commissioning tests canhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 be kept to a minimum and need only include hardware tests and conjunctive tests. The function tests are carried out according to user’s correlative regulations.

following tests are necessary to ensure the normal operation of the equipment before it is first put into service. z Hardware tests

tests are performed for the following hardware to ensure that there is no hardware

. Defects of hardware circuits other than the following can be detected by self-monitoring when the DC power is supplied. z User interfaces test

Binary input circuits and output circuits test z AC input circuits test z Function tests

tests are performed for the following functions that are fully software-based. Tests of

protection schemes and fault locator require a dynamic test set. z Measuring elements test z Timers test

Metering and recording test z Conjunctive tests

://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ING NARI-RELAYS ELECTRIC CO., LTD

Chapter 10 Commissioning

[此处图片未下载成功]

tests are performed after the relay is connected with the primary equipment and other external equipment. z On load test.

Phase sequence check and polarity check. 10.5.1.1 Visual Inspection

unpacking the product, check for any damage to the relay case. If there is any damage, the internal module might also have been affected, contact the vendor. Following items listed is necessary.

Protection panel

examine the protection panel, protection equipment inside and other parts inside to

that no physical damage has occurred since installation.

rated information of other auxiliary protections should be checked to ensure it is correct for the particular installation. z Panel wiring

the conducting wire which is used in the panel to assure http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949that their cross section

the requirement.

examine the wiring to see that they are no connection failure exists. z Label

all the isolator binary inputs, terminal blocks, indicators, switches and push buttons to make sure that their labels meet the requirements of this project. z Equipment plug-in modules

each plug-in module of the equipments on the panel to make sure that they are well installed into the equipment without any screw loosened. z Earthing cable

whether the earthing cable from the panel terminal block is safely screwed to the panel

sheet.

Switch, keypad, isolator binary inputs and push button

whether all the switches, equipment keypad, isolator binary inputs and push buttons

normally and smoothly. 10.5.1.2 Insulation Test (if required)

resistance tests are only necessary during commihttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ssioning if it is required for them to be done and they have not been performed during installation.

all wiring from the earth and test the isolation with an electronic or brushless insulation tester at a DC voltage not exceeding 500V, The circuits need to be tested should include:

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 10 Commissioning

Voltage transformer circuits z Current transformer circuits z DC power supply

Optic-isolated control inputs z Output contacts z Communication ports

insulation resistance should be greater than 100M  at 500V. Test method:

unplug all the terminals sockets of this relay, and do the Insulation resistance test for each circuit above with an electronic or brushless insulation tester.

completion of the insulation resistance tests, ensure all external wiring is correctly reconnected to thttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949he protection

.5.1.3 External Wiring

that the external wiring is correct to the relevant relay diagram and scheme diagram. Ensure as far as practical that phasing/phase rotation appears to be as expected.

the wiring against the schematic diagram for the installation to ensure compliance with the customer’s normal practice. 10.5.1.4 Auxiliary Supply

relay can be operated from either 110/125Vdc or 220/250Vdc auxiliary supply depending on the relay’s nominal supply rating. The incoming voltage must be within the operating range specified in the following table, before energizing the relay, measure the auxiliary supply to ensure it within the operating range.

Voltage

[此处图片未下载成功]

Variation

% ~ 120%

% ~ 120%

should be noted that the relay can withstand an AC ripple of up to 12% of the upper rated voltage on the DC auxiliary supply.://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ar: Energize this relay only if the power supply is within the specified operating ranges.

.5.2 With the Relay Energized

following groups of checks verify that the relay hardware and software is functioning correctly and should be carried out with the auxiliary supply applied to the relay.

current and voltage transformer connections must remain isolated from the relay for these checks. The trip circuit should also remain isolated to prevent accidental operation of the

NARI-RELAYS ELECTRIC CO., LTD

Chapter 10 Commissioning

[此处图片未下载成功]

circuit breaker.

.5.2.1 Front Panel LCD Display

liquid crystal display (LCD) is designed to operate in a wide range of substation ambient temperatures. For this purpose, this relay has an automatic “LCD contrast” adjusting feature, which is capable to adjust LCD contrahttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949st automatically according to the ambient temperature. Connect the relay to DC power supply correctly and turn the relay on. Check program version and forming time displayed in command menu to ensure that are corresponding to what ordered. 10.5.2.2 Date and Time

the time and date is not being maintained by substation automation system, the date and time should be set manually.

the date and time to the correct local time and date using menu item “CLOCK”.

the event of the auxiliary supply failing, with a battery fitted on CPU board, the time and date will be maintained. Therefore when the auxiliary supply is restored the time and date will be correct and not need to set again.

test this, remove the auxiliary supply from the relay for approximately 30s. After being re-energized, the time and date should be correct. 10.5.2.3 Light Emitting Diodes (LEDs)

power up, the green LED “HEALhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949THY” should have illuminated and stayed on indicating that the relay is healthy.

relay has latched signal relays which remember the state of the trip, auto-reclose when the relay was last energized from an auxiliary supply. Therefore these indicators may also illuminate when the auxiliary supply is applied. If any of these LEDs are on then they should be reset before proceeding with further testing. If the LED successfully reset, the LED goes out. There is no testing required for that that LED because it is known to be operational.

is likely that alarms related to voltage transformer supervision will not reset at this stage. 10.5.2.4 Testing the HEALTHY and ALARM LEDs

the rated DC power supply and check that the “HEALTHY” LED is lighting in green. We need to emphasize that the “HEALTHY” LED is always lighting in operation course except that the equipment find serious errors in it.

://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 one of the abnormal conditions listed in Chapter 4, the “ALARM” LED will light in yellow. When abnormal condition reset, the “ALARM” LED extinguishes. 10.5.2.5 Testing the TRIP LED

“TRIP” LED can be tested by initiating a manual circuit breaker trip from the relay. However the “TRIP” LED will operate during the setting checks (performed later). Therefore no further testing of the “TRIP” LED is required at this stage.

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 10 Commissioning

.5.2.6 Testing the RECLOSE LED

“RECLOSE” LED can be tested by initiating a manual circuit breaker trip from the relay. However the “RECLOSE” LED will operate during the setting checks (performed later). Therefore no further testing of the “RECLOSE” LED is required at this stage. 10.5.2.7 Testing the AC Current Inputs

test verified that the accuracy of current meashttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949urement is within the acceptable tolerances. Apply current equal to the line current transformer secondary winding rating to each current transformer input of the corresponding rating in turn, see the following table or external connection diagram for appropriate terminal numbers, checking its magnitude using a multimeter/test set readout. The corresponding reading can then be checked in the relays menu.

current measurement accuracy of the relay is &#177;2.5%. However an additional allowance must be made for the accuracy of the test equipment being used. Current channel linearity and precision checkout

Input

(on LCD)

.5.2.8 Testing the AC Voltage Inputs

test verified that the accuracy of voltage measurement is within the acceptable tolerances. Apply rated voltage to each voltage transformer input in turn; checking its magnitude using a mhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ultimeter/test set readout. The corresponding reading can then be checked in the relays menu. The voltage measurement accuracy of the relay is &#177;0.5%. However an additional allowance must be made for the accuracy of the test equipment being used. Voltage channel linearity and precision checkout

Input

(on LCD)

.5.2.9 Testing the Binary Inputs

test checks that all the binary inputs on the relay are functioning correctly.

binary inputs should be energized one at a time, see external connection diagrams for terminal numbers.

that the voltage applied on the binary input must be within the operating range.

NARI-RELAYS ELECTRIC CO., LTD 137

Chapter 10 Commissioning

[此处图片未下载成功]

status of each binary input can be viewed using menu item “ENABLING_BI” and “TELE_BI_STATE”. “1” dehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949notes an energized input and “0” denotes a de-energized input. Binary Inputs testing checkout

Name

without energized

with energized

[此处图片未下载成功]

?

.5.3 Protective Function Testing

setting checks ensure that the entire application-specific relay, for the particular installation, has been correctly applied to the relay.

: The trip circuit should remain isolated during these checks to prevent accidental operation of the associated circuit breaker.

.5.3.1 Demonstrate correct protection operation

above tests have already demonstrated that the protection is within calibration, thus the purpose of these tests is as follows:

To conclude that the primary function of the protection can trip according to the correct

settings. z To verify correct setting of all related phttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949rotective elements. 10.5.3.2 Overcurrent Protection Check

check, performed the stage 1 overcurrent protection function in the No.1 setting group, demonstrates that the relay is operating correctly at the application-specific settings. 1. Enable the stage 1 overcurrent protection with VCE and directional element control.

Set the logic setting [En_OC1] as “1” in the relay’s “PROTECT_SETTING” menu. z Set the logic setting [En_VCE_OC1] as “1” in the relay’s “PROTECT_SETTING” menu. z Make the setting [Opt_Dir_OC1] as “1” in the relay’s “PROTECT_SETTING” menu. z Set other logic settings as “0” in the relay’s “PROTECT_SETTING” menu. z Set the VEBI setting [VEBI_OC1] as “1” in the “Virtual_Enabling_BI” menu.

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 10 Commissioning

. De-energize all the binary inputs of this relay.

. Simulate a normal condition withttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949h normal busbar voltage and line current and voltage. 4. Simulate a single-phase fault or multi-phase fault, the current of the fault phase is 1.05 &#215;

[I_OC1], and the bus voltages satisfy the VCE condition (see Section 3.2.2) and forward directional control condition (see Section 3.2.3). 5. After the period of [t_OC1], the stage 1 overcurrent protection will operate and issue the trip

. The “TRIP” LED indicator will be lit; a relevant report will be shown on the LCD. 6. After the fault is disappeared, this relay will restore the stage 1 overcurrent protection

. Restore the “TRIP” indicator and the LCD manually. 10.5.3.3 IDMT Overcurrent Protection Check

check, performed the IDMT overcurrent protection function with very inverse curve in No.1 setting group, demonstrates that the relay is operating correctly at the application-specific settings. 1. Enable the IDMT overcurrehttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949nt protection.

Set the logic setting [En_OC1] as “1” in the relay’s “PROTECT_SETTING” menu. z Set the logic setting [En_InvOC] as “1” in the relay’s “PROTECT_SETTING” menu. z Set the setting [Opt_InvOC] as “2” in the relay’s “PROTECT_SETTING” menu. z Set other logic settings as “0” in the relay’s “PROTECT_SETTING” menu. z Set the VEBI setting [VEBI_OC1] as “1” in the “Virtual_Enabling_BI” menu. 2. De-energize all the binary inputs of this relay.

. Simulate a normal condition with normal busbar voltage and line current and voltage. 4. Simulate a single-phase fault or multi-phase fault, and the current of the fault phase is 2 &#215;

[I_OC1]. 5. After the period of 13.5 &#215; [TMS_InVOC] &#215; [t_OC1], the IDMT overcurrent protection will

and issue the trip command. The “TRIP” LED indicator will be lit; a relevant report will be shown on the LCD.

. After the fault is disappeared, thihttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949s relay will restore the IDMT protection automatically. Restore

“TRIP

[此处图片未下载成功]

” indicator and the LCD manually.

: The IDMT overcurrent protection with standard inverse curve or extremely can be checked through the same method. Note to set the relevant characteristic and logic settings correctly.

.5.3.4 Zero Sequence Overcurrent Protection Check

check, performed the stage 1 zero sequence overcurrent protection function in the No.1 setting group, demonstrates that the relay is operating correctly at the application-specific settings.

NARI-RELAYS ELECTRIC CO., LTD

Chapter 10 Commissioning

[此处图片未下载成功]

. Enable the stage 1 zero sequence overcurrent protection.

Set the logic setting [En_ROC1] as “1” in the relay’s “PROTECT_SETTING” menu. z Set other logic settings as “0” in the relay’s “PROTECT_SETTING” http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949menu. z Set the setting [Opt_Calc_3I0] as “0” in the relay’s “SYS SETTINGS” menu. z Set the VEBI setting [VEBI_ROC1] as “1” in the “Virtual_Enabling_BI” menu. 2. De-energize all the binary inputs of this relay.

. Simulate a normal condition, the external input current of the zero sequence CT is less than

.95 &#215; [I_ROC1]. 4. Simulate a single-phase earth fault, the external input current of the zero sequence CT is

than 1.05 &#215; [I_ROC1]. 5. After the period of [t_ROC1], the stage 1 zero sequence overcurrent protection will operate

issue the trip command. The “TRIP” LED indicator will be lit; a relevant report will be shown on the LCD.

. After the fault is disappeared, this relay will restore the stage 1 zero sequence overcurrent

automatically. Restore the “TRIP” indicator and the LCD manually.

[此处图片未下载成功]

NOTE: Another way for testing the zerohttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 sequence overcurrent protection is using the self- calculation zero sequence current.

.5.3.5 Thermal Overload Protection Check

check, performed the thermal overload protection function in No.1 setting group, demonstrates that the relay is operating correctly at the application-specific settings. 1. Enable the thermal overload protection.

Set the logic setting [En_OvLd] as “1” in the relay’s “PROTECT_SETTING” menu. z Set other logic settings as “0” in the relay’s “PROTECT_SETTING” menu. z Set the VEBI setting [VEBI_OvLd] as “1” in the “Virtual_Enabling_BI” menu. 2. De-energize all the binary inputs of this relay.

. Simulate a normal condition with normal bus voltage and line current and voltage, and the

current of the line is less than 0.95 &#215; [I_OvLd]. 4. Simulate a line overload condition; the current of the line is more than 1.05 &#215; [I_OvLd]. 5. After the period of [t_http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949OvLd], the thermal overload protection will operate and issue the trip

. The “TRIP” LED indicator will be lit; a relevant report will be shown on the LCD. 6. After the fault is disappeared, this relay will restore the thermal overload protection

. Restore the “TRIP” indicator and the LCD manually.

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 10 Commissioning

.5.3.6 UFLS Protection Check

check, performed the UFLS protection function in No.1 setting group, demonstrates that the relay is operating correctly at the application-specific settings. 1. Enable the UFLS protection.

Set the logic setting [En_UFLS] as “1” in the relay’s “PROTECT_SETTING” menu. z Set the logic setting [En_df/dt_UFLS] as “1” in the relay’s “PROTECT_SETTING” menu. z Set other logic settings as “0” in the relay’s “PROTECT_SETTING” menu. z Set the VEBhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949I setting [VEBI_UFLS] as “1” in the “Virtual_Enabling_BI” menu. 2. Energize the binary input [EBI_UFLS], and de-energize all the other binary inputs. 3. Simulate a normal condition with normal bus voltage and line current and voltage.

. Simulate a system frequency decline condition. The decline rate of the frequency is less than

setting [df/dt_UFLS], and the input busbar voltage is greater than the setting [Vpp_UV_VCE_UFLS]. 5. After the period of [t_UFLS], the UFLS protection will operate and issue the trip command.

“TRIP” LED indicator will be lit; a relevant report will be shown on the LCD.

. After the fault is disappeared, this relay will restore the UFLS protection automatically.

the “TRIP” indicator and the LCD manually. 10.5.3.7 Auto-recloser Check

check, performed the auto-reclosing with synchronism check function in No.1 setting group, demonstrates that thhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949e relay is operating correctly at the application-specific settings.

are many operation elements can make the auto-recloser operate. Here, all the check is based on the assumption that the stage 1 overcurrent protection is operated. 1. Enable the stage 1 overcurrent protection and auto-recloser of this relay.

Set the logic setting [En_OC1] as “1” in the relay’s “PROTECT_SETTING” menu. z Set the logic setting [En_AR] as “1” in the relay’s “PROTECT_SETTING” menu.

Set the logic setting [En_SynChk_AR] as “1” in the relay’s “PROTECT_SETTING” menu. z Set the logic setting [En_DeadChk_AR] as “0” in the relay’s “PROTECT_SETTING”

. z Set other logic settings as “0” in the relay’s “PROTECT_SETTING” menu. z Set the setting [N_AR] as “1” in the relay’s “PROTECT_SETTING” menu. z Set the VEBI setting [VEBI_OC1] as “1” in the “Virtual_Enabling_BI” menu. z Set the VEBI setting [VEBI_AR] as “1” in the “Vhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949irtual_Enabling_BI” menu.

NARI-RELAYS ELECTRIC CO., LTD 141

Chapter 10 Commissioning

[此处图片未下载成功]

. De-energize all the binary inputs of this relay.

. Simulate a normal condition with normal busbar voltage and line current and voltage, and the

breaker is closed. After 15s delay, the auto-recloser is ready and in service. A full charged battery sign is shown on the right bottom of the LCD. 4. Simulate a single-phase fault or multi-phase fault, and the current of the fault phase is 1.05 &#215;

[I_OC1]. 5. After the period of [t_OC1], the stage 1 overcurrent protection will operate and issue the trip

. The “TRIP” LED indicator will be lit; a relevant report will be shown on the LCD. 6. Just at the same time, simulate a normal condition with normal voltage inputs (busbar and line)

without current inputs, and the circuit breaker ishttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 opened. After the period of [t_AR], the

recloser will operate, the “RECLOSE” LED indicator will be lit; a relevant report will be shown on the LCD.

auto-recloser with other check modes can be checked through the same method. Note to set the relevant logic settings as “1”. For more information about the auto-recloser theory, see Section 3.12 “Three Phase Auto-reclosing”

.5.3.8 SOTF Overcurrent Protection Check

check, performed the SOTF overcurrent protection in No.1 setting group, demonstrates that the relay is operating correctly at the application-specific settings.

. Enable the SOTF overcurrent protection. Do following configuration on the base of the setting

as described in Section 10.5.3.7.

Set the logic setting [En_OC_SOTF] as “1” in the relay’s “PROTECT_SETTING” menu. z Set the setting [Opt_SOTF] as “0” in the relay’s “PROTECT_SETTING” menu.http://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 z Set the VEBI setting [VEBI_OC_SOTF] as “1” in the “Virtual_Enabling_BI” menu. 2. De-energize all the binary inputs of this relay.

. Repeat the step 3 to step 6 as described in Section 10.5.3.7, and make the stage 1

protection and the auto-recloser operate successfully. 4. Simulate a single-phase fault or multi-phase fault, and the current of the fault phase is 2 &#215;

[I_OC_SOTF], and the circuit breaker is closed at the same time. 5. After the period of [t_OC_SOTF], the SOTF overcurrent protection will operate and issue the

command. The “TRIP” LED indicator will be lit; a relevant report will be shown on the LCD.

.5.4 On-load Checks

objectives of the on-load checks are:

Confirm the external wiring to the current and voltage inputs is correct. z Measure the magnitude of on-load current and voltage (if applicable).

NARI-RELAYShttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949 ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 10 Commissioning

Check the polarity of each current transformer.

, these checks can only be carried out if there are no restrictions preventing the tenderization of the plant being protected.

all test leads, temporary shorting leads, etc. and replace any external wiring that has been removed to allow testing.

it has been necessary to disconnect any of the external wiring from the protection in order to perform any of the foregoing tests, it should be ensured that all connections are replaced in accordance with the relevant external connection or scheme diagram. Confirm current and voltage transformer wiring.

.5.5 Final Checks

the above tests are completed, remove all test or temporary shorting leads, etc. If it has been necessary to disconnect any of the external wiring from the protection in order to perhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949form the wiring verification tests, it should be ensured that all connections are replaced in accordance with the relevant external connection or scheme diagram. Ensure that the protection has been restored to service.

the protection is in a new installation or the circuit breaker has just been maintained, the circuit breaker maintenance and current counters should be zero. If a test block is installed, remove the test plug and replace the cover so that the protection is put into service.

that all event records, fault records, disturbance records and alarms have been cleared and LED’s has been reset before leaving the protection.

NARI-RELAYS ELECTRIC CO., LTD 143

Chapter 10 Commissioning

[此处图片未下载成功]

NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 11 Maintenance Chapter 11 Maintenance

.1 Maintenance Schedule://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ris recommended that products supplied by NARI-RELAYS receive periodic monitoring after installation. In view of the critical nature of protective relays and their infrequent operation, it is desirable to confirm that they are operating correctly at regular intervals.

relay is self-supervised and so requires less maintenance than earlier designs of relay. Most problems will result in an alarm so that remedial action can be taken. However, some periodic tests should be done to ensure that the relay is functioning correctly and the external wiring is intact.

.2 Regular Testing

relay is almost completely self-supervised. The circuits which can not be supervised are binary input, output circuits and human machine interfaces. Therefore regular testing can be minimized to checking the unsupervised circuits.

.3 Failure Tracing and Repair

will be detected by automatic superhttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949vision or regular testing.

a failure is detected by supervision, a remote alarm is issued and the failure is indicated on the front panel with LED indicators and LCD display. It is also recorded in the alarm record. Failures detected by supervision are traced by checking the “ALM REPORT” screen on the LCD. See Section 0 “Display under Abnormal Condition” for the details of the alarm events.

a failure is detected during regular testing, confirm the following:

Test circuit connections are correct

Modules are securely inserted in position

Correct DC power voltage is applied

Correct AC inputs are applied

Test procedures comply with those stated in the manual

.4 Replace Failed Modules

the failure is identified to be in the relay module and the user has spare modules, the user can recover the protection by replacing the failed modules.

://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949NG NARI-RELAYS ELECTRIC CO., LTD 145

Chapter 11 Maintenance

[此处图片未下载成功]

Repair at the site should be limited to module replacement. Maintenance at the component level is not recommended.

that the replacement module has an identical module name and hardware type-form as the removed module. Furthermore, the replaced module should have the same software version. And the replaced analog input module and power supply module should have the same ratings.

[此处图片未下载成功]

WARNING: Units and modules may only be replaced while the supply is switched off and

by appropriately trained and qualified personnel. Strictly observe the basic precautions to guard against electrostatic discharge.

[此处图片未下载成功]

WARNING: When handling a module, take anti-static measures such as wearing an

wrist band and placing modules on an earthed conductive mat. Otherwise, mahttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ny of the electronic components could suffer damage. After replacing the CPU module, check the settings.

[此处图片未下载成功]

DANGER: After replacing modules, be sure to check that the same configuration is set

before the replacement. If this is not the case, there is a danger of the unintended operation of switchgear taking place or of protections not functioning correctly. Persons may also be put in danger.

NANJING NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 12 Decommissioning and Disposal Chapter 12 Decommissioning and Disposal

.1 Decommissioning

.1.1 Switching off

switch off this relay, switch off the external miniature circuit breaker of the power supply. 12.1.2 Disconnecting cables

the cables in accordance with the rules and recommendations made by relational department.

[此处图片未下载成功]

DANGER: Before dischttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949onnecting the power supply cables that connected with the power

module of this relay, make sure that the external miniature circuit breaker of the

[此处图片未下载成功]

power supply is switched off.

: Before disconnecting the cables that are used to connect analog input module

the primary CT and VT, make sure that the circuit breaker for the primary CT and VT is switched off.

.1.3 Dismantling

rack of this relay may now be removed from the system cubicle, after which the cubicles may

[此处图片未下载成功]

also be removed.

: When the station is in operation, make sure that there is an adequate safety

to live parts, especially as dismantling is often performed by unskilled personnel. 12.2 Disposal

every country there are companies specialized in the proper disposal of electronic waste.

[此处图片未下载成功]

NOTE: Strihttp://www.mianfeiwendang.com/doc/aa73319709c08f26d0fe4949ctly observe all local and national regulations when disposing of the device.

NARI-RELAYS ELECTRIC CO., LTD 147

Chapter 12 Decommissioning and Disposal

[此处图片未下载成功]

NANJING NARI-RELAYS ELECTRIC CO., LTD

[此处图片未下载成功]

Chapter 13 Manual Version History Chapter 13 Manual Version History

the current version of the instruction manual, several descriptions on existing features have been modified.

version and modification history records Version

.00

1.00    Date 2010-02-10    Description of change Form the original manual.

NARI-RELAYS ELECTRIC CO., LTD 149

Chapter 13 Manual Version History

[此处图片未下载成功]

NANJING NARI-RELAYS ELECTRIC CO., LTD

文档下载网是专业的免费文档搜索与下载网站，提供行业资料，考试资料，教学课件，学术论文，技术资料，研究报告，工作范文，资格考试，word文档，专业文献，应用文书，行业论文等文档搜索与文档下载，是您文档写作和查找参考资料的必备网站。

文档下载 http://www.mianfeiwendang.com/

亿万文档资料，等你来发现