Fire Damper BKA-EN

Specification text

The fire damper BKA-EN conforms to EN 15650, EN 13501-3 and EN 1366-2. BKA-EN has been tested according to EN 1366-2 in compliance with Declaration of performance no. 09-19-DoP-BSK-EN-2013-07-01. It has the EC certificate of conformity 0761 - CPD - 0244. Its category according to EN 13501-3 is EI 90 (ve, ho i↔o) S.

According to Directive 94/9/EC, EC Certificate of Conformity Number EPS 09 ATEX 2 153 X, its use in areas subject to explosion hazards is permitted, not only with spring return actuator X10 (ExMax-5.10-BF), including safety temperature limiter (FireSafe or ExPro-TT), but also with mechanical trigger via fusible link (manual actuation with or without ATEX limit switch ES-Ex). The fire damper is marked as follows according to

ATEX:

|  | II 2 G IIC T6 II 2D T80°C II 3 D T80°C*) | EPS 09 ATEX 2 153 X |
| --- | --- | --- |
| *) when using the safety temperature limiter FireSafe. |

Housing made of galvanised sheet steel - 2-part -, without circumferential stop profiles for largest possible free cross-section, thermal insulation made of silicate structural panels, 2 facing inspection openings. Damper blade made of abrasion-resistant, glass-fibre-reinforced lightweight concrete with circumferential hose and intumescent seals to meet the cold and hot leakage requirements according to DIN EN 1366-2.

Any accessories that may be required for the respective mounting situation (flexible connection pieces, suspensions, pole braces, etc.) are listed in separate positions of the specification.

For connection to ventilation ducts (one- or two-sided), air flow direction optional.

Connection to smoke detectors with general building supervisory approval possible.

Installation:

in solid walls and ceilings

on solid walls together with the mounting kit AS-E1 (the mounting kit AS-E1 can be used exclusively with   BKA-EN L=375.)

away from solid walls

with mounting frame in lightweight partition walls with metal posts and panelling on both sides as classified according to EN 1350 1-2 or comparable national standards. (The mounting frame can be used exclusively with BKA-EN L=500.)

directly under the ceiling with mineral wool inlay in lightweight partition walls with metal posts and panelling on both sides according to classification to EN 13501-2 or comparable national standards.

in lightweight partition walls with metal posts and panelling on both sides and inside steel sheet inlay (fire wall) in possession of the following general building supervisory test certificates (abP):

abP no. P-3391/170/08-MPA BS (Knauf)

abP no. P-3020/0109-MPA BS (Rigips)

abP no. P-3796/7968-MPA BS (Promat)

in lightweight partition walls with metal posts and panelling on one side according to classification to EN 13501-2 or comparable national standards.

flange to flange (for installation in solid walls and solid ceilings)

partial mortar lining (for installation in solid walls)

Product: SCHAKO type BKA-EN

Declaration of performance no. 09-19-DoP-BKA-EN-2013-07-01

Dimensions::

| Width (B): | ……………………..mm |
| --- | --- |
| Height (H): | ……………………..mm |
| Length (L): | 375 / 500 mm |
| (Unless stated otherwise, the mechanical model length 500 mm and fusible link trigger temperature 72°C will be delivered) |

Alternative designs or accessories (at an extra charge) (select as desired)

Model made of stainless steel material no. 1.4301 (V2A)

Model made of stainless steel material no. 1.4571 (V4A)

Housing with DD coating (solvent-containing two-component top coat based on polyurethane varnish - RAL 7035 / light-grey)

DD coating, inside/outside

Thermal release with mechanical fusible link release temperature 98°C (for hot-air heating)

Electric limit switch type ES for "OPEN" and/or "CLOSED" position indicators, switching element containing one NC and one NO contact:

Type ES 1Z: "CLOSED"

Type ES 1A: "OPEN"

Type ES 2: "OPEN" and "CLOSED"

Limit switch type ES-Ex for "OPEN" or/and "CLOSED" position indicators, application in areas subject to explosion hazards:

Type ES EX 1Z: "CLOSED"

Type ES EX 1A: "OPEN"

Type ES EX 2: "OPEN" and "CLOSED"

Limit switch type Easy-Eco-Tx, for connection to SCHAKO signalling and switching bus system EasyBus, the status of the damper position being transferred by radio signal. Additional radio receiver type Easy-Eco-Rx required.

Electric spring return actuator with thermoelectric release device BAT or BAE72B-S.

Triggers at a duct inside temperature of 72°C (optionally: 95°C) containing integrated micro switches for indication of damper end positions (24 V drive with connector), assignment of the actuators according to Fehler! Verweisquelle konnte nicht gefunden werden. page Fehler! Textmarke nicht definiert.:

    - Type B10 (BFL24-T-ST SO)

B11 (BFL130-T SO)

B20 (BFN24-T-ST SO)

B21 (BFN230-T SO)

B30 (BF24-T-ST SO)

B31 (BF230-T SO)

Electric spring return actuator with thermoelectric trigger device BAE72 TL

Triggers at a duct inside temperature of 72°C (optionally: 95°C) containing integrated micro switches for indication of damper end positions, connection to LON or Belimo MP bus systems possible via communication devices. Available for all dimensions.

Type B40 (BF24TL-T-ST SO; 24V AC/DC)

  - Communication device BKN230-24 LON for connection to LON bus system

  - Communication device BKN230-24MP for connection to Belimo MP bus system

Electric explosion-protected spring return actuator with safety temperature limiter (FireSafe or ExPro-TT).

  - Triggers at a duct inside temperature of 72°C (option: 95%)

  - End position signalling by integrated auxiliary switches

  - Type X10 (ExMax-5.10-BF; universal power supply 24 - 240 V AC/DC)

Joventa - Drives upon request

Pneumatic swivel drive type PND 6 bar

Magnetic clamp/pulse magnet (24 V DC, 230 V AC)

Extension piece type VT, for installation with large wall/ceiling thicknesses; to maintain the minimum distance amin = 50 mm from the open damper blade when mounting the finishing protective grating type ASG, flexible connection piece type FS or duct connection pipe type RS. Extension part made of galvanised profiled sheet steel fitted with connecting flanges, L=180 mm (damper height 200 to 750 mm), L=210 mm (damper height 800 mm).

Product: SCHAKO type VT

Dimensions:

| Width (B): | ……………………mm |
| --- | --- |
| Height (H): | ……………………mm |

Extra charge for anticorrosive paint - inside/outside -

  - DD coating (two-component top coat based on polyurethane varnish - RAL 7035 / light-grey)

Extra charge for powder coating (RAL 9010 / pure white), inside and outside

Extra charge for design:

Material no. 1.4301 (V2A)

Material no. 1.4571 (V4A)

Assembly part type EBT, to be built into the SCHAKO smoke detection system RMS, assembly part made of profiled galvanised sheet steel (painted black matt on the inside) fitted with connection flanges and installation opening to fit SCHAKO smoke detection system RMS, L= 180 mm (damper height 200 to 750 mm), L = 210 mm (damper height 800 mm).

Product: SCHAKO type EBT

Dimensions:

| Width (B): | ……………………mm |
| --- | --- |
| Height (H): | ……………………mm |

Extra charge for design:

Material no. 1.4301 (V2A)

Material no. 1.4571 (V4A)

Flexible connection piece type FS, consisting of profiled connection flanges made of galvanised sheet steel with elastic intermediate piece made of polyester fabric PVC-coated on both sides, normally inflammable to EN 13501-1, with welded lip seals (tightness class C to EN 13180 / EN 1507; temperature-resistant from -20°C to 80°C). Flexible part of the connection piece (polyester fabric) must have a minimum length Lmin of 100 mm when mounted, resulting in an installation dimension of approx L = 160 mm.

The required equipotential bonding must be carried out on-site according to VDE regulations.  The fire dampers must not be subject to mechanical stress under any circumstances.

Product: SCHAKO type FS

Dimensions:

| Width (B): | ……………………mm |
| --- | --- |
| Height (H): | ……………………mm |

Extra charge for connection flanges made of:

Material no. 1.4301 (V2A)

Material no. 1.4571 (V4A)

Duct connection pipe type RS, for connecting round ventilation ducts to BKA-EN, consisting of joining plate with bores and connecting pipe, galvanised sheet steel.

Product: SCHAKO type RS

Dimensions (B;H according to damper size):

| Width (B): | ……………………mm |
| --- | --- |
| Height (H): | ……………………mm |
| Connection pipe ø (øD) | ……………………mm |

Extra charge for anticorrosive paint - inside and outside -

  - DD coating (two-component top coat based on polyurethane varnish - RAL 7035 / light-grey)

Extra charge for powder coating (RAL 9010 / pure white), inside and outside

Extra charge for design:

Material no. 1.4301 (V2A)

Material no. 1.4571 (V4A)

Finishing protective grating type ASG, for connection with ventilation duct connection on only one side, galvanised sheet steel, mesh width < 20 mm, minimum distance amin = 50 mm from the open damper blade must be taken into account, if necessary, use extension piece type VT.

Product: SCHAKO type ASG

Dimensions:

| Width (B): | ……………………mm |
| --- | --- |
| Height (H): | ……………………mm |

Extra charge for anticorrosive paint - inside and outside -

  - DD coating (two-component top coat based on polyurethane varnish - RAL 7035 / light-grey)

Extra charge for powder coating (RAL 9010 / pure white), inside and outside

Extra charge for design:

Material no. 1.4301 (V2A)

Material no. 1.4571 (V4A)

Position indicator type MSZ, consisting of a steel cable - galvanised - with clamping nipple and position indicator made of plastic material. The mechanical position indicator for false ceilings is usable for each mechanically operated BKA-EN with hand lever.

Product: SCHAKO type MSZ

Mounting frame type ER, consisting of silicate structural panels, incl. fastening material and glue on waterglass base, for installation of the BKA-EN (L=500) in lightweight partition walls with metal posts and panelling on both sides according to classification to EN 13501-2 or comparable national standards. The mounting frame ER can be delivered loose as mounting kit or mounted ex works at an extra charge. A circumferential intumescent seal is located in the centre of the mounting frame ER.

Product: SCHAKO mounting frame type ER

Dimensions (B;H according to damper size):

| Width (B): | ……………………mm |
| --- | --- |
| Height (H): | ……………………mm |

(Unless stated otherwise, the mounting frame ER will be delivered loose as mounting kit)