3583 1-8h/D LED CGLine+

Pos.    )		ea.

Self-monitoring LED self-contained safety luminaire for ceiling recessing with asymmetric optics according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-560 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CGLine+ Web-Controller (requires a non-shielded 2-core bus line).

Round Bezel with 80 mm diameter, coated white (similar to RAL 9010). Heat sink of die cast aluminium. Installation of the luminaire without use of tools by clamping springs for ceiling thicknesses of up to 20 mm. Drill hole diameter 68 mm. LED supply module in a separate housing made of plastics with through-wiring terminals and strain relief. Required depth for entering the ceiling only 250 mm.

Symmetric white beam light distribution for enlarged spacing with mounting heights of up to 9m. Maximum spacing between luminaires: > 15m from mounting heights of between 6 m to 9 m (1 h operation/escape route illumination). In 8 h operation, mounting heights of up to 3.5 m are achieved with maximum spacing between luminaires of 7 m (basis of calculation at least 1 lx in escape route illumination - maintenance factor WF = 0.8).

Light source: 3 x high efficient, white HighPower LEDs 1 W with a service life of 50.000 h due to optimised LED operating conditions.

Serial functionality:

- Manual function test or duration test via integrated testing button

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED

- Automatic function test (weekly) and automatic duration test (every 6 months)

Can be optionally switched off with reminder of due duration test after 12 months

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

- Blocking function via CGLine+ Web-Controller during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux:					385 lm

Luminous flux E/N

at the end of rated operating time: 		100% at 1 h, 70% at 3 h, 25% at 8 h

Battery:						LiIon 3.7V 4000mAh

Housing material: 				steel, PC

Housing colour: 				white (similar to RAL 9010)

Connection terminal:				Through-wiring from mains L, L’, N, PE to 2.5 mm²

CGLine+ bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V AC, 50/60 Hz

Connected load with mains operation: 		7 VA / 6.6 W

Insulation class:					II

Type of protection				IP 40

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions (mm) :				D = 80 H = 38

Housing for LED converter:

L = (340 + 50), H = 46 (bent construction)

Dimensions - ceiling cutout (mm):		Diameter = 68mm

Type: 3583 1-8h/D LED CGLine+

Manufacturer: CEAG