71811 1-8h/D LED CGLine+

Pos.    )		ea.

Self-monitoring self-contained Escape sign luminaire, singled sided, according to EN 60598-1, EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-560 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CGLine+ Web-Controller (requires a non-shielded 2-core bus line).

Luminaire housing for wall mounting, made from Aluminium profile, matt anodized, with pictogram made from polycarbonate with silk-screen printing.

Uniform illumination of the pictogram with Lm >= 500 cd/m² (Mains operation) in the white area.

Serial functionality:

- Manual function test or duration test via testing button

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED

- Automatic function test (weekly) and automatic duration test (every 6 months)

Can be optionally switched off with reminder of due duration test after 12 months

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

- Blocking function via CGLine+ Web-Controller during idle operating times

- Generally suitable for maintained or non-maintained operation

Viewing distance								32 m

Luminous flux (E/(N

at the end of rated operating time: 			100% at 1 h, 70% at 3 h, 25% at 8 h

Battery											LiIon 3.7V / 4000 mAh

Housing material: 								Aluminium

Housing colour: 								Matt anodized

Connection terminals:							Through-wiring from mains L, L’, N, PE to 2.5 mm²

CGLine+ bus through-wiring to 1.5 mm²

Connection voltage:							220 - 240 V, 50/60 Hz

Connected load with mains operation:		7 VA / 6.6 W

Insulation class: 								I

Protection rating: 								IP 40

Permissible ambient temperature: 			-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions (mm):								W = 349 mm, H = 188 mm, D = 80 mm

Pictograms:

….. Pictogram silk-screened

….. Pictogram blind

Accessories:

..... Wire guard

Type: 71811 1-8h/D LED CGLine+

Manufactured by: CEAG

71821 1-8h/D LED CGLine+ WM

Pos.    )		ea.

Self-monitoring self-contained Escape sign luminaire, double sided, according to EN 60598-1, EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-560 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CGLine+ Web-Controller (requires a non-shielded 2-core bus line).

Luminaire housing for 90° wall mounting, made from Aluminium profile, matt anodized, with pictogram made from polycarbonate with silk-screen printing.

Uniform illumination of the pictogram with Lm >= 500 cd/m² (Mains operation) in the white area.

Serial functionality:

- Manual function test or duration test via testing button

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED

- Automatic function test (weekly) and automatic duration test (every 6 months)

Can be optionally switched off with reminder of due duration test after 12 months

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

- Blocking function via CGLine+ Web-Controller during idle operating times

- Generally suitable for maintained or non-maintained operation

Viewing distance								32m

Luminous flux (E/(N

at the end of rated operating time: 			87% at 1 h, 45% at 3 h, 15% at 8 h

Battery											LiIon 3.7V / 4000 mAh

Housing material: 								Aluminium

Housing colour: 								Matt anodized

Connection terminals:							Through-wiring from mains L, L’, N, PE to 2.5 mm²

CGLine+ bus through-wiring to 1.5 mm²

Connection voltage:							220 - 240 V, 50/60 Hz

Connected load with mains operation:		8.8 VA / 8.3 W

Insulation class: 								I

Protection rating: 								IP 40

Permissible ambient temperature: 			-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions (mm):								W = 349 mm, H = 188 mm,  D = 80 mm

(Without mounting accessories)

Pictograms:

….. Pictogram silk-screened

….. Pictogram blind

Accessories:

..... Wall / Ceiling mounting kit

Type: 71821 1-8h/D LED CGLine+ WM

Manufactured by: CEAG

71821 1-8h/D LED CGLine+ DM

Pos.    )		ea.

Self-monitoring self-contained Escape sign luminaire, double sided, according to EN 60598-1, EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-560 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CGLine+ Web-Controller (requires a non-shielded 2-core bus line).

Luminaire housing for ceiling mounting, made from Aluminium profile, matt anodized, with pictogram made from polycarbonate with silk-screen printing.

Uniform illumination of the pictogram with Lm >= 500 cd/m² (Mains operation) in the white area.

Serial functionality:

- Manual function test or duration test via testing button

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED

- Automatic function test (weekly) and automatic duration test (every 6 months)

Can be optionally switched off with reminder of due duration test after 12 months

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

- Blocking function via CGLine+ Web-Controller during idle operating times

- Generally suitable for maintained or non-maintained operation

Viewing distance								32m

Luminous flux (E/(N

at the end of rated operating time: 			87% at 1 h, 45% at 3 h, 15% at 8 h

Battery											LiIon 3.7V / 4000 mAh

Housing material: 								Aluminium

Housing colour: 								Matt anodized

Connection terminals:							Through-wiring from mains L, L’, N, PE to 2.5 mm²

CGLine+ bus through-wiring to 1.5 mm²

Connection voltage:							220 - 240 V, 50/60 Hz

Connected load with mains operation:		8.8 VA / 8.3 W

Insulation class: 								I

Protection rating: 								IP 40

Permissible ambient temperature: 			-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions (mm):								W = 349 mm, H = 188 mm,  D = 80 mm

(Without mounting accessories)

Pictograms:

….. Pictogram silk-screened

….. Pictogram blind

Accessories:

..... Wall / Ceiling mounting kit

Type: 71821 1-8h/D LED CGLine+ DM

Manufactured by: CEAG

71821 1-8h/D LED CGLine+ PM

Pos.    )		ea.

Self-monitoring self-contained Escape sign luminaire, double sided, according to EN 60598-1, EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-560 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CGLine+ Web-Controller (requires a non-shielded 2-core bus line).

Luminaire housing for ceiling mounting, made from Aluminium profile, matt anodized, with pictogram made from polycarbonate with silk-screen printing.

Uniform illumination of the pictogram with Lm >= 500 cd/m² (Mains operation) in the white area.

Serial functionality:

- Manual function test or duration test via testing button

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED

- Automatic function test (weekly) and automatic duration test (every 6 months)

Can be optionally switched off with reminder of due duration test after 12 months

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

- Blocking function via CGLine+ Web-Controller during idle operating times

- Generally suitable for maintained or non-maintained operation

Viewing distance								32m

Luminous flux (E/(N

at the end of rated operating time: 			87% at 1 h, 45% at 3 h, 15% at 8 h

Battery											LiIon 3.7V / 4000 mAh

Housing material: 								Aluminium

Housing colour: 								Matt anodized

Connection terminals:							Through-wiring from mains L, L’, N, PE to 2.5 mm²

CGLine+ bus through-wiring to 1.5 mm²

Connection voltage:							220 - 240 V, 50/60 Hz

Connected load with mains operation:		8.8 VA / 8.3 W

Insulation class: 								I

Protection rating: 								IP 40

Permissible ambient temperature: 			-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions (mm):								W = 349 mm, H = 188 mm, D = 80 mm

(Without mounting accessories)

Pictograms:

….. Pictogram silk-screened

….. Pictogram blind

Accessories:

..... Suspension kit

..... Chain fastening

Type: 71821 1-8h/D LED CGLine+ PM

Manufactured by: CEAG