GuideLed  10611 1-3h/D AT Set-e

Pos.    )		ea.

Self-monitoring LED self contained escape sign luminaire for wall surface-mounting, according to EN 60598-1, EN 60598-2-22 and EN1838.

LED Lightguide technology for homogeneous and bright illumination of the pictogram acc. EN 1838. Including pictogram set acc. to ISO 7010 (arrow down, left, right) with snap-in mounting.

High service life via optimised LED operating conditions.

Increased safety via redundant construction of LED unit consisting of 3-chip LEDs with high luminous efficacy >100 lm/W for significantly reduced connected load. Polarity reversal-protected wiring of LED unit.

Slender design with low construction height of only 41 mm including pictogram and mounting set.

Tool-free mounting of LED pictogram to the mounting set. Cable infeeds at rear, above and on side,

with additional space for cable routing.

Serial functionality:

- Emergency light operating duration settable at 1 h, 2 h or 3 h

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

Can be optionally switched off with reminder of due duration test after 12 months.

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

(according to DIN VDE 0100-718)

- Generally suitable for maintained or non-maintained operation

Luminous flux (E/(N: 				80% at 1 h, 80% at 2 h, 75% at 3 h

Emergency light rated operating time:		1 h, 2 h or 3 h

Battery						LiIon 3.7V 2000 mAh

Viewing distance: 				20 m

Housing material: 				PC

Housing colour: 				Light grey RAL7035

Connection terminals:				Through-wiring  L, L’, N, PE up to 2.5 mm²

Connection voltage:				220 - 240 V AC, 50 Hz

Connected load with mains operation:		3.8 VA / 3.3 W

Insulation class: 				II (functional earth required)

Protection rating: 				IP 20

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 226, H = 134, D = 13

Dimensions including wall mounting set:  	W = 226, H = 134, D = 41

Type: GuideLed 10611 1-3h/D AT Set-e

Manufacturer: CEAG

GuideLed 10621 1-3h/D AT Set-e

Pos.    )		ea.

Self-monitoring LED self contained escape sign luminaire for ceiling surface-mounting, according to EN 60598-1, EN 60598-2-22 and EN1838.

LED Lightguide technology for homogeneous and bright illumination of the pictogram acc. EN 1838. Including pictogram set acc. to ISO 7010 (arrow down, left, right, blind) with snap-in mounting.

High service life via optimised LED operating conditions.

Increased safety via redundant construction of LED unit consisting of 3-chip LEDs with high luminous efficacy >100 lm/W for significantly reduced connected load. Polarity reversal-protected wiring of LED unit.

Slender design with low pictogram width of only 12mm and canopy with height of only 33mm.

Serial functionality:

- Emergency light operating duration settable at 1 h, 2 h or 3 h

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

Can be optionally switched off with reminder of due duration test after 12 months.

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

(according to DIN VDE 0100-718)

- Generally suitable for maintained or non-maintained operation

Luminous flux (E/(N: 				80% at 1 h, 80% at 2 h, 75% at 3 h

Emergency light rated operating time:		1 h, 2 h or 3 h

Battery						LiIon 3.7V 2000 mAh

Viewing distance: 				20 m

Housing material: 				Polycarbonate

Housing colour: 				Light grey RAL7035

Connection terminals:				Through-wiring L, L’, N, PE up to 2.5 mm²

Connection voltage:				220 - 240 V AC, 50 Hz

Connected load with mains operation:		4.0 VA / 3.6 W

Insulation class: 				II (functional earth required)

Protection rating: 				IP 40

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 227, H = 134, D = 12

Dimensions of ceiling mounting set (mm):	W = 227, H = 33, D = 80

Type: GuideLed 10621 1-3h/D AT Set-e

Manufacturer: CEAG

GuideLed  10625 1-3h/D AT Set-e

Pos.    )		ea.

Self-monitoring LED self contained escape sign luminaire for wire suspension, according to EN 60598-1, EN 60598-2-22 and EN1838.

LED Lightguide technology for homogeneous and bright illumination of the pictogram acc. EN 1838. Including pictogram set acc. to ISO 7010 (arrow down, left, right, blind) with snap-in mounting.

High service life via optimised LED operating conditions.

Increased safety via redundant construction of LED unit consisting of 3-chip LEDs with high luminous efficacy >100 lm/W for significantly reduced connected load. Polarity reversal-protected wiring of LED unit.

Slender design with low pictogram width of only 12mm and canopy with height of only 33mm.

Wire mounting set includes transparent insulated wire suspension for voltage supply.

Freely settable suspension height adjusted without tools via steel cord holders to 1.5 m.

Serial functionality:

- Emergency light operating duration settable at 1 h, 2 h or 3 h

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

Can be optionally switched off with reminder of due duration test after 12 months.

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

(according to DIN VDE 0100-718)

- Generally suitable for maintained or non-maintained operation

Luminous flux (E/(N: 				80% at 1 h, 80% at 2 h, 75% at 3 h

Emergency light rated operating time:		1 h, 2 h or 3 h

Battery						LiIon 3.7V 2000 mAh

Viewing distance: 				20 m

Housing material: 				Polycarbonate

Housing colour: 				Light grey RAL7035

Connection terminals:				Through-wiring  L, L’, N, PE up to 2.5 mm²

Connection voltage:				220 - 240 V AC, 50 Hz

Connected load with mains operation:		4.0 VA / 3.6 W

Insulation class: 				II (functional earth required)

Protection rating: 				IP 40

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 227, H = 134, D = 12

Dimensions of ceiling mounting set (mm):	W = 227, H = 33, D = 80

Type: GuideLed 10625 1-3h/D AT Set-e

Manufacturer: CEAG

GuideLed  11611 1-3h/D AT Set-e

Pos.    )		ea.

Self-monitoring LED self contained escape sign luminaire for wall surface-mounting, according to EN 60598-1, EN 60598-2-22 and EN1838.

LED Lightguide technology for homogeneous and bright illumination of the pictogram acc. EN 1838. Including pictogram set acc. to ISO 7010 (arrow down, left, right) with snap-in mounting.

High service life via optimised LED operating conditions.

Increased safety via redundant construction of LED unit consisting of 3-chip LEDs with high luminous efficacy >100 lm/W for significantly reduced connected load. Polarity reversal-protected wiring of LED unit.

Slender design with low construction height of only 41 mm including pictogram and mounting set.

Tool-free mounting of LED pictogram to the mounting set. Cable infeeds at rear, above and on side,

with additional space for cable routing.

Serial functionality:

- Emergency light operating duration settable at 1 h, 2 h or 3 h

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

Can be optionally switched off with reminder of due duration test after 12 months.

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

(according to DIN VDE 0100-718)

- Generally suitable for maintained or non-maintained operation

Luminous flux (E/(N: 				95% at 1 h, 95% at 2 h, 90% at 3 h

Emergency light rated operating time:		1 h, 2 h or 3 h

Battery						LiIon 3.7V 2000 mAh

Viewing distance: 				30 m

Housing material: 				Polycarbonate

Housing colour: 				Light grey RAL7035

Connection terminals:				Through-wiring  L, L’, N, PE up to 2.5 mm²

Connection voltage:				220 - 240 V AC, 50 Hz

Connected load with mains operation:		4.0 VA / 3.6 W

Insulation class: 				II (functional earth required)

Protection rating: 				IP 20

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 326, H = 184, D = 13

Dimensions including wall mounting set:  	W = 326, H = 184, D = 41

Type: GuideLed 11611 1-3h/D AT Set-e

Manufacturer: CEAG

GuideLed  11621 1-3h/D  AT Set-e

Pos.    )		ea.

Self-monitoring LED self contained escape sign luminaire for ceiling surface-mounting, according to EN 60598-1, EN 60598-2-22 and EN1838.

LED Lightguide technology for homogeneous and bright illumination of the pictogram acc. EN 1838. Including pictogram set acc. to ISO 7010 (arrow down, left, right, blind) with snap-in mounting.

High service life via optimised LED operating conditions.

Increased safety via redundant construction of LED unit consisting of 3-chip LEDs with high luminous efficacy >100 lm/W for significantly reduced connected load. Polarity reversal-protected wiring of LED unit.

Slender design with low pictogram width of only 12mm and canopy with height of only 33mm.

Serial functionality:

- Emergency light operating duration settable at 1 h, 2 h or 3 h

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

Can be optionally switched off with reminder of due duration test after 12 months.

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

(according to DIN VDE 0100-718)

- Generally suitable for maintained or non-maintained operation

Luminous flux (E/(N: 				85% at 1 h, 80% at 2 h, 60% at 3h

Emergency light rated operating time:		1 h, 2 h or 3 h

Battery						LiIon 3.7V 2000 mAh

Viewing distance: 				30 m

Housing material: 				Polycarbonate

Housing colour: 				Light grey RAL7035

Connection terminals:				Through-wiring  L, L’, N, PE up to 2.5 mm²

Connection voltage:				220 - 240 V AC, 50 Hz

Connected load with mains operation:		double-sided 4.5 VA / 4.2 W

Insulation class: 				II (functional earth required)

Protection rating: 				IP 40

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 327, H = 184, D = 12

Dimensions of ceiling mounting set (mm):	W = 327, H = 33, D = 80

Type: GuideLed 11621 1-3h/D AT Set-e

Manufacturer: CEAG

GuideLed  11625 1-3h/D AT Set-e

Pos.    )		ea.

Self-monitoring LED self contained escape sign luminaire for wire suspension, according to EN 60598-1, EN 60598-2-22 and EN1838.

LED Lightguide technology for homogeneous and bright illumination of the pictogram acc. EN 1838. Including pictogram set acc. to ISO 7010 (arrow down, left, right, blind) with snap-in mounting.

High service life via optimised LED operating conditions.

Increased safety via redundant construction of LED unit consisting of 3-chip LEDs with high luminous efficacy >100 lm/W for significantly reduced connected load. Polarity reversal-protected wiring of LED unit.

Slender design with low pictogram width of only 12mm and canopy with height of only 33mm.

Wire mounting set includes transparent insulated wire suspension for voltage supply.

Freely settable suspension height adjusted without tools via steel cord holders to 1.5 m.

Serial functionality:

- Emergency light operating duration settable at 1 h, 2 h or 3 h

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

Can be optionally switched off with reminder of due duration test after 12 months.

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

(according to DIN VDE 0100-718)

- Generally suitable for maintained or non-maintained operation

Luminous flux (E/(N: 				85% at 1 h, 80% at 2 h, 60% at 3h

Emergency light rated operating time:		1 h, 2 h or 3 h

Battery						LiIon 3.7V 2000 mAh

Viewing distance: 				30 m

Housing material: 				Polycarbonate

Housing colour: 				Light grey RAL7035

Connection terminals:				Plug-in terminal 4 x 2 x 2.5 mm² (mains connection)

Connection voltage:				220 - 240 V AC, 50 Hz

Connected load with mains operation:		double-sided 4.5 VA / 4.2 W

Insulation class: 				II (functional earth required)

Protection rating: 				IP 40

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 327, H = 184, D = 12

Dimensions of ceiling mounting set (mm):  	W = 327, H = 33, D = 80

Type: GuideLed 11625 1-3h/D AT Set-e

Manufacturer: CEAG