GuideLed SL 13851 1-8h/D CGLine Ceiling recessed with asymmetric optics for the illumination of ‘Points of emphasis’ acc. EN 1838

Pos.    )		ea.

Self-monitoring LED self-contained safety luminaire for ceiling recessing with asymmetric optics for the illumination of ‘Points of emphasis’ acc. EN 1838, according to DIN EN 60598-1, DIN EN 60598-2-22 and for systems according to DIN EN 50172, DIN VDE 0100-718 and DIN V VDE V 0108-100 for separate operation or for connection to a central CGLine monitoring facility (requires a non-shielded 2-core bus line).

Asymmetric optics especially for 5 lx vertically for first aid posts, firefighting equipment and call points acc. EN 1838. Suitable for mounting heights up to 5.6 m above the illuminated equipment with a distance up to 2 m in horizontally. The illuminated area has a width of up to 2.8 m. (Calculation for 1 h duration and maintenance factor = 0.8)

Light source: 2 x high efficiency High Power LEDs, white, 1.6 W, with 50,000 h service life due to optimised LED operating conditions.

Rectangular design with appearance practically flush with the ceiling: visible housing part only 4 mm high. Low recess depth of only 39 mm. Heat sink of diecast aluminium. Tool-free mounting of luminaire via clamp springs for ceiling thicknesses to 20 mm. LED supply electronics in separate housing with plug connections with cable strain relief for mains and bus connection.

Serial functionality:

- Manual function test or duration test via testing button

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

Can be optionally switched off with reminder of due duration test after 12 months.

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

(according to DIN VDE 0100-718)

- Blocking function via CGLine monitoring facility during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux with mains operation:		310 lm

Luminous flux (E/(N

at the end of the rated service time:		100% at 1 h, 55% at 3 h, 20% at 8 h

Battery						LiIon 3.7V 4000mAh

Housing material: 				PC, PMMA, aluminium

Housing colour: 				White, similar to RAL9010

Connection terminals:				Through-wiring from mains L, L’, N, PE to 2.5 mm²

CGLine bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V, 50 Hz

Connected load with mains operation:		6.9 VA / 6.7 W

Insulation class: 				II

Protection rating: 				Luminaire IP 41; Module housing IP 20

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions (mm):				L = 100, W = 100, H = 38

Housing for LED converter:

L = 340, W = 50, H = 46  (angular construction)

Dimensions of ceiling cut-out (mm):		L = 87, W = 87

3rd party certificate:				ENEC

Type: GuideLed  SL  13851 CGLine  Ceiling recessed with asymmetric optics for the illumination of ‘Points of emphasis’ acc. EN 1838

Manufacturer: CEAG