# eLLK 92018/18 CG-S 2/6-2

Pos. ...)  ... pcs.

Completely monitored explosion-protected light fittings with EVG for G 13 bi-pin fluorescent lamps 2 x 18 W.

With integrated CG-S module for connection to CEAG emergency lighting system with 20-digit address circuit. Single lamp operation during DC-power supply (emergency operation) acc. to EN 60079 and EN 61241.

EC-Type Examination Certificate BVS 09 ATEX E 034,

Marking acc. to 94/9/EG: Ex II2 G Ex de mb II T4, Ex II 2 D Ex tD A21 IP66 T80 °C

Enclosure made of reinforced polyester and protective bowl made of poly-carbonate. Double ended through wiring with EEx-e cable entries for double-ended cable connection.

Rated voltage:

AC: 220 - 254 V ± 10 %, 47 - 63 Hz

DC: 196 – 250 V ± 10 %

Permissible temperature: -20°C to + 50°C

Loop terminals:

L1, L2, L3, L, N, PE; max. 2 x 6 sqmm single wire per terminal

Lamp: Bi-pin fluorescent lamp 18 W (G13-IEC-60081-Bl. 22/20)

Cable entries:

2 x EEx e cable entries

2 x EEx e cable entries M25 x 1.5 for cable entries Ø 8 - 17 mm

Insulation class I; Degree of protection: IP 66 to EN 60529 (acc. IEC 60529)

Weight: approx. 4.6 kg

Rated current: DC 0.1 A

Power consumption: 44 VA

Dimensions (mm): L = 760, W = 188, H = 130

Type: eLLK 92018/18 CG-S 2/6-2,

Manufactured by: CEAG

# Attention: Lamp is not a part of delivery

# eLLK 92036/36 CG-S 2/6-2

Pos. ...)  ... pcs.

Completely monitored explosion-protected light fittings with EVG for G 13 bi-pin fluorescent lamps 2 x 36 W.

With integrated CG-S module for connection to CEAG emergency lighting system with 20-digit address circuit. Single lamp operation during DC-power supply (emergency operation) acc. to EN 50014 to 50020, 50028 and 60598.

EC-Type Examination Certificate BVS 09 ATEX E 034,

Marking acc. to 94/9/EG: Ex II2 G Ex de mb II T4, Ex II 2 D Ex tD A21 IP66 T80 °C

Enclosure made of reinforced polyester and protective bowl made of poly-carbonate. Double ended through wiring with EEx-e cable entries for double-ended cable connection.

Rated voltage:

AC: 220 - 254 V ± 10 %, 47 - 63 Hz

DC: 196 – 250 V ± 10 %

Permissible temperature:-20°C to + 50°C

Loop terminals: L1, L2, L3, L, N, PE; max. 2 x 6 sqmm single wire per terminal

Lamp: Bi-pin fluorescent lamp 36 W (G13-IEC-60081-Bl. 24/20)

Cable entries:

2 x EEx e cable entries

2 x EEx e cable entries M25 x 1.5 for cable entries Ø 8 - 17 mm

Insulation class I; Degree of protection IP 66 to EN 60529 (acc. IEC 60529)

Weight: approx. 6.7 kg

Rated current: DC 0.17 A

Power consumption: 81 VA

Dimensions (mm): L = 1360, W = 188, H = 130

Type: eLLK 92036/36 CG-S 2/6-2

Manufactured by: CEAG

Attention: Lamp is not a part of delivery

# eLLK 92058/58 CG-S 2/6-2

Pos. ...)  ... pcs.

Completely monitored explosion-protected light fittings with EVG for G 13 bi-pin fluorescent lamps 2 x 58 W.

With integrated CG-S module for connection to CEAG emergency lighting system with 20-digit address circuit. Single lamp operation during DC-power supply (emergency operation) acc. to EN 50014 to 50020, 50028 and 60598.

EC-Type Examination Certificate BVS 09 ATEX E 034,

Marking acc. to 94/9/EG: Ex II2 G Ex de mb II T4, Ex II 2 D Ex tD A21 IP66 T80 °C

Enclosure made of reinforced polyester and protective bowl made of poly-carbonate. Double ended through wiring with EEx-e cable entries for double-ended cable connection.

Rated voltage:

AC: 220 - 254 V ± 10 %, 47 - 63 Hz

DC: 196 – 250 V ± 10 %

Permissible temperature:-20°C to + 40°C

Loop terminals: L1, L2, L3, L, N, PE; max. 2 x 6 sqmm single wire per terminal

Lamp: Bi-pin fluorescent lamp 58 W (G13-IEC-60081-Bl. 21/22)

Cable entries:

2 x EEx e cable entries

2 x EEx e cable entries M25 x 1.5 for cable entries Ø 8 - 17 mm

Insulation class I;

Degree of protection IP 66 to EN 60529 (acc. IEC 60529)

Weight: approx. 8.0 kg

Rated current: DC 0.27 A

Power consumption: 124 VA

Dimensions (mm): L = 1660, W = 188, H = 130

Type: eLLK 92058/58 CG-S 2/6-2

Manufactured by: CEAG

Attention: Lamp is not a part of delivery