VL8-1 CGLine

Pos.    )		Pcs.

Self-monitoring self-contained single power supply for systems acc. to DIN EN 50172, DIN VDE 0100-718 und E DIN VDE 0108-100 for the installation into luminaires acc. to DIN EN 60598-1 and DIN EN 60598-2-22.

Suitable for separate operation or for connection to the central monitoring device CG-Controller CGLine 400.

If connected to the central monitoring device CG-Controller CGLine 400 a non-screened 2-core bus cable to the luminaire is also needed.

Standard version with:

- Test button with integrated 3-coloured LED indicator

- Test results with fault analysis (lamps, charging and battery circuit) as well as status displays (operation, function test, duration test) via multicolour LED

- automatic function test (weekly)

- automatic duration test (every 3 months)

- automatic charging monitoring

- deep discharge protection with restart inhibit

- automatic cut off in case of failures within the lamp circuit

- intelligent charge: integrated capacity control for optimized recharge in case of partial   
  discharge

- manual function test or duration test with test button

- Blocking function via CG-Controller CGLine 400

- 1 minute delay of normal mode after mains returns

Luminous flux depending on connected lamp power

Module is suitable for maintained or non-maintained mode.

Maintained mode with additional conventional ballast or electronic ballast. Maximum distance VL8 – EVG: 1m.

The switchover between mains and battery operation is carried out via a 5-pole switchover unit.

Suitable for following lamps:

T26: 36W / 58W ; TC-TEL: 32W / 42W ; TC-L: 36W / 40W / 55W ; TC-F: 36W

Emergency lighting rated operating time:

..... 1 h NC rechargeable battery 3.6 V/1.5 Ah

..... 3 h NC rechargeable battery 3.6 V/4.0 Ah

Permitted temperature range:

Battery: 0°C to + 40°C

Electronics: -10°C to +50°C

Housing:

Metal case.

Insulation class: I; Degree of protection: IP 40

Connection terminals: 1.5 sq. mm mains supply, 10 x 1.5 sq. mm lamp and electronic ballast connection

Supply voltage: 230V 50Hz

Dimensions (mm): L = 260. H = 31. W = 40

Type: VL 8-1 CGLine - ... Ah

Manufactured by: CEAG

VL8-2 CGLine

Pos.    )		Pcs.

Self-monitoring self-contained single power supply for systems acc. to DIN EN 50172, DIN VDE 0100-718 und E DIN VDE 0108-100 for the installation into luminaires acc. to DIN EN 60598-1 and DIN EN 60598-2-22.

Suitable for separate operation or for connection to the central monitoring device CG-Controller CGLine 400.

If connected to the central monitoring device CG-Controller CGLine 400 a non-screened 2-core bus cable to the luminaire is also needed.

Standard version with:

- Test button with integrated 3-coloured LED indicator

- Test results with fault analysis (lamps, charging and battery circuit) as well as status displays (operation, function test, duration test) via multicolour LED

- automatic function test (weekly)

- automatic duration test (every 3 months)

- automatic charging monitoring

- deep discharge protection with restart inhibit

- automatic cut off in case of failures within the lamp circuit

- intelligent charge: integrated capacity control for optimized recharge in case of partial   
  discharge

- manual function test or duration test with test button

- Blocking function via CG-Controller CGLine 400

- 1 minute delay of normal mode after mains returns

Luminous flux depending on connected lamp power

Module is suitable for maintained or non-maintained mode.

Maintained mode with additional conventional ballast or electronic ballast. Maximum distance VL8 – EVG: 1m.

The switchover between mains and battery operation is carried out via a 5-pole switchover unit.

Suitable for following lamps:

T26: 18W; TC-SEL: 11W; TC-DEL: 10W / 13W / 18W / 26W; TC-TEL: 13W / 18W / 26W;                 TC-F: 18W/24W; TC-L 18W / 24W

Emergency lighting rated operating time:

..... 1 h NC rechargeable battery 3.6 V/1.5 Ah

..... 3 h NC rechargeable battery 3.6 V/4.0 Ah

Permitted temperature range:

Battery: 0°C to + 40°C

Electronics: -10°C to +50°C

Housing:

Metal case.

Insulation class: I; Degree of protection: IP 40

Connection terminals: 1.5 sq. mm mains supply, 10 x 1.5 sq. mm lamp and electronic ballast connection

Supply voltage: 230V 50Hz

Dimensions (mm): L = 260. H = 31. W = 40

Type: VL 8-2 CGLine - ... Ah

Manufactured by: CEAG