GuideLed  11821 1-8h/D  CGLine+  for ceiling surface-mounting

Pos.    )		ea.

Self-monitoring LED self-contained escape sign luminaire for ceiling surface-mounting, according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-560 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CGLine+ Web-Controller (requires a non-shielded 2-core bus line).

Escape sign with LED Lightguide technology for especially homogeneous and

bright illumination of the pictogram acc. DIN 4844-1 and ISO 3864-1:

Lm >= 500 cd/m² (mains operation) for the white contrast colour and

Lm >= 200 cd/m² (mains operation) over the complete pictogram, uniformity Lmin/Lmax > 0.8.

LED-strip with high service life via optimised LED operating conditions and high luminous efficacy >100 lm/W for significantly reduced connected load. Easy connection via polarity reversal-protected wiring.

Slender design with low pictogram width of only 12mm and canopy with height of only 33mm.

Serial functionality:

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED

- Automatic function test (weekly) and automatic duration test (every 6 months)

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

- Blocking function via CGLine+ Web-Controller during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux (E/(N

at the end of the rated service time:		single-sided: 100% at 1 h, 50% at 3 h, 15% at 8h

double-sided: 85% at 1 h, 25% at 3 h, 8% at 8h

Battery						LiIon 3.7V 2000 mAh

Viewing distance: 				30 m

Housing material: 				PC, PMMA

Housing colour: 				light grey RAL 7035

Connection terminals:				Through-wiring from mains L, L’, N, PE to 2.5 mm²

CGLine+ bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V AC, 50/60 Hz

Connected load with mains operation:		single-sided 5.3 VA / 4.7 W

double-sided 6.6 VA / 6.3 W

Insulation class: 				II (protective earth required)

Protection rating: 				IP 40

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 327, H = 184, D = 12

Dimensions of ceiling mounting set (mm):	W = 327, H = 33, D = 80

3rd party certificate:				ENEC

Type: GuideLed 11821 1-8h/D CGLine+ for ceiling surface-mounting

Manufacturer: CEAG

GuideLed 11822 1-8h/D CGLine+ for suspended mounting, 0.5 m

Pos.    )		ea.

Self-monitoring LED self-contained escape sign luminaire for suspended mounting (0.5m), according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-560 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CGLine+ Web-Controller (requires a non-shielded 2-core bus line).

Escape sign with LED Lightguide technology for especially homogeneous and

bright illumination of the pictogram acc. DIN 4844-1 and ISO 3864-1:

Lm >= 500 cd/m² (mains operation) for the white contrast colour and

Lm >= 200 cd/m² (mains operation) over the complete pictogram, uniformity Lmin/Lmax > 0.8.

LED-strip with high service life via optimised LED operating conditions and high luminous efficacy >100 lm/W for significantly reduced connected load. Easy connection via polarity reversal-protected wiring.

Slender design with low pictogram width of only 12mm and canopy with height of only 33mm.

Serial functionality:

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED

- Automatic function test (weekly) and automatic duration test (every 6 months)

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

- Blocking function via CGLine+ Web-Controller during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux (E/(N

at the end of the rated service time:		single-sided: 100% at 1 h, 50% at 3 h, 15% at 8h

double-sided: 85% at 1 h, 25% at 3 h, 8% at 8h

Battery						LiIon 3.7V 2000 mAh

Viewing distance: 				30 m

Housing material: 				PC, PMMA

Housing colour: 				light grey RAL 7035

Connection terminals:				Through-wiring from mains L, L’, N, PE to 2.5 mm²

CGLine+ bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V AC, 50/60 Hz

Connected load with mains operation:		single-sided 5.3 VA / 4.7 W

double-sided 6.6 VA / 6.3 W

Insulation class: 				II (protective earth required)

Protection rating: 				IP 40

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 327, H = 184, D = 12

Dimensions of ceiling mounting set (mm): 	W = 327, H = 33, D = 80

3rd party certificate:				ENEC

Type: GuideLed 11822 1-8h/D CGLine+ for suspended mounting, 0.5 m

Manufacturer: CEAG

GuideLed 11823 1-8h/D CGLine+ for suspended mounting, 1.5 m

Pos.    )		ea.

Self-monitoring LED self-contained escape sign luminaire for suspended mounting (1.5 m), according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-560 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CGLine+ Web-Controller (requires a non-shielded 2-core bus line).

Escape sign with LED Lightguide technology for especially homogeneous and

bright illumination of the pictogram acc. DIN 4844-1 and ISO 3864-1:

Lm >= 500 cd/m² (mains operation) for the white contrast colour and

Lm >= 200 cd/m² (mains operation) over the complete pictogram, uniformity Lmin/Lmax > 0.8.

LED-strip with high service life via optimised LED operating conditions and high luminous efficacy >100 lm/W for significantly reduced connected load. Easy connection via polarity reversal-protected wiring.

Slender design with low pictogram width of only 12mm and canopy with height of only 33mm.

Serial functionality:

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED

- Automatic function test (weekly) and automatic duration test (every 6 months)

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

- Blocking function via CGLine+ Web-Controller during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux (E/(N

at the end of the rated service time:		single-sided: 100% at 1 h, 50% at 3 h, 15% at 8h

double-sided: 85% at 1 h, 25% at 3 h, 8% at 8h

Battery						LiIon 3.7V 2000 mAh

Viewing distance: 				30 m

Housing material: 				PC, PMMA

Housing colour: 				light grey RAL 7035

Connection terminals:				Through-wiring from mains L, L’, N, PE to 2.5 mm²

CGLine+ bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V AC, 50/60 Hz

Connected load with mains operation:		single-sided 5.3 VA / 4.7 W

double-sided 6.6 VA / 6.3 W

Insulation class: 				II (protective earth required)

Protection rating: 				IP 40

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 327, H = 184, D = 12

Dimensions of ceiling mounting set (mm): 	W = 327, H = 33, D = 80

3rd party certificate:				ENEC

Type: GuideLed 11823 1-8h/D CGLine+ for suspended mounting, 1.5 m

Manufacturer: CEAG

GuideLed 11824 1-8h/D CGLine+ for ceiling recessing

Pos.    )		ea.

Self-monitoring LED self-contained escape sign luminaire for ceiling recessing, according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-560 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CGLine+ Web-Controller (requires a non-shielded 2-core bus line).

Escape sign with LED Lightguide technology for especially homogeneous and

bright illumination of the pictogram acc. DIN 4844-1 and ISO 3864-1:

Lm >= 500 cd/m² (mains operation) for the white contrast colour and

Lm >= 200 cd/m² (mains operation) over the complete pictogram; uniformity Lmin/Lmax > 0.8.

LED-strip with high service life via optimised LED operating conditions and high luminous efficacy >100 lm/W for significantly reduced connected load. Easy connection via polarity reversal-protected wiring.

Slender design with low pictogram width of only 12mm and only 55mm recess depth.

Ceiling recessing housing of sheet steel with steplessly adjustable fixing clips, clamping range 1 to 25 mm.

Serial functionality:

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED

- Automatic function test (weekly) and automatic duration test (every 6 months)

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

- Blocking function via CGLine+ Web-Controller during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux (E/(N

at the end of the rated service time:		single-sided: 100% at 1 h, 50% at 3 h, 15% at 8h

double-sided: 85% at 1 h, 25% at 3 h, 8% at 8h

Battery						LiIon 3.7V 2000 mAh

Viewing distance: 				30 m

Housing material: 				PC, PMMA, sheet steel

Housing colour: 				light grey RAL 7035

Connection terminals:				Through-wiring from mains L, L’, N, PE to 2.5 mm²

CGLine+ bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V AC, 50/60 Hz

Connected load with mains operation:		single-sided 5.3 VA / 4.7 W

double-sided 6.6 VA / 6.3 W

Insulation class: 				I

Protection rating: 				IP 40

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 327, H = 184, D = 12

Dimensions of recess housing (mm):  		W = 374, H = 65, D = 92 (recess depth 61 mm)

Ceiling cut-out (365 mm x 78 mm)

3rd party certificate:				ENEC

Type: GuideLed 11824 1-8h/D CGLine+ for ceiling recessing

Manufacturer: CEAG