GuideLed SL 13812 1-8h/D CGLine+ Ceiling surface-mounting with asymmetric optics for escape route illumination

Pos.    )		ea.

Self-monitoring LED self-contained safety luminaire for ceiling surface-mounting with asymmetric optics according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-560 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CGLine+ Web-Controller (requires a non-shielded 2-core bus line).

Asymmetric optics for especially efficient escape route illumination.

Light control via twin lens technology combined with reflectivity-enhanced reflectors integrated in the luminaire. Light source: 2 x high efficiency High Power LEDs, white, 1.6 W, with 50,000 h service life due to optimised LED operating conditions.

Housing on ceiling side of diecast aluminium for optimised thermal dissipation. Visible housing of white polycarbonate (RAL 9010) and clear cover panel. Cable entry is possible on ceiling side or laterally for mains and bus line, with additional space for cable routing.

Serial functionality:

- Manual function test or duration test via testing button

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED

- Automatic function test (weekly) and automatic duration test (every 6 months)

Can be optionally switched off with reminder of due duration test after 12 months

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

- Blocking function via CGLine+ Web-Controller during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux with mains operation:		210 lm

Luminous flux (E/(N

at the end of rated operating time: 		100% at 1 h, 65% at 3 h, 25% at 8 h

Battery						LiIon 3.7V / 4000 mAh

Housing material: 				PC, PMMA, aluminium

Housing colour: 				White, similar to RAL9010

Connection terminals:				Through-wiring from mains L, L’, N, PE to 2.5 mm²

CGLine+ bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V, 50/60 Hz

Connected load with mains operation:		6.9 VA / 6.7 W

Insulation class: 				I

Protection rating: 				Luminaire IP 41

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions (mm):				L = 195, W = 195, H = 40

3rd party certificate:				ENEC

Type: GuideLed SL 13812 CGLine+ Ceiling surface-mounting with asymmetric light distribution

Manufacturer: CEAG

GuideLed SL 13822 1-8h/D CGLine+ Ceiling surface-mounting with symmetric optics for wide area illumination

Pos.    )		ea.

Self-monitoring LED self-contained safety luminaire for ceiling surface-mounting with symmetric optics according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-560 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CGLine+ Web-Controller (requires a non-shielded 2-core bus line).

Symmetric optics for homogeneous, wide area illumination.

Light control via twin lens technology combined with reflectivity-enhanced reflectors integrated in the luminaire. Light source: 2 x high efficiency High Power LEDs, white, 1.6 W, with 50,000 h service life due to optimised LED operating conditions.

Housing on ceiling side of diecast aluminium for optimised thermal dissipation. Visible housing of white polycarbonate (RAL 9010) and clear cover panel. Cable entry is possible on ceiling side or laterally for mains and bus line, with additional space for cable routing.

Serial functionality:

- Manual function test or duration test via testing button

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED

- Automatic function test (weekly) and automatic duration test (every 6 months)

Can be optionally switched off with reminder of due duration test after 12 months

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

- Blocking function via CGLine+ Web-Controller during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux with mains operation:		204 lm

Luminous flux (E/(N

at the end of rated operating time: 		100% at 1 h, 65% at 3 h, 25% at 8 h

Battery						LiIon 3.7V / 4000 mAh

Housing material: 				PC, PMMA, aluminium

Housing colour: 				White, similar to RAL9010

Connection terminals:				Through-wiring from mains L, L’, N, PE to 2.5 mm²

CGLine+ bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V, 50/60 Hz

Connected load with mains operation:		6.9 VA / 6.7 W

Insulation class: 				I

Protection rating: 				Luminaire IP 41

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions (mm):				L = 195, W = 195, H = 40

3rd party certificate:				ENEC

Type: GuideLed SL 13822 CGLine+ Ceiling surface-mounting with symmetric light distribution

Manufacturer: CEAG