Outdoor Wall CGLine+

Pos)            ea.

Self-monitoring LED self-contained safety luminaire with high protection class (IP65) for wall mounting for indoor applications, according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-560 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CGLine+ Web-Controller (requires a non-shielded 2-core bus line).

Robust design (IK10) made of die-cast aluminium housing and impact resistant cover made of clear polycarbonate. Suitable for operational areas with fire hazard (D mark).

Light direction by double optics technology.  Light direction by double optics technology tilted for optimal illumination along the wall.

Light source: 2 x highly efficient, white high-power LEDs 1.6 W, with a service life of 50,000 h on account of optimised LED operating conditions.

Serial functionality:

- Manual function test or duration test started with a magnet

- Emergency light operating duration settable via dip switch

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

Can be optionally switched off with reminder of due duration test after 12 months.

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

- Blocking function via CGLine+ Web-Controller during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux with mains operation:		225 lm

Luminous flux (E/(N

at the end of rated operating time: 		100% at 1 h, 65% at 3 h, 25% at 8 h

Battery						LiIon 3.7V / 4000 mAh

Housing material: 				PC, aluminium

Housing colour: 				Grey

Connection terminals:				Through-wiring from mains L, L’, N, PE to 2.5 mm²

CGLine+  bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V, 50/60 Hz

Connected load with mains operation:		7.2 VA / 7.0 W

Insulation class: 				I

Protection rating: 				IP65

Additional marking:				D mark

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions (mm):				L = 303, W = 136, H = 62

3rd party certificate:				ENEC

Type: Outdoor Wall 1-8h/D CGLine+

Manufacturer: CEAG

Outdoor Wall CGLine+ H

Pos)            ea.

Self-monitoring LED self-contained safety luminaire with high protection class (IP65) for ceiling mounting according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-560 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CGLine+ Web-Controller (requires a non-shielded 2-core bus line).

Robust design (IK10) made of die-cast aluminium housing and impact resistant cover made of clear polycarbonate. Suitable for operational areas with fire hazard (D mark).

Self-regulating battery heater for use at low ambient temperature up to -20°C.

Light direction by double optics technology.  Light direction by double optics technology tilted for optimal illumination along the wall.

Light source: 2 x highly efficient, white high-power LEDs 1.6 W, with a service life of 50,000 h on account of optimised LED operating conditions.

Serial functionality:

- Manual function test or duration test started with a magnet

- Emergency light operating duration settable via dip switch

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

Can be optionally switched off with reminder of due duration test after 12 months.

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

- Blocking function via CGLine+ Web-Controller during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux with mains operation:		225 lm

Luminous flux (E/(N

at the end of rated operating time: 		100% at 1 h, 65% at 3 h, 25% at 8 h

Battery						LiIon 3.7V / 4000 mAh

Housing material: 				PC, aluminium

Housing colour: 				Grey

Connection terminals:				Through-wiring from mains L, L’, N, PE to 2.5 mm²

CGLine+  bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V, 50/60 Hz

Connected load with mains operation:		9.4 VA / 9.3 W battery heater on

7.2 VA / 7.0 W battery heater off

Insulation class: 				I

Protection rating: 				IP65

Additional marking:				D mark

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions (mm):				L = 303, W = 136, H = 62

3rd party certificate:				ENEC

Type: Outdoor Wall 1-8h/D CGLine+ H

Manufacturer: CEAG