本文档下载自文档下载网，内容可能不完整，您可以点击以下网址继续阅读或下载：

http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3

ATPDManul5.6版的学习手册

ATP5.6版的学习手册

5.6

[此处图片未下载成功]

' Manual

&#225;szl&#243; Prikler,

Kristian H&#248;idalen

permission from the authors.

Release No. 1.0 November 2009

version 5.6

[此处图片未下载成功]

1

Users' Manual documents all main features of ATPDraw version 5.6. The manual is an extensive update of the previous User Manual prepared by L&#225;szl&#243; Prikler at SYSTRAN Engineering Services Ltd. in Budapest for version 3.5 (SINTEF TR F5680) dated 2002. Version 5.6 is substantially updated compared to version 3.5; New design, new and extended components, new handling of Models, Hybrid Transformer, multi-phase nodes, vector graphics, Output Manager, Line Check, Circuit Texts, Optimization etc.. The Reference Manual gives a summary of menu items and menu options. The Advanced Manual covers the feathttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ures Grouping, Models, electrical machine, line/cable-, and transformer modeling, and optimization. Finally the Application Manual is extended with several examples. New ATPDraw users are advised to start with the Installation and Introductory manuals.

is developed by NTNU and SINTEF Energy Research. Program and development have been financed by Bonneville Power Administration, USA, version 5 in co-operation with EEUG and Schneider Electric, France.

Norwegian University of Technology Trondheim, Norway, November 26th 2009.

Kr. H&#248;idalen

NTNU-Norway

is a graphical, mouse-driven preprocessor to the ATP version of the Electromagnetic Transients Program (EMTP) on the MS-Windows platform. The program is written in CodeGear Delphi 2007 and runs under Windows 9x/NT/2000/XP/Vista. In ATPDraw the user can construct an electrical circuit using thhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3e mouse and selecting components from menus, then ATPDraw generates the ATP input file in the appropriate format based on &quot;what you see is what you get&quot;. The simulation program ATP and plotting programs can be integrated with ATPDraw.

supports multiple circuit modeling that makes possible to work on more circuits simultaneously and copy information between the circuits. All kinds of standard circuit editing facilities (copy/paste, grouping, rotate, export/import, undo/redo) are available. In addition, ATPDraw supports the Windows clipboard and metafile export. The circuit is stored on disk in a single project file, which includes all the simulation objects and options needed to run the case. The project file is in zip-compressed format that makes the file sharing with others very simple.

of the standard components of ATP as well as TACS are supported, and in addition the user can create new objehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3cts based on MODELS or $Include (Data Base Module). Line/Cable modeling (KCLee, PI-equivalent, Semlyen, JMarti and Noda) is also included in ATPDraw where the user specifies the geometry and material data and has the option to view the cross section graphically and verify the model in the frequency domain. Special components support the user in machine and transformer modeling based on the powerful Universal Machine and BCTRAN components in ATP-EMTP. In addition the advanced Hybrid Transformer model XFMR and Windsyn support is included.

supports hierarchical modeling by replacing selected group of objects with a single icon in an almost unlimited numbers of layers. Components have an individual icon in either bitmap or vector graphic style and an optional graphic background. ATPDraw supports up to 10.000 components each with maximum 64 data and 32 nodes.

version 5.6

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ge TABLE OF CONTENTS

.  Introduction . . .......................................................................................................................7

.1 What is ATPDraw?..............................................................................................................9

.2 What is ATP?.....................................................................................................................10

.3 Operating priciples and capabilities of ATP......................................................................10

.3.1 Integrated simulation modules in ATP........................................................................11

.3.2 Program capabilities....................................................................................................12

.3.3 Main characteristics of plotting programs for ATP............................................http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3........13

.3.4 Typical EMTP applications.........................................................................................15

.3.5 Hardware requirements for ATP.................................................................................15

.4 Contents of this manual.....................................................................................................15

.5 Manual conventions...........................................................................................................16

.  Installation Manual . . ..........................................................................................................17

.1 ATP licencing policy.........................................................................................................19

.2 How to download ATPDraw?...................................................................................http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3.........19

.3 Hardware requirements for ATPDraw...............................................................................20

.4 Program installation...........................................................................................................20

.5 Files and sub-folders in the ATPDraw system folder........................................................21

.5.1 Organizing the files.....................................................................................................22

.5.2 Configuring ATPDraw................................................................................................22

.6 Interfacing ATPDraw with other programs of the ATP-EMTP package..........................22

.6.1 Calling Watcom ATP and GNU MingW32 ATP from ATPDraw..............................24

.6.2 Calling PlotXY , PCPlot or ATP_Analyzer..........................http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3......................................25

.6.3 ATPDraw command line options................................................................................25

.6.4 Drag and drop project files..........................................................................................25

.7 How to get help?................................................................................................................25

.7.1 Help from the author of ATPDraw..............................................................................26

.7.2 Help via electronic mail..............................................................................................26

.7.3 Help via the ATP-EMTP-L mailing list......................................................................26

.8 Available circuit objects in ATPDraw.............................................................................http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3..27

.  Introductory Manual . . ........................................................................................................29

.1 Operating windows............................................................................................................31

.2 Operating the mouse..........................................................................................................34

.3 Edit operations...................................................................................................................35

.4 Overview of working with ATPDraw................................................................................35

.5 Your first circuit (Exa_1.adp)............................................................................................37

.5.1 Building the circuit.................................................................................http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3.....................38

.5.2 Storing the project file on disk....................................................................................48

.5.3 Creating the ATP input file.........................................................................................48

.5.4 Running the simulation...............................................................................................50

.6 Multi-phase phase circuits.................................................................................................50

. Reference Manual . . ............................................................................................................55

.1 Main window.....................................................................................................................57

.2 Main menu...................................................................................http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3......................................58

.2.1 File...............................................................................................................................58

version 5.6  3

.2.2 Edit..............................................................................................................................60

.2.3 View............................................................................................................................65

.2.4 Zoom In.......................................................................................................................67

.2.5 ATP.............................................................................................................................69

.2.6 Library........................................................................................................................82http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3

.2.7 Tools...........................................................................................................................88

.2.8 Window.......................................................................................................................95

.2.9 Help.............................................................................................................................96

.3 Shortcut menu....................................................................................................................97

.4 Component selection menu...............................................................................................98

.5 Component dialog box......................................................................................................99

.6 Connection dialog box......................................................................http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3...............................102

.7 Text dialog box................................................................................................................103

.8 Node dialog box..............................................................................................................103

.9 Open Probe dialog box....................................................................................................105

.10 Open Group dialog box................................................................................................105

.11 Circuit objects in ATPDraw.........................................................................................106

.11.1 Probes &amp; 3-phase...................................................................................................108

.11.2 Branch Linear................................................................http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3........................................110

.11.3 Branch Nonlinear...................................................................................................111

.11.4 Lines/Cables..........................................................................................................112

.11.5 Switches.................................................................................................................115

.11.6 Sources..................................................................................................................116

.11.7 Machines................................................................................................................117

.11.8 Transformers..........................................................................................................118

.11.9 MODELS............................................................http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3...................................................120

.11.10 TACS.....................................................................................................................124

.11.11 User Specified.......................................................................................................129

.11.12 Steady-state............................................................................................................130

.11.13 Standard Component.............................................................................................131

.11.14 Plugins...................................................................................................................132

.  Advanced Manual . . .........................................................................................................133

.1 Grouping: an ATPDraw feature for multilevel modeling.http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3..............................................135

.1.1 Grouping nonlinear objects.......................................................................................140

.2 Non-standard component dialog boxes...........................................................................142

.2.1 Saturable 3-phase transformer..................................................................................142

.2.2 Universal machines...................................................................................................144

.2.3 Statistic/systematic switch........................................................................................148

.2.4 Harmonic source.......................................................................................................149

.2.5 Windsyn component.................................................................................http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3................150

.3 Using the integrated LCC object for line/cable modeling...............................................152

.3.1 Model and Data page settings for Overhead Lines...................................................155

.3.2 Model and Data page settings for Single Core Cable systems.................................158

.3.3 Model and Data page settings for Enclosing Pipe type cables.................................160

.4 Verification of the Line/Cable model performance.........................................................162

.4.1 Internal Line/Cable Verify........................................................................................162

.4.2 External Line Check.................................................................................................165

.5 Using MODELS simulation language.................................................http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3............................166

version 5.6

.5.1 The automatic approach............................................................................................167

.5.2 The manual approach................................................................................................169

.5.3 Recording internal MODELS variables....................................................................172

.6 BCTRAN support in ATPDraw.......................................................................................173

.7 Hybrid Transformer, XFMR............................................................................................177

.7.1 Overview...................................................................................................................177

.7.2 XFMR dialog box...........................................................http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3...........................................178

.8 Creating new circuit objects in ATPDraw.......................................................................181

.8.1 Creating a 6-phase rectifier bridge............................................................................181

.8.2 Creating a user specified, nonlinear transformer model...........................................187

.9 Vector graphic editor.......................................................................................................190

.9.1 Properties...................................................................................................................192

.9.2 Editing: Selecting, moving, resizing and clipboard..................................................193

.9.3 Drawing new elements..............................................................................................194://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3r

.9.4 Layers and visible......................................................................................................194

.9.5 Example of complex icons........................................................................................195

.10 Bitmap background.......................................................................................................195

.11 Optimization.................................................................................................................196

.11.1 Optimization routines.............................................................................................197

.11.2 Cost function..........................................................................................................197

.11.3 Optimization dialog...............................................................................................198://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3

.11.4 Example: Resonance grounding (Exa_18.acp)......................................................199

.  Application Manual . . .......................................................................................................201

.1 Switching studies using JMarti LCC objects...................................................................203

.1.1 JMarti model of a 750 kV line..................................................................................203

.1.2 Line to ground fault and fault tripping transients (Exa_7a.adp)...............................205

.2 Lightning overvoltage study in a 400 kV substation (Exa_9.adp)..................................208

.3 Modeling Rectifiers, zigzag transformers and analysis of Harmonics (Exa_14.adp).....214

.4 Modelling of electrical machines and controls................................................................2http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db320

.4.1 TACS controlled induction machine (Exa_4.adp)....................................................220

.4.2 Windsyn machine model...........................................................................................224

.4.3 Machine control (Exa_17.acp)..................................................................................225

.5 Simulating transformer inrush current transients.............................................................231

.5.1 Energization of a 400/132/18 kV auto-transformer (Exa_10.adp)............................231

.5.2 Energization of a 132/15 kV generator step-up transformer (Exa_11.adp)..............237

.5.3 Using the Hybrid Transformer component  (Exa_16.acp)........................................241

.6 Switching overvoltage studies with statistical approach (Exa_12.adp)..........................243

.6.1 Setting prhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ogram options for the statistical simulation...............................................243

.6.2 Results of the statistical study...................................................................................244

.  Appendix . . . . . . . . . . .......................................................................................................247

.1 PFC simulations in ATPDraw..........................................................................................249

.2 Line Check.......................................................................................................................252

.2.1 Single phase systems.................................................................................................253

.2.2 3-phase systems.........................................................................................................256

.3 Hybrid Transfohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3rmer, XFMR............................................................................................257

.3.1 Leakage inductance...................................................................................................258

.3.2 Winding resistance....................................................................................................259

.3.3 Capacitance...............................................................................................................260

version 5.6           5

.3.4 Core...........................................................................................................................261

.4 References.......................................................................................................................265

.5 Index...............................................................................http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3.................................................266

version 5.6

[此处图片未下载成功]

ATPDraw version 5.6   7

.1 What is ATPDraw?

for Windows is a graphical, mouse-driven preprocessor to the ATP version of the Electromagnetic Transients Program (EMTP). In ATPDraw the user can construct the digital model of the circuit to be simulated using the mouse and selecting predefined components from an extensive palette, interactively. Then ATPDraw generates the input file for the ATP simulation in the appropriate format based on &quot;what you see is what you get&quot;. Circuit node naming is administrated by ATPDraw, thus the user needs to give a name only to nodes having special interest.

has a standard Windows layout and offers a large Windows help file system. All kinds of standard circuit editing facilities (cophttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3y/paste, grouping, rotate/flip, export/import, undo/redo) are available. Other facilities in ATPDraw are: built-in editor for ATP-file editing, text viewer for displaying the output LIS-file of ATP, automatic LIS-file checking with special trigger strings to detect simulation errors, support of Windows clipboard and metafile export. ATPDraw supports multiple circuit modeling that makes possible to work on more circuits simultaneously and copy information between the circuits.

of the standard components of ATP (both single and 3-phase), as well as TACS are supported, and in addition the user can create new objects based on MODELS or $INCLUDE (Data Base Module). Line/Cable modeling (KCLee, PI-equivalent, Semlyen, JMarti and Noda) is also included in ATPDraw where the user specifies the geometry and material data and has the option to view the cross section graphically and verify the model in the frequency domain.http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 Objects for Harmonic Frequency Scan (HFS) have also been added. Special objects help the user in machine and transformer modeling including the powerful UNIVERSAL MACHINE and BCTRAN features of ATP. An advanced Hybrid Transformer model based on Test Report, Design or Typical values with topologically correct core is also supported. ATPDraw also integrated with Windsyn for Universal Machine modeling based on manufacturers data.

supports hierarchical modeling to replace a selected group of objects with a single icon in unlimited numbers of layers. $PARAMETER feature of ATP is also implemented, allowing the user to specify a text string as input in a components' data field, then assign numerical values to these texts strings later. The circuit is stored on disk in a single project file, which includes all the simulation objects and options needed to run the case. The project file is in zip-compressed format thhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3at makes the file sharing with others very simple.

is most valuable to new users of ATP-EMTP and is an excellent tool for educational purposes. However, the possibility of multi-layer modeling makes ATPDraw a powerful front-end processor for professionals in analysis of electric power system transients, as well.

3.6 and above of ATPDraw for 9x/NTx/2000/XP Windows platforms are written in Borland Delphi 6.0. From version 5.3 CodeGear Delphi 2007 is used. This version uses the html help file system supported in Windows VISTA.

is a trademark and copyrighted by &#169; 2005-2009 Norwegian University of Science and Technology, Norway. Program developer is Dr. Hans Kristian H&#248;idalen in Trondheim, Norway, with Dahl Data Design in Norway as a programming sub-contractor and SYSTRAN Engineering Services in Hungary as a sub-contractor for program documentation. Progrhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3am development has mainly been financed by Bonneville Power Administration in Portland, Oregon,

version 5.6  9

, with Pacific Engineering Corporation as project coordinator. Development in version 5 has in addition been co-funded by the European EMTP User's Group and Schneider Electric.

ATPDraw program is royalty free and can be downloaded free of charge from several Internet sites. The on-line help of ATPDraw and the present program documentation includes third-party proprietary information of, thus ATP licensing is mandatory prior to get permission to download the program and documentation from the Internet, or to receive ATP related materials from others.

.2 What is ATP?

Alternative Transients Program (ATP) is considered to be one of the most widely used universal program system for digital simulation of transient phenomena of electromaghttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3netic as well as electromechanical nature in electric power systems. With this digital program, complex networks and control systems of arbitrary structure can be simulated. ATP has extensive modeling capabilities and additional important features besides the computation of transients.

Electromagnetic Transients Program (EMTP) was developed in the public domain at the Bonneville Power Administration (BPA) of Portland, Oregon prior to the commercial initiative in 1984 by the EMTP Development Coordination Group and the Electric Power Research Institute (EPRI) of Palo Alto, California. The birth of ATP dates to early in 1984, when Drs. Meyer and Liu did not approve of proposed commercialization of BPA's EMTP and Dr. Meyer, using his own personal time, started a new program from a copy of BPA's public-domain EMTP. Since then the ATP program has been continuously developed through international contributions by Drs. http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3W. Scott Meyer and Tsu-huei Liu, the co-Chairmen of the Canadian/American EMTP User Group. Several experts around the world have been contributing to EMTP starting in 1975 and later to ATP in close cooperation with program developers in Portland, USA.

BPA work on EMTP remains in the public domain by U.S. law, ATP is not in the public domain and licensing is required before access to proprietary materials is granted. Licensing is, however, available free of all charge to anyone in the world who has not participated voluntarily in the sale or attempted sale of any electromagnetic transients program, (hereafter called &quot;EMTP commerce&quot;).

.3 Operating priciples and capabilities of ATP1

ATP program predicts variables of interest within electric power networks as functions of time, typically initiated by some disturbances. Basically, trapezoidal rule of integration is used to solve the dhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ifferential equations of system components in the time domain. Non-zero initial conditions can be determined either automatically by a steady-state phasor solution or they can be entered by the user for simpler components.

has many models including rotating machines, transformers, surge arresters, transmission lines and cables. Interfacing capability to the program modules TACS (Transient Analysis of Control Systems) and MODELS (a simulation language) enables modeling of control systems and components with nonlinear characteristics such as arcs and corona. Dynamic systems without any electrical network can also be simulated using TACS and MODELS control system modeling.  1               Source: http://www.wendangwang.com

version 5.6

or unsymmetrical disturbances are allowed, such as faults, lightning surges and several kind of swithttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ching operations including commutation of valves. Frequency-domain harmonic analysis using harmonic current injection method (HARMONIC FREQUENCY SCAN) and calculation of the frequency response of phasor networks using FREQUENCY SCAN feature is also supported. The model-library of ATP at present consists of the following components:

Uncoupled and coupled linear, lumped R,L,C elements. Transmission lines and cables with distributed and frequency-dependent parameters. Nonlinear resistances and inductances, hysteretic inductor, time-varying resistance, TACS/MODELS controlled resistance. Components with nonlinearities: transformers including saturation and hysteresis, surge arresters (gapless and with gap), arcs. Ordinary switches, time-dependent and voltage-dependent switches, statistical switching (Monte-Carlo studies). Valves (diodes, thyristors, triachttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3s), TACS/MODELS controlled switches. Analytical sources: step, ramp, sinusoidal, exponential surge functions, TACS/MODELS defined sources.  Rotating machines: 3-phase synchronous machine, universal machine model. User-defined electrical components that include MODELS interaction

.3.1 Integrated simulation modules in ATP

in ATP is a general-purpose description language supported by an extensive set of simulation tools for the representation and study of time-variant systems.

description of each model is enabled using free-format, keyword-driven syntax of

context and that is largely self-documenting.

MODELS in ATP allows the description of arbitrary user-defined control and circuit components, providing a simple interface for connecting other programs/models to ATP.     As a general-purpose programmable tool, MODELS can be used for processing simulation results either ihttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3n the frequency domain or in the time domain.

is a simulation module for time-domain analysis of control systems. It was originally developed for the simulation of HVDC converter controls. For TACS, a block diagram representation of control systems is used. TACS can be used for the simulation of

HVDC converter controls

Excitation systems of synchronous machines

power electronics and drives

electric arcs (circuit breaker and fault arcs).

between electrical network and TACS is established by exchange of signals such as node voltage, switch current, switch status, time-varying resistance, voltage- and current sources.

routines are integrated utilities inside the program that support the users in conversion between manufacturers' data format and the one required by the program, or to calculate electrical parameters of lines and cables from geomethttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3rical and material data. Supporting modules in ATP are:

Calculation of electrical parameters of overhead lines and cables using program modules LINE CONSTANTS, CABLE CONSTANTS and CABLE PARAMETERS.

ATPDraw version 5.6

Introduction

[此处图片未下载成功]

Generation of frequency-dependent line model input data (Semlyen, J.Marti, Noda line models). Calculation of model data for transformers (XFORMER, BCTRAN). Saturation and hysteresis curve conversion. Data Base Modularization (for $INCLUDE usage).

.  1.1 - Supporting routines in ATP.

: http://www.wendangwang.com

.3.2 Program capabilities

-EMTP tables are dimensioned dynamically at the start of execution to satisfy the needs of users and their hardware (e.g., RAM). No absolute limits have ever been observed, and the standard version has limits that avehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3rage more than 20 times default table sizes. Today, the largest simulations are being performed using Intel-based PC's. The following table shows maximum limits for standard program distribution. Busses 6000Sources 900

10000Nonlinear elements 2250

1200Synchronous machines  90

version 5.6

Introduction

.3.3 Main characteristics of plotting programs for ATP

post-processors are interfaced with ATP via disk files and their main function is to display the results of a time- or frequency domain simulation. ATP simulation data are stored in a file having extension .pl4, and it can be processed either off-line, or on-line. The latter (i.e. to display results while the simulation proceeds) is available only if the operating system provides concurrent PL4-file access for ATP and the postprocessor program.

.  1.2 – Plotthttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ing programs for ATP.

Analyzer is a Windows based program intended for observing and analyzing analog signals and discrete channel data associated power generation, transmission and distribution systems. The programis capable of reading and displaying analog signals produced by ATP as type PL4 output file data, industry standard COMTRADE file and analog and digital data produced from protective relays and fault recorder equipment, analog signals from table ASCII text data, and audio wave files. A total of 254 signals can be managed.

can be displayed in time domain in multiple overlay charts. One or more signals can be displayed as a function of another on an X versus Y chart. Up to three signals can be displayed simultaneously in the frequency domain as harmonics or as a broad frequency spectrum. Charts may be printed and copied to the Windows clipborard.

program can process the data fohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3r harmonic content and store processed data in a Windows Access Data base.

is a plotting program for processing PL4 output of ATP. It is compiled with the GNU FORTRAN, and makes use of the graphical package DISLIN. The program is available for DOS-djgpp extender, Windows 32, and Linux. GTPPLOT can read widenn, formatted PL4-files (FMTPL4 = 10Fnn.), C-like binary files, unformatted files, COMTRADE and ASCII data files. GTPPLOT is able to process graphics files with up to 1000000 points and up to 1000 variables. The program can plot up to 20 curves end export the graphics in nine different formats: HP-GL, CGM, WMF, PCX, PostScript, PNG, WMF, JAVA and GNUPLOT. For FS and HFS runs the plot can be bar charts. The data can be exported as widenn PL4, COMTRADE, Matlab, MathCad and Mathematica files. Furthermore, the program calculates lot of Power Quality Indexes from data, can be used for FOURIER analysis, turbine http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3shaft loss of life estimation. Various simple math operations with variables, as integration, derivation, RMS, power, energy, I2T are also supported. GTPPLOT can be used to generate KIZILCAY F-DEPENDENT elements from

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

version 5.6  13

Introduction

SCAN PL4 output, as well. GTPPLOT has no graphical interface, the user must use the keyboard for all the input commands.

is a WIN32 plotting program originally designed for ATP-EMTP. The program is mainly designed to make, as easy and fast as possible, line plots in Microsoft Windows environments. It is also able to perform some post-processing on the plotted curves: algebraic operations, computation of the Fourier series coefficients. The program has an easy-to use graphical user interhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3face, and the 32 bit code provides very fast operation. Up to 3 PL4 or ADF files can be simultaneously held in memory for easy comparison of different data and up to 8 curves per plots versus time, or X-Y plots are allowed. The program has a clever automatic axis scaling capability and able to make plots with two independent vertical axes and provides easy tools for factors, offsets and zoom support, and a graphical cursor to see values in numerical format. Screen plots can be exported as Windows Metafile via win32 clipboard. The program also comes in a multi-window edition PlotXwin.exe.

period, he/she must send an acknowledgement letter to the developer.

was steadily developed and improved until 1997 using Borland Turbo Pascal under MS-DOS platforms. The program can read PL4-file types of unformatted, C-like binary and formatted files. PCPLOT can display maximum 4 curves with 16000 plot points phttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3er curve. The maximum number of plot variables stored in the plot file is limited up to 100. The program supports three different plot types: time function (results of the simulations), X-Y plot (one variable against another), frequency-response (results of &quot;FREQUENCY SCAN&quot; cases). The values of the plotted variables can be displayed by means of a vertical marker line. Different type of curves (e.g. currents and voltages) can be mixed in the same plot by defining scaling factors and offset. The curves are drawn using solid lines with different colors and user can mark each curve with different characters at the desired positions. Visually redundant data points on plots are eliminated to accelerate the drawing speed. Screen plots can be sent to disk file in HP-GL format.

is a graphical output program for ATP-EMTP running under Microsoft Windows 95/98/NT/2000. The program is capable of processing PL4-files ofhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 C-like and formatted types Maximum 6 variables in the same diagram are allowed. Zooming, redraw features and a readout facility to obtain instantaneous values of plotted curves are provided. Screen plots can be copied to clipboard or save as color or monochrome bitmap image file.

characteristics of other postprocessors for ATP are summarized in [6].

version 5.6

Introduction

.3.4 Typical EMTP applications

-EMTP is used world-wide for switching and lightning surge analysis, insulation coordination and shaft torsional oscillation studies, protective relay modeling, harmonic and power quality studies, HVDC and FACTS modeling. Typical EMTP studies are:

Lightning overvoltage studies  Switching transients and fhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3aults  Statistical and systematic overvoltage studies  Very fast transients in GIS and groundings  Machine modeling  Transient stability, motor startup  Shaft torsional oscillations  Transformer and shunt reactor/capacitor switching  Ferroresonance  Power electronic applications  Circuit breaker duty (electric arc), current chopping  FACTS devices: STATCOM, SVC, UPFC, TCSC modeling  Harmonic analysis, network resonances  Protection device testing

.3.5 Hardware requirements for ATP

is available for most Intel based PC platforms under DOS, Windows 3.1/9x/NT, OS/2, Linux and for other computers, too (e.g., Digital Unix and VMS, Apple Mac’s, etc.). Most users, including program developers, use Intel Pentium-based PCs with MS-Windows 9x/NT. A standard Pentium PC configuration with min. 128 MB RAM, hard disk (20 MB free space) and VGA graphics is sufficient to execute ATP under MS-Windows. Most popular programhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 versions are at present:

MS-Windows 9x/NT/2000/XP/Vista : 32-bit GNU-Mingw32 and Watcom ATP

MS-DOS, MS-Windows 3.x/95/98 : 32-bit Salford ATP (requires DBOS/486)

Linux: GNU version of ATP

.4 Contents of this manual

User’s Manual of ATPDraw for Windows 5.5 contains five parts:

MANUAL

to obtain the ATP license

to download ATPDraw

to install ATPDraw

requirements

to configure your system

to use ATPDraw as operating shell for other ATP simulations

to communicate with other users and program developers

MANUAL

to create a circuit in ATPDraw

windows

first circuit

version 5.6  15

Introduction

-phase circuits and connections

MANUAL

of mahttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3in menu items and program options

of the Component, Text, Connection, Node and Group dialog boxes

of ATPDraw circuit objects

MANUAL

to create new circuit objects in ATPDraw

to use MODELS and $Include in ATPDraw?

to use the integrated LCC object for line/cable modeling

to use the integrated BCTRAN object for transformer modeling

to use the Hybrid Transformer component

four non-standard Component dialog boxes:

3-phase transformer

Machines

switches

source

graphics and picture background

module

MANUAL

/cable constant application examples

-phase to ground fault and fault tripping transients

capacitor bank switching

studies, arrehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ster modeling

width modulated induction machine

machine controls

station, rectifier/converter modeling

energization, inrush currents

energization studies with statistical approach

.5 Manual conventions

following typographical conventions are used in this manual:

: Menus in ATPDraw

.g.: Select Edit | Rotate L : Select Rotate L command in the pop-up menu Edit.

9 - 10: Data files.

.g.: Listing of ATP input files, MODELS code, etc.

of menu options in component dialog boxes.

11 - 12: Data code and file names.

.g.: Give the file the name HVDC_6.LIB and store it in the directory.

directory is a directory under the main directory of ATPDraw.

12 : Commands on the DOS prompt.

.g.: C:&gt;setup: Type the commanhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3d setup at C:&gt;.

version 5.6

[此处图片未下载成功]

ATPDraw version 5.6  17

Manual         ATPDraw version 5.6

Installation Manual

.1 ATP licencing policy

and the present documentation includes ATP proprietary information, thus ATP licensing is mandatory prior to get permission to download the program from the Internet. ATP license is free of all charge for all who have not engaged in EMTP commerce, and it can be obtained from the Canadian/American EMTP User Group, or an authorized regional users group. In general, organizational licensing is preferred over licensing of individuals. Undergraduate students are not licensed personally. If ATP usage is to be organizational rather than personal (i.e., if ATP materials are to be used by, in, for, or on behalf of, a company, university, etc.), the

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3par[此处图片未下载成功]

licensee must certify that the organization has not participated in EMTP commerce -- nor has any employee, contractor, or other agent who would be granted access to ATP materials. Once one is licensed, he/she is authorized to download ATP materials from the secure Internet sites or obtain them from a similarly licensed user, or order these materials from the regional user groups.

present the Canadian/American, European and the Japanese user groups accepts ATP license applications via the Internet. Interested parties are requested to visit the on-line licensing page at http://www.wendangwang.com, fill-in and submit the appropriate web-form. Potential users of other continents must follow the licensing procedure of their regional EMTP user group. Geographical location of ATP-EMTP user groups and contact information details are shown below:

.  2.1 - Location of ATP-EMTP user groups.http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3

2.7.3 of the Installation Manual gives further information about the ATP related Internet resources.

.2 How to download ATPDraw?

licensing is mandatory prior to receiving any materials. Following the license agreement approval by an authorized user group, you are eligible to use the ATP program and all ATP related tools, like ATPDraw and this manual. There are different sources of obtaining ATPDraw and additional ATP related tools and program manuals:

Order ATP materials from the Canandian/American EMTP User Group (http://www.wendangwang.com/canamfl.html#ger) in Oregon, USA, or from the European EMTP-ATP Users Group Association (http://www.wendangwang.com).

Download from secure, password-protected web site of the European EMTP-ATP Users Group Association (http://www.wendangwang.com/files/secret)

version 5.6  Source: http://www.wendangwang.com 1http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db39

Installation Manual

Download from secure, password-protected web sites of the Japanese ATP User Group (http://alpha.kisarazu.ac.jp/~secure, or

://pels.pwr.eng.osaka-u.ac.jp/~atp/restricted)

Download from the password-protected FTP file server at Michigan Technological University in Houghton (USA) (http://www.ee.mtu.edu/atp/ftp.html).

contact the regional user group to acquire passwords to access these sites. Passwords are changed regularly!

.3 Hardware requirements for ATPDraw

requires moderate CPU power and memory. It runs even on a slow Pentium 100 MHz/32 MB PC with acceptable speed. A standard Pentium PC configuration with min. 128 MB RAM (256 MB under Windows 2000 and XP), 100 MB free hard disk space and XVGA graphics is sufficient to execute ATPDraw and other ATP programs.

.4 Program installation

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3e /atpdraw subfolder under the above secure servers contains a zip-compressed archive atpdraw5x.zip, a short installation guide and the latest patch file (if any). Following a successful download of the distribution kit, perform the next operations:

) Copy the atpdraw5x.zip file into a TEMP directory and unzip it.

) Run the program setup.exe. The installation process will be assisted by a standard Install Shield Wizard.

) Specify a destination directory for ATPDraw when prompted. It is wise to avoid using directory name including &quot;space&quot;. E.g. C:Files is not recommended. Install the program into a root directory, e.g. D:. If you are not allowed to install programs outside Program Files, let the Wizzard to install ATPDraw into this folder. Note that in such a case special care is needed when setting environmental variables for ATP.

) The installation process will be comhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3pleted after creating a new shortcut for ATPDraw under Start | Programs | ATPDraw. When you start ATPDraw5.exe first time it will create the necessary system sub-folders /ATP, /BCT, /HLP, /LCC, /MOD, /Project under the main program folder.

) Download the latest patch file called patchxv5.zip (if exists on the server), then unzip it and simply overwrite the existing files in the ATPDraw system folder with the newer ones received in the patch file.

program installation will create a directory structure as shown next. ATPDraw can be uninstalled in the standard manner using Windows' uninstaller (Start menu | Settings | Control Panel | Add/Remove programs).

&lt;DIR&gt;        10-22-01  9:54p Project

&lt;DIR&gt;        10-22-01  9:54p lcc

&lt;DIR&gt;        10-22-01  9:58p Atp

&lt;DIR&gt;        04-29-02  8:11a Usp

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3OD            &lt;DIR&gt;        10-22-01  9:58p Mod

&lt;DIR&gt;        03-22-02 12:42p Bct

version 5.6

ATPDRAW  EXE     2,465,792  04-12-08 10:58a Atpdraw.exe

CHM     1,069,056  04-12-08  3:24p ATPDraw.chm

SCL       184,320  04-10-08 10:08p ATPDraw.scl

_ISREG32 DLL        24,576  02-07-96  8.07a _ISREG32.dll

ISU         2,863  06-08-02 10.11a DeIsL1.isu

BAT            71  10-22-01 10:22p runAF.bat

_G BAT            90  10-22-01 10:56p runATP_G.bat

_S BAT           108  10-22-01 10:55p runATP_S.bat

_W BAT            90  10-22-01 10:54p runATP_W.bat Installation Manual

files _ISREG32.dll and DeIsL1.isu are created by the install shield for uninstall purposes.

.5 Files and sub-folders in the ATPDraw system folder

use ATPDrawhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 three files are required: ATPDraw.exe, ATPDraw.scl (standard component library), and ATPDraw.chm (help file). Besides, the user can create his own library components (user specified or models) and include files. ATPDraw does not rely on other specific disk files.

fileproject file is compressed by a public domain Pkzip 2.0 routine and can in fact be opened with any version of WinZip. (It may occur that a virus checker inaccurately recognizes the project files as virus infected and quarantine them when you send or receive such a file in e-mail attachments. If it happens, the local virus filtering database should be modified to allow the exchange of project files. Contact IT staff!)

file: All components inherit their properties from a support file. This file describes the type of component, the nodes (phases, position, identity) and data (default value, limits, parameter flag, number of digits, identity)http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3, the default icon (bitmap or vector) and a help text. The support files for standard components are zipped together in the file ATPDraw.sclsupport files can be edited inside ATPDraw in the Library menu. The default icon can also be modified by using the built in icon editors. New user specified objects are created by specifying new support files.

file: This file is produced by ATPDraw and used as input to ATP simulation. The .atp files with all $Include files are written to the Result Directory with default location is specified as the sub-directory under Tools|Options/Files&amp;Folders. The Result Directory can be changed via ATP|Sup-process|Make ATP file. The ATP can be edited with any text-processors, including ATPDraw’s own Text Editor (Atp|Edit ATP file (F4)). It is advised, however only for experts to modify this file manually.

files: User Specified Objects, Line&amp;Cables, and Windsyn componehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3nts are described in a library file (.lib). This text file has a pre-defined format (as specified in by the Data Base Module of ATP) and contains a header describing the positions of the parameters, further the ATP cards and finally a trailer containing the specification of the parameters. The library file is included in the ATP input file with $Include. The include files are stored in memory and written to the Result Directory (same as ATP file) each time the ATP file is created. Some nonlinear components or saturable transformers might also have an include file for the nonlinear characteristic.

files: The user can export data for special components to a libray for later use. A data file is introduced because the involved components have too many data to fit in to the standard

version 5.6  21

Installation Manual

library data structure. The data for a component http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3in the circuit is stored internally in memory. The following file types are used:

A line or cable is described by an .alcline-, cable constants or cable parameter data. It should preferably be stored in the directory.

BCTRAN (Transformer) component is described in a .bct file. This binary file contains the input data required for the supporting routine BCTRAN of ATP-EMTP. It should preferably be stored in the directory.

Hybrid Transformer model is described by a .xfm file. This file contains the winding resistance, leakage inductance, capacitance, and core data. It should preferably be stored in the directory.

model is described in a model file (.mod). This text file starts with MODEL &lt;name&gt; and ends with ENDMODEL. The &lt;name&gt; must be equal to the model file name. The model file is included directly in the final ATP input data file. It is recommended to store the models http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3file in the sub-directory.

.5.1 Organizing the files

ATPDraw opens a project no file is written to disk. All data are stored in memory. When the project is stored the disk files are not deleted. Thus, as times goes by the number of files on are stored in the project and only the files you export/modify yourself outside a project need to be kept. Two house-keeping options are available under Tools|Options/View/ATP:

Delete temp-files after simulation: Deletes all temporary BCTRAN/LCC files (.dat, .lis. pch) and all temporary ATP files *.bin when the simulation is finished. The files required to run ATP outside of ATPDraw (atp- and lib- files) are left on disk. In case of protected elements the lib-files are immediately deleted and the atp-file is modified. During

a LCC or BCTRAN model this button should be left unchecked.

Delete result files on exit: Deletes the all tehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3mporary and result files (.atp, .lib, .lis, .pl4, .dat, .pch, .bin, .gnu) from ResultDir (the ATP folder as default) when the circuit is closed. All data is stored in the project files of ATPDraw anyway.

.5.2 Configuring ATPDraw

ATPDraw.ini file contains customizable program options. One such file for each user of the computer is stored in %APPDATA%. The environmental variable APPDATA is system dependent but typical equal to 'c:and SettingsData'. Generally, default settings meet most of the user’s requirements. When required, the .ini file can either be modified via Tools | Options menu of the program, or by using a text editor.

.6 Interfacing ATPDraw with other programs of the ATP-EMTP package

ATP-EMTP simulation package consists of various separate programs which are communicating with each other via disk files: i.e. the output of pre-processors are used http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3as input for the main program TPBIG.EXE, while the product of the simulation can be used as input for plotting programs. The main program itself is often used as pre-processor (e.g. for LINE CONSTANTS, CABLE CONSTANTS, BCTRAN or DATA BASE MODULE runs), and the punch-file products in that cases can be re-used as input in a subsequent run via $Include. Taking that the

version 5.6

Installation Manual

of the program components is rather difficult, a user shell to supervise the execution of separate programs and input/output flows has a great advantage.

Edit Commands…feature of ATPDraw supports to extend the command set under the ATP menu by integrating optional user commands, such as

[此处图片未下载成功]

Run ATP (file) / Run PlotXY / Run TPPlot / Run PCPlot / / Run ATP_Analyzer / Run ACC / Run PL42mat, etc.

[此处图片未下载成功]

This option makhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3es possible to use the ATPDraw program as a graphical operating environment and execute the other ATP programs in a user friendly way as shown in Fig. 2.2.

.ADP project file

.ALC

data USP

.PCH library Fig.  2

[此处图片未下载成功]

.  2.3 - The Edit Commands dialog box.       Fig.  2.4 - User specified commands.

version 5.6  23

Installation Manual

the Edit Commands dialog box of Fig.  2.3 the user can specify the name of a .bat or an .exe file and the name of a file, which then will be sent as parameter (e.g. ATP.bat &lt;current .atp file&gt; or PlotXY.exe &lt;current .pl4 file&gt;) when ATPDraw executes these external programs. The Name field specifies the name of the command, while the Command and Parameter fields specify the name of the file to be executed and the optional parameter. Selecting Current ATP radio button, the full nhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ame of the ATPDraw project in the current circuit window with extension .atp

[此处图片未下载成功]

will be sent as parameter. When selecting the File button, the ATPDraw performs a file open dialog box before executing the command, where the user can select a file, which is then will be passed as parameter. The commands are inserted in the ATP menu dynamically, when the user activates the Update button as shown above.

.  2.5 - Default settings to run ATP and Armafit.

default batch command that is executed when the user selects run ATP or (F2) is specified under the Tools | Options /Preferences tab as shown in Fig.  2.5. Checking the contents of this batch file is very important following the program installation, because ATPDraw needs to be able to execute ATP for several reasons automatically, and this has always performed by activating this command. It must be noted that ATPDraw has no connectihttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3on with the main program of ATP (TPBIG.EXE) at the code level or via DLLs. The run ATP menu item simply executes the external commands specified by the user. So it is always the user’s responsibility to install ATP properly and provide these external .bat files in correct format.

.6.1 Calling Watcom ATP and GNU MingW32 ATP from ATPDraw

execution of the Watcom and GNU version of ATP requires that environmental variables WATDIR or GNUDIR be set correctly1, i.e. SET WATDIR=Drive: in the AUTOEXEC.BAT if you use Win9x, or set these parameters under My Computer | Properties dialog if Windows NT/2000 or XP is used. The RunATP_W.BAT and RunATP_G.BAT commands are created by the install program of ATPDraw. These batch files has a single line: %watdir%tpbig.exe both %1 * -r

The Install Shield wizard of the annual ATP program ditribution for EEUG members makes these settings automaticahttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3lly.

version 5.6

%gnudir%tpbig.exe both %1 s –r Installation Manual

an additional “W” or “G” is seen at the end of the ATP executable (TPBIG.EXE) in your installation, you have to modify the RunATP_*.BAT accordingly. You may find inserting some additional commands into these batch files, as well. E.g.:

off

%gnudir%tpbigg.exe both %1 s -r

-- waits for user interaction before the DOS box of ATP closed (optional)

dum*.bin      -- delete temporary files created by ATP (optional)

*.tmp

...tmp

illustrated in Fig.  2.3 it is in some cases possible to run the tpbix.exe program directly from ATPDraw. The batch file flag %1 must then be replace by $$ in the ATP-command.

.6.2 Calling PlotXY , PCPlot or ATP_Analyzer

main plotting command can be set as shown in Fig.  2.5http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3. When selecting this command (short cut F8) the plotting program starts with the current ATP-file (with extension .PL4) as parameter. The user can in addition create the Run ATP Analyzer and/or Run WPCPLOT commands using the ATP | Edit Commands submenu selet “Current PL4” as Parameter and Browse to select the name of the executable disk file of the corresponding application. Update button adds the new Run…command to the ATP menu.

.6.3 ATPDraw command line options

lines are rarely used under Windows operating systems, nevertheless ATPDraw provides an option to load one or more project files at program start. In the example below, the project file my1st.acp and my2nd.acp will be loaded automatically and displayed in separate circuit windows.

:&gt;atpdraw c:st.acp c:nd.acp

MS-Windows environment you can use this property to create a shortcuts on the deshttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ktop for the ATPDraw project files. For instance, click with the right mouse button on an empty space of the desktop and select New | Shortcut, then browse and select ATPDraw.exe. Click right on the just created icon and select Properties. Specify the ‘Target:’ properties of the new shortcut as the full path of the program including the project file name (e.g. c:.exe mycir.adp), and the ‘Start in:’ parameter as the project file directory (e.g. c:).

.6.4 Drag and drop project files

accepts project files dragged from the Windows File Manager (from v. 5.6). Dropping the project file (.acp) on the header, main menu of background causes the file to be opened in a new circuit window. Dropping the file in an existing circuit window causes the file to be imported into that circuit.

.7 How to get help?

offers a standard Windows help file system. http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3This file provides help on all windows and menus in ATPDraw and assists in building up a circuit. Several links between help pages and a relatively large index register for searching text or phrases are also available. A Help button is

version 5.6  25

Installation Manual

to all circuit objects, which shows a brief overview of the meaning of each parameter. Modification and extension of these help files with users’ own remarks are also possible using the built in Help Editor in the Tools menu.

.7.1 Help from the author of ATPDraw

author of the program is also available for questions from ATPDraw users, but is only responsible to Bonneville Power Administration and Pacific Engineering Corporation.

: Dr. Hans Kr. H&#248;idalen

University of Science and Technology

. Electric Power Engineering

Trondheim - NOhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3RWAY

://www.ntnu.no

-mail: Hans.Hoidalen@elkraft.ntnu.no

:   47 73594225

:    47 73594279

ATPDraw Web page is maintained at address:

://www.elkraft.ntnu.no/atpdraw

.7.2 Help via electronic mail

mail is the most known feature of the Internet. By this way, anyone who has an account on a computer connected to the Internet can send messages to others. For ATP users this service provides an easy, efficient and very fast way of communication with other users all over the world, including program developers, regional user group representatives, or the author of ATPDraw.

.7.3 Help via the ATP-EMTP-L mailing list

listserver is an E-mail remailer program, which rebroadcasts incoming messages to all subscribers to the list. The European EMTP-ATP Users Group Association in cooperation with the German Research Network (Dhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3FN) and the University of Applied Sciences of Osnabr&#252;ck, Germany operates a free electronic mailing list using address atp-emtp-l@listserv.dfn.de. This LISTSERV mailing list is for ATP-related announcements, questions, answers, etc. The ATP-EMTP-L list is moderated and only licensed ATP users are entitled to subscribe by means of the authorized persons of the regional ATP-EMTP user groups, who checks first the license status of the applicant, then send a subscription request to the list operator. To learn more about the subscription procedure and the operation rules of this very active mailing list, please visit the http://www.wendangwang.com web site.

your name has been added to the list, you can post messages. To do this, you simply send e-mail to atp-emtp-l@listserv.dfn.de. Your message then will be submitted to moderators, who decide whether or not to accept it. The task of moderators is maintenance ohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3f the quality of communication and discussion. The language of communication is English. Messages written in any other language are not accepted. The author of each submission must be clearly identified. This includes name, organizational affiliation, and location. Attachments, especially encoded files, are not allowed. They can be forwarded later to interested persons by private e-mail. Any subscriber who sends a message to this mailing list gives up his right to confidentiality. This is regardless of the message's possible declaration in auto-attached legal disclaimers, which are

version 5.6

Installation Manual

by moderators. Subscribers of the ATP-EMTP-L mailing list must fulfill the ATP license requirements. Specifically, they are forbidden to disclose to non-licensed persons ATP information that is received from this mail service.

.8 Available circuit ohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3bjects in ATPDraw

the time of writing of this manual ATPDraw's standard component library contains 262 circuit object support files. These 262 files support more than 170 of ATP's components, i.e. many components have several versions in ATPDraw.

components

branches:

, Inductor, Capacitor, RLC

3-phase, symmetric and non symmetric

and capacitor with initial condition

-linear branches:

-phase nonlinear R and L components

dependent resistor, type 99

, 96 and 98 nonlinear inductors including initial flux linkage conditions             Time dependent resistor, type 97

and 3-phase MOV type 92 exponential resistor

controlled resistor

models:

, PI-equivalents (type 1, 2...) and RL coupled components (type 51, 52...)             RL symmetric, sequence inphttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ut. 3 and 6-phase

lines of constant parameters, Transposed (Clarke), untransposed (KCLee)             LCC objects: Bergeron, nominal PI, JMarti, Semlyen and Noda models

:

controlled. 1 and 3-phase

controlled

, thyristor, triac (type 11 switches)

TACS controlled switch of type 13

switches

and systematic switches, independent and master-slave

:

, type 11

, type 12

-slope ramp, type 13

source. 1 and 3 phase, type 14

-exponential surge source, type 15

-type source, type 15

-type source, type 15

&#201;-type source, type 15

source, type 60

DC source, type 11 18

AC source, type 14 18

:

machine type 59 with no control, or max. 8 TACS chttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ontrols

machines. Universal machines (type 1, 3, 4, 6, and 8)

(separate program, manufacturer data)

version 5.6  27

Installation Manual

:

-phase and 3-phase ideal transformer. Type 18 source

-phase saturable transformer

-phase, 2- or 3 winding saturable transformer (Auto, Delta, Wye, and ZigZag)

. 1-3 phases, 2-3 windings. Auto-transformers, Y-, and D- connections

Transformer (XFMR) with topological core; triplex, 3 or 5-legged, shell form. 3-phases. 2-3 windings. Auto, Y- and D-coupled windings.

/output and Data variables of MODELS code are recognized automatically             Corresponding support file for the model is automatically created

94 (Thevenin, Norton, Iterative) objects are supported

cost function

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3rto circuit object helps in hybrid simulations

functions: General Laplace transfer function with or without limits

, Derivative, first order Low and High Pass transfer functions

statements: General Fortran statement (single line expression)

Math statements or Logical operators

: DC, AC, PULSE, RAMP.

devices (50-66).

condition for TACS objects (type-77)

specified objects

can create new objects using Data Base Modularization and $Include

-state components

sources for Harmonic Frequency Scan studies

and 3-phase frequency dependent loads in CIGR&#201; format

phase RLC element with frequency dependent parameters

flow components

version 5.6

Installation Manual

.

[http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3此处图片未下载成功]

version 5.6  29

Introductory Manual

part of the user’s manual gives the basic information on how to get started with ATPDraw. The Introductory Manual starts with the explanation of how to operate windows and mouse in ATPDraw. The manual shows how to build a circuit step by step, starting from scratch. Then special considerations concerning three phase circuits are outlined.

[此处图片未下载成功]

3.1 Operating windows

has a standard Windows user interface. This chapter explains some of the basic functionalities of the Main menu and the Component selection menu of the Main window.

menu Tool bar iconsZoom and Node

,

file

action

Status bar with

option hinhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ts Component

menu

.1 - The Main window and the floating Component selection menu. Fig.  The ATPDraw for Windows program is functionally similar to the DOS version [1]. The Component selection menu is hidden, however, but appears immediately when you click the right mouse in the open area of the Circuit window.

.  3.1 shows the main window of ATPDraw containing two open circuit windows. ATPDraw supports multiple documents and offers the user to work on several circuits simultaneously along with the facility to copy information between the circuits. The size of the circuit window is much larger than the actual screen, as is indicated by the scroll bars of each circuit window. The Main window consists of the following parts:

version 5.6  31

Introductory Manual

Frame:

a standard Windows element, it contains the system menu onhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 the left side, a header text and minimize, maximize, exit buttons on the right side. The main window is resizable.

menu: Contains possible window actions: Close, Resize, Restore, Move, Minimize,

or Resize and Next. The last one exists only if multiple circuit

are open.

text: The header text is the program name in case of the main window and the

circuit file name in case of the circuit window(s). To move a window,

in the header text field, hold down and drag.

button: A click on this button will iconize the main window.

button: A click on this button will maximize the window. The maximize button will

be replaced with a resize button. One more click on this button will bring

window back to its previous size.

:  Click on the corner, hold down and drag to resize the window.

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ain menu:

main menu provides access to all the functions offered by ATPDraw. The menu items are explained in detail in the Reference part of this Manual:

:   Load and save circuit files, start a new one, import/export circuit files, create

and metafile/bitmap files, print the current circuit and exit.

:   Circuit editing: copy/paste/delete/duplicate/flip/rotate, select, move label, copy

to clipboard and undo/redo etc.

:  Tool bar, status bar and comment line on/off, zoom, refresh and view options. ATP:  Run ATP, make and edit ATP-file, view the LIS-file, make node names, ATP-file

(miscellaneous, file format, file sorting etc.), assign data to variables for

$PARAMETER. Find Node and Line Check. Output Manager lists all output requests. Library: Edit support files (default values, min/max limits, icon and help file), create new files://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3parMODELS and User Specified Objects.

: Icon editor, help file editor, text editor, setting of various program options.

: Arrange the circuit windows and show/hide the Map window.

:  About box and Windows help file system.

and node size:

these menus you can type in zoom and node size in [%] or select predefined values in the popup box.

window:

circuit is built up in this window. The circuit window is the container of circuit objects. From the File menu you can load circuit objects from disk or simply create an empty window to start building a new circuit. Circuit objects include standard ATP components, user specified elements, MODELS and TACS components, connections and relations. To move around in the circuit, you can use the window scrollbars, or drag the view rectangle of the Map window to another position. Component selection menu:

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3parthe Circuit window. In this menu you select the circuit objects. After selecting an object in one of the sub-menus, the object is drawn in the circuit window in marked and moveable mode. Circuit comments:

comment line below the circuit window shows a user defined circuit comment text.

version 5.6

Introductory Manual

window:

window gives a bird's eye view of the entire circuit. The size of a circuit is 10000x10000 pixels (screen points); much larger than your screen would normally support. Consequently, the Circuit window displays only a small portion of the circuit. The actual circuit window is represented by a rectangle in the Map window.

and hold down the left mouse button in the map rectangle to move around in the map. When you release the mouse button, the circuit window displays the part of the circuit defined by the nehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3w rectangle size and position. The map window is a stay-on-top window, meaning that it will always be displayed on the top of other windows. You can show or hide the map selecting the Map Window option in the Window menu, or pressing Ctrl M character,

bar - Action mode field:

current action mode of the active circuit window is displayed in the status bar at the bottom of the main window, when the Status Bar option is activated in the View menu. ATPDraw can be in various action modes. The normal mode of operation is MODE : EDIT , in which new objects are selected and data are given to objects. Drawing connections brings ATPDraw into CONN.END mode and so on. ATPDraw’s possible action modes are:

.END The normal mode. After a click on a node, the action mode turns into CONN.END indicating that

program is waiting for a left mouse click to set the end-point of a new

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3parconnection. To cancel drawing a connection, click the right mouse button or

the ESC key to return to MODE : EDIT.

that text editing is preferred. Hold down the Alt key to enter this

of operation or select Edit Text from the Edit menu. Click left in an

space to add a new text. Click the left mouse button on an existing text

(circuit text, label, node name) to edit it direcly on screen. Click left, hold

and drag to move it to a new position. If the text is overlapped by a

icon, this mode of operation is required to access the text.

region selection. Double clicking the left mouse button in an empty

of the active circuit window enables you to draw a polygon shaped

. To end the selection, click the right mouse button. Any objects within

selected region are marked then for selection. To canchttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3el region selection,

the Esc key.

the start of a relation when TACS | Draw relation is activated in the

menu. Clicking the left mouse button on a component node or on the

-point of another relation will initiate the drawing of a new relation.

are used to visualize information flow into FORTRAN statements

are drawn as blue connections, but do not influence the connections of

.

the end of a relation. The program is waiting for a left mouse button

to set the end-point of the new relation. To cancel drawing relation, click

right mouse button or press the Esc key. EDIT TEXT GROUP  INFO.START INFO.END

bar - Modified and Hints field:

middle field of the status bar is used to display the Modified state of the active circuit. As soon as you alter the circuit (moving http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3a label, deleting a connection, inserting a new component, etc.), the text Modified appears, indicating that the circuit should be saved before exit. The field will be empty when you save the circuit or undo all modifications. The rightmost field of the status bar displays the menu option hints.

version 5.6  33

Introductory Manual

.2 Operating the mouse

chapter contains a summary of the various actions taken dependent on mouse operations. The left mouse button is generally used for selecting objects or connecting nodes; the right mouse button is used for specification of object or node properties.

object: Selects object or connection.

the Shift key is pressed, the object is added to the current selection group.

connection: Draw a new connection with the same properties. On object node: Begins to draw a connection.

the mouse to thhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3e end node, left click to place, right to cancel.

text, labels and node names: Edit the text directly on screen. Press Alt to favour the text

compared to components and connections.

open area of the circuit window: Unselects object.

open area of the circuit window:

the Component selection menu, or

the connection made if connection draw mode has been activated earlier.

object node:

-up the Node data window.

unselected object:  Opens the Component/Connection or Text dialog box.

Shift key is pressed simultaneously: opens the circuit window Shortcut menu.

selected object(s): Rotates object(s).

Shift key is pressed simultaneously: opens the circuit window Shortcut menu.

object: Moves the object or selected group of objects.

connection: Select connection.

node: Resizes connehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ction (it is often necessary to select connection first).

open area of the circuit window: Draws a rectangle for group selection.  Objects inside the rectangle are becoming member of the group when

mouse button is released.

text, labels and node names: Move the text. Press Alt to favour the text selection

to components and connections.

object node:

the Node data window.

selected or unselected single object:

the Component/Connection or Text dialog box.

selected group of objects:

an Open Group dialog box.

open area of the circuit window:

the group selection facility. Click left to create an enclosing polygon, click right

close. Objects inside the polygon become a group.

version 5.6

Introductory Manual

.3 Edit http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3operations

offers the most common edit operations like copy, paste, duplicate, rotate and delete. The edit options operate on a single object or on a group of objects. Objects must be selected before any edit operations can be performed. Selected objects can also be exported to a disk file and any circuit files can be imported into another circuit.

Ctrl Z   Edit | Undo REDO            Ctrl Y   Edit | Redo Cut/Copy     Ctrl X/Ctrl C  Edit | Cut/Copy Delete         DEL   Edit | Delete Paste         Ctrl V   Edit | Paste Duplicate        Ctrl D   Edit | Duplicate Select/All        Ctrl A   Edit | Select All  Select/Inside       Ctrl I   Edit | Select| Inside (or left double click in open space) Select/Properties       Ctrl P   Edit | Select| by Properties New/Select text       Ctrl T   Edit | Edit text Rotate clockwise       Ctrl R   Edit | Rotate R (or right click) Rotate left        Ctrl L http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3  Edit | Rotate L Flip         Ctrl F   Edit | Flip Rubber Band       Ctrl B    Edit | Rubber Bands  Edit Group/Circuit  Ctrl G/Ctrl H  Edit | Edit Group/Circuit  (one layer down or up) Zoom In/Out        NUM   / -  View | Zoom In / Out Refresh        Ctrl Q    View | Refresh (redraw the circuit)

.4 Overview of working with ATPDraw

selecting a component in the Component selection menu the new circuit object appears in the middle of the circuit window enclosed by a lime-colored rectangle. Click on it with the left mouse button to move, or the right button to rotate, finally click in the open space to unselect and place the object.

select and move an object, simply press and hold down the left mouse button on the object while moving the mouse. Release the button and click in an empty area to unselect and confirm its new position. The object is then moved to the nearest grid point (known as gridhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3snapping). If two or more components overlap as a consequence of a move operation, you are given a warning message and can choose to proceed or cancel the operation.

a group of objects for moving can be done in three ways: Holding down the Shift key while left clicking on an object. Pressing and holding down the left mouse button in an empty area enables the user to drag a rectangular outline around the objects he wants to select. And finally, double-clicking the left mouse button in an empty area enables the definition of a polygon-shaped region by repeatedly clicking the left mouse button in the circuit window. To close the region, click the right mouse button. Components with centre point within the indicated region or rectangle are added to the selected objects group. Connections require both end points within the region to be selected. Select Edit|Rubber Bands to stretch connections with one end insidhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3e and one end outside. To move the selected group of objects, press and hold down the left mouse button inside the group while moving the mouse. Unselect and confirm the new position by clicking in an empty area. Any overlapping components will produce a warning. To move objects outside of the visible part of the circuit, use the window scrollbars or the view rectangle in the

version 5.6  35

Introductory Manual

window. Any selected objects will follow the window to its new position. Objects or a group can be rotated by clicking the right mouse button inside the selected object or group. Other object manipulation functions, such as undo/redo and clipboard options can be found in the Edit menu. Additionally, the most frequently used object manipulation functions can be accessed by holding down the Shift key while clicking with the right mouse button on an object or on a selected group of obhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3jects. This will display and activate the circuit window shortcut menu.

and component nodes can be opened for editing by a right-click (or left double-click) on an unselected component or node. Either the Node data, Component or Open Probe dialog box will appear, allowing the user to change component or node attributes and characteristics. The Component dialog box shown in Fig. 3.2 has the same layout for most circuit objects. In this

[此处图片未下载成功]

window the user must specify the required component data. The number of DATA and NODES menu fields are the only difference between input windows for standard objects. The nonlinear branch components have a Characteristic page too, in addition to the normal Attributes page, where the nonlinear characteristics and some include file options can be specified. Some of the advanced components like LCC, BCTRAN, Hybrid Transformer have special dialog boxehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3s for input.

.2 – Component dialog box, attributes page. Fig.

Component dialog box shown in Fig.  3.2 consists of a Data part and a Node part. In the Data part the user can specify values using ‘.’ as the decimal symbol and use 'e' as exponent. A variable name (6-char text string) can also be specified and given a global value under ATP|Settings/Variables. Specifying a variable is only possible if the Param property in the definitions is set to unity (and the data is not used in internal calculations; RLC-lines with lengths&lt;&gt;1, phase angle of 3-phase AC source etc.). The Copy/Paste buttons allows copying the entire data set via the Windows clipboard. Node names (6 or 5 characters) can be specified in the right grid. Node names drawn in a red color are already given a name by the user while black names are inherited. If the user wants to change a node name the red names/nodes should be preferred, otherwise nhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ame conflict warnings will appear. Node data are also given in the Node dialog box by clicking on the nodes. Multi-phase nodes can only take a 5 character name, and the phase sequence extension A..Z is added automatically.

version 5.6

Introductory Manual

is optionally used for sorting (ATP|Settings/Format; sorting by order (low-high)), Label is a 12 character text string on screen, and Comment is a line of text written to the ATP file in front of the component’s cards. The Output panel varies somewhat between components, but is usually used for branch output requests. In the lower left corner there is Edit definitions button. This gives access to all the local properties inherited from the support file, including the icon, local help, names of nodes and data, node positions, default values, param flags, limits, and units.

on Help will display http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3the helt text for the component; first comes the global help obtained from the support files (ATPDraw.scl for standard components), second comes local help specific to this component, and finally comes global help from the /HLP directory.

component attributes are stored in support files. Access to create and customize support files is provided by the Library menu.

are connected if their nodes overlap or attached to the same connection. To draw a connection, click on a node with the left mouse button. A line is drawn between that node and the mouse cursor. Click the left mouse button again to place the connection (clicking the right button cancels the operation). The gridsnap facility helps overlapping the nodes. Connected nodes are given the same name by the run ATP option in the ATP menu. Nodes can be attached along a connection as well as at connection end-points. A connection shhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ould not unintentionally cross other nodes (what you see is what you get). A warning for node naming appears during the ATP-file creation if a connection exists between nodes of different names, or if the same name has been given to unconnected nodes. Connections can be selected as any other objects. To resize a connection, click on its end-point with the left mouse button, hold down and drag. If several connections share the same node, the desired connection to resize must be selected first. Selected connection nodes are marked with squares at both ends of the selection rectangle.

.5 Your first circuit (Exa_1.adp)

chapter describes how to use ATPDraw step by step. As an example, composing the circuit file of a single-phase rectifire bridge (see Fig.  3

[此处图片未下载成功]

.3) is presented. Reading this tutorial carefully, you will be proficient in the use of the most important ATPDraw functionshttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3, such as:

How to select and assemble components? How to perform edit operations and give data to components? How to give node names, draw connections and specify grounding? How to create the ATP input file and perform the simulation?

.  3.3 – Single-phase rectifier bridge.

version 5.6  37

Introductory Manual

[此处图片未下载成功]

[此处图片未下载成功]

Fig.  3.4 – Your first circuit (Exa_1.adp).

circuit is a single-phase rectifier bridge, supplied by a 120 Vrms, 60 Hz source. The source inductance is 1 mH in parallel with a damping resistor of 300 Ω. The snubber circuits across the rectifying diodes have a resistance of 33 Ω and a capacitance of 1 μF. The smoothing capacitor is 1000 μF and the load resistor is 20 Ω. The example has been taken from [2], exercise 1. The units given in Fig.  3.3 are based on settings of Xophttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3t and Copt equal to zero as will be

.4 has been chosen since its construction involves the most explained later. The circuit in Fig.

used edit operations.

.5.1 Building the circuit

parts of the building process will be demonstrated in this chapter, along with the explanation of correcting possible drawing errors. The normal mode of operation is MODE : EDIT. You must always be in this mode to be able to select and specify data to objects. To return to EDIT from other modes, press Esc.

.5.1.1 Starting to create a new circuit

the New command in the File menu or pressing the new (empty) page symbol in the Component Toolbar, a new circuit window will be created.

.5.1.2 Source

, an AC source is selected from the Component selection menu, which appears with a right mouse click on open area of the circuit window. Fig.  3.5 shhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ows how to select a general AC (type

) source under Sources | AC source (1&amp;3).

.  3.5 - Selecting an AC source.

you have clicked in the AC source (1&amp;3) field, the selected source appears in the circuit window in lime color, enclosed by a rectangle. Click on it with the left mouse button, hold down and drag it to a desired position. Then click with the left mouse button in open space to place it. The AC object is redrawn in red color as an indication that no data have been given to the object.

[此处图片未下载成功]

ATPDraw version 5.6

Introductory Manual

give data to the AC source component, click on with the right mouse button (or left double

[此处图片未下载成功]

click). You can give data to objects at any time during the building process. If you right click on the AC source icon, a window as shown in Fig.  3.6 appears. Click the radhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3io button RMS L-G

[此处图片未下载成功]

internally (the RMS L-LAmplitideA value the Peak L-G (standard, no scaling) option is required. A negative value for StartA parameter means that the source is active during steady-state initialization.

.6 - Component dialog box of the single-phase sinusoidal source. Fig.

.6 refer to the circuit parameters of Fig.  3.3. The name of the Data values shown in Fig.

fields is identical with that of used by the ATP Rule Book [3] for an AC source. This AC source has 5 input data and one node; AC (ACNEG and Interanl nodes disappear for grounded voltage sources). Click on the

[此处图片未下载成功]

HELP button to learn about the meaning of parameters.  The node names can also be specified in this window. Click OK to close the window and update the object values. Click on Cancel to just quit the window.

you have given data to thehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 AC source and closed the window (note how the object layout changes when you exit the window), proceed to the other objects. Next select the source inductance as shown in Fig.  3.7:

.  3.7 - Selecting an inductor.

version 5.6

[此处图片未下载成功]

39

Introductory Manual

you have clicked in the Inductor field, the selected inductor appears in the circuit window enclosed by a rectangle (an optional, parallel damping resistance is included). Click on it with the

.8: left mouse button, hold down and drag it to a position shown in Fig.

on the white space with the left mouse button to place the inductor

(the enclosing rectangle disappears). A grid snap facility helps you to  place the inductor in the correct position. The component position is Fig.  3

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

.http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db38 rounded to the nearest 10th pixel. (The included parallel resistor is shown

a gray style.)

inductor in Fig.  3.8 should be placed so that the node of the inductor touches the source. Objects having overlapping node dots will automatically be connected.

next figure shows two situations where the inductor has been misplaced and are disconnected. To correct the lower example, a connection could be drawn between the objects as will be explained later. In this example you are supposed to place the inductor so that its left node overlaps the AC source node. To move the inductor, follow the instructions below.

on the object with the left mouse button, hold down and drag it to the

position, then click on white space. The grid snap feature will help you. Fig.  3.9 – Not connected!

you have placed the inductor, you can add the damping resistanhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ce (possibly directly included). After you have clicked in the Resistor field of the component selection menu, a resistor icon appears enclosed by a rectangle. Click on it with the left mouse button, hold down and drag it to a position shown in Fig.  3.10. Click in open space to place/unselect it.

resistor is supposed to be parallel with the inductor and connections will be drawn later. The

in Fig.  3.10 would also be recognized as in parallel with the inductor, if it

been placed in a position completely overlapping the inductor. This tricky

is not recommended however, since the readability of the drawing is strongly

(also warnings will be issued by the circuit compiler).

.10

[此处图片未下载成功]

Fig.

[此处图片未下载成功]

want to measure the source current flowing into the diode bridge. To be able to do so, you can add a meashttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3uring switch. A special multi-phase current probe is available for such measurements in ATPDraw. When using this object, you are requested to specify the number of phases and in which phases the current should be measured. Select the probe as shown in Fig.  3.11.

.

[此处图片未下载成功]

3.11 - Selecting a current measuring probe.

you have clicked in the Probe Curr. field, the selected probe appears in the circuit window enclosed by a rectangle. Click on it with the left mouse button, hold down and drag it to a position shown in the figure, then place it.

this stage of the building process, it is time to draw some connections in the circuit diagram. To draw a connection you just click the left mouse button on a node, release the button and move

[此处图片未下载成功]

ATPDraw version 5.6

Introductory Manual

mouse. The curshttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3or style now changes to a pointing hand and a line is drawn between the

[此处图片未下载成功]

starting position and the current mouse position (the action mode now is MODE : CONN.END indicating that the program is waiting for the end point of the connection). Click with the left mouse button again to place the connection or click with the right button to cancel the starting point.

connection drawings are required to parallel connecting the source inductance and the damping resistor as shown below. The Connection dialog (color, phase number) automatically appears for connections drawn between multi- and single phase nodes, but not in this case.

left

move      Click left   Release   move    Click left     Click left

last object we want to introduce in the source part of the circuit is a voltage measuring probe, which results in an output request for the node http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3voltage in the ATP input file. The voltage sensor

be selected via the Probe &amp; 3-phase | Probe Volt in the component

menu (see Fig.

[此处图片未下载成功]

3.11). The probe is drawn in the circuit window in

and moveable mode. Use the left mouse button to drag and place

probe as shown on the figure to the left.

you place an object by clicking on open area of the circuit window, you will sometimes receive a warning message as shown in Feil! Fant ikke referansekilden.. This message appears if a center of one of the permanent objects is inside the enclosing polygon of a marked object (or more general; a group of objects). This is to prevent unintentional object overlap if the left mouse button were pressed while moving the object.

you click on No, the object is not placed but continues to be selected

you can move it further. Normally ihttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3t is OK to click on Yes. If you

your mind later, the Edit | UNDO option provides an easy way

[此处图片未下载成功]

to return to an earlier version of the circuit. If objects with the same

completely overlap the visual unambishiousity is violated (what

(MakeFile/run ATP).

.  3.12 - Prevent object overlap.

, give data to the components placed so far. Click with the right mouse button on the resistor and inductor icon, respectively. The inductor has a built in damping resistor option, but turn this off by choosing Kp=0.

probe objects have different input

than other objects. To open the

or current probe input window, click

its icon with the right mouse button. In this

, you can select the number of phases

the probe and which phases to monitor. In

single-phase examphttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3le, default values (no.

phases=1, monitored phase=A) of both  voltage and current probes should be selected, 3

[此处图片未下载成功]

.13 - Open probe dialog box. Fig.  as shown in Fig.  3.13

version 5.6

[此处图片未下载成功]

[此处图片未下载成功]

41

[此处图片未下载成功]

Introductory Manual

.5.1.3 Diode bridge

this process, you will learn how to use some editing options like rotate, group, duplicate and paste. Since the diode bridge consists of four equal branches, you do not need to build all of them from scratch. First, you select a diode from the selection menu as shown in Fig.  3.14. After you have clicked on Diode (type 11) the diode appears in the circuit window enclosed by a rectangle.

diode has to be rotated so click the right

button or select Edit in the main menu

click on Rotate L. The diodehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 is now rotated

deg. counter clock-wise. Click on the diode

the left mouse button, hold down and drag 3.15. to the position shown in Fig.

.  3.14 - Selecting a diode.

with the left mouse button on empty area to place the diode.

the grid snap facility and the overlap warning.

, you select the snubber circuit across the diode. In this example

snubber circuit is a resistor and a capacitor in series. Select an Fig.  3.15 RLC object from the component selection menu (Fig.  3.7).

on the selected RLC branch with the right mouse button to

, then click with the left button, hold down and drag the RLC branch to be in parallel with the diode. Click on the left mouse button to place.

idea is further to copy the diode and the RLC branch, but before doing so, it is wise to give data to them (since thehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 data are kept when copied). A simple click on the RLC or diode icon with the right mouse button activates the component dialog box to give data to objects.

, an explanation of the input parameters is given in a help file. Click the HELP button to see this help text. The numerical values of the diode are all zero, meaning that the diode is ideal and is open during the steady state. The RLC branch in Fig.  3.15 has been given a resistance of 33 Ω and a capacitance of 1 μF. The icon then changes to a resistor in series with a capacitor.

have now given data to the diode and the RLC branch and instead of repeating the drawing and data entering process four times, you can use the copy facility. First, you have to select a group of components. This can be done by selecting Edit | Select| Inside field in the main menu or with a double click with the left mouse button on an empty space of the Circuihttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3t window.

[此处图片未下载成功]

Then cursor style changes to a pointing hand and the action mode is EDIT : GROUP. The process is then to click with the left mouse button to create a corner in a fence and to click the right button to enclose the fence (polygon). All components having their center inside the fence are included in the group.

way of group selection is to draw a rectangle around the objects by a left mouse click and hold at the upper-left corner of the desired rectangle, and moving thereafter to the lower-right corner. Objects inside the rectangle become a group when the mouse button is released.

[此处图片未下载成功]

.16. You can follow the procedure shown in Fig.

version 5.6

[此处图片未下载成功]

[此处图片未下载成功]

Introductory Manual

. 3 .16 - Drawing a polygon: First double click on white space, chttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3lick the left mouse button at

corner of the polygon, then click the right button to enclose the polygon.

.16 can be copied/rotated etc. like a single object. Now we want to The group created in Fig.

this group. Click on the main menu Edit field and choose Duplicate or press the Ctrl D shortcut key. The selected group is copied to the clipboard and pasted in the same operation. The old group is redrawn in normal mode and the copy is drawn in the top of the original.

enclosing polygon is now a rectangle. The pasted

is moveable, so you can click on it with the left

button, hold down and drag to a desired position.

the left mouse button on open space to put the group Fig.  3.17 - Move a group. in the position shown in Fig.  3.17.

you misplaced the group you can reselect it or use the Undo facility found in the Edit main mehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3nu field.

can now paste a second copy of the diode/RLC group into the circuit. Since the duplicate facility has already copied the group to the clipboard, you can just select the Paste

[此处图片未下载成功]

option from the Edit menu by using the mouse or pressing

[此处图片未下载成功]

Ctrl V, or selecting the Paste icon from the Toolbar. The pasted group is drawn on top of the original one enclosed by a rectangle. Click on this group with the left mouse button, hold down and drag it to a position shown in Fig.  3.18.

.  3.18    Fig. 3.19

part of the connection between the rectifier bridge and the load a small resistor is included in Fig.  3.3. The resistor is included to demonstrate the option of using a small resistor for current measurement purposes.

a resistor in the component selection menu, then click on the resistor with the left mouse

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db33.19. You must place the button, hold down and drag it to a desired position as shown in Fig.

precisely, because the next step is to connect the top nodes of the diode bridge with the resistor.

doing so first, give data to this resistor opening the component dialog box by a right-click on the resistor. Specify data value RES= 0.01 Ω

[此处图片未下载成功]

and set Output to 1-Current to get the branch

→current in the subsequent ATP run. Having closed the component dialog box a small Isymbol

on the top-left side of the resistor indicating the current output request.

you can start to connect the diode bridge and the resistor together. The procedure is to first click with the left mouse button on a starting node, as shown in Fig.  3.20. The cursor style now

version 5.6  43

Introductory Manual

to a pointihttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ng hand and the action mode is MODE : CONN.START. Then release the mouse button and move the mouse (a rubber band is drawn from the starting point to the current cursor position). To place a connection, click on the left mouse button again. Click on the right

[此处图片未下载成功]

button or press

[此处图片未下载成功]

Esc to cancel the connection make operation.

connection draw in Fig.  3.20 picks up intermediate nodes so all the five nodes will be connected together. In this way, ATPDraw suits the requirement: “What you see is what you get” and the amount of required connections are significantly reduced.

.  3.20 - Click left button. Release   move, then click left button to place the connection.   If you made a mistake in the connection drawing process, you can correct the error easily, because

[此处图片未下载成功]

connections are editable (copy/move/rotate) as any other objects. Ihttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3f you would like to correct/modify a misplaced connection, click on it and hold with the left mouse button. After this selection, the connection is enclosed by a rectangle and two squares replace node dots at the end of the line. To move the connection, click on an internal point of it using the left mouse button, then hold down and move, and release the mouse at the correct position. To reposition a connection, click on the node squares with the left button and stretch the connection as illustrated in Fig.  3.21:

.21 - Edit connection. Click any point of the line then click node squares and stretch. Fig.

.5.1.4 Load

last part of this example circuit is the load consisting of a smoothing capacitor with initial condition and a load resistor. First, you can select the capacitor as shown in Fig.  3.22:

version 5.6

[此处图片未下载成功]

[此处图片未下载成功]://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ar

Introductory Manual

[此处图片未下载成功]

Fig.  3.22 - Select capacitor with initial condition.

this selection, the capacitor appears in the middle of the circuit window in moveable mode enclosed by a rectangle. Click on the capacitor with the left mouse button, hold down and drag to a desired position, then click the right mouse button (or press Ctrl R) to orient the capacitor as shown in Fig.  3.23. Finally, click on open space to place the capacitor.

[此处图片未下载成功]

Fig.  3.23 - Placing a capacitor with initial conditions.

select the load resistor in the component selection menu Branch linear   Resistor. The resistor is drawn in moveable mode in the circuit window. Click on it with the right mouse button to rotate, then click with the left mouse button, hold down and drag it to a desired position and place as shown in Fig.  3.24.

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3par3.24 - Place load resistor. Fig.

time has come to connect the load to the rest of the diode bridge. The process has been explained before. Click on the component nodes you wish to connect with the left mouse button, sequentially. A left mouse click on open area while in MODE: CONN.END generates a new node dot, which can be used as the starting point of any new connections. This way creating a circuit having only perpendicular connections (recommended for complex circuits, to improve the circuit readability) is a relatively simple task, as shown in Fig.  3.25.

[此处图片未下载成功]

Fig.  3.25 - Your first circuit is almost ready!

you have finished connecting the source side and the load side of the circuit, you can

version 5.6  45

Introductory Manual

the load data. Click with the right mouse button on the capacitor and specify the parameters shhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3own in Fig.  3.26.

.  3.26 - Capacitor data with initial condition.

capacitance is 1000 μF (if Copt=0 in ATP | Setting | Simulation). The positive node has an initial voltage of 75 V and the negative -75 V. Both branch current and voltage will be calculated, so the Current&amp;Voltage is selected in the Output combo box. Following the branch output request, the appearance of the object's icon will change if the Show branch output is checked under View | Option. If this option is enabled, a small  symbol appears on the top-left side of the capacitor, indicating the branch voltage and the current output requests (see Fig.  3.27).

click with the right mouse button on the load resistor to get the input window and specify the load resistance of 20 Ω. Branch current and voltages will be calculated so the small symbol  appears again on the top-left side of the resistor after leaving the dialog boxhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3. Once all the entries in the component dialog box are completed, select the OK button to close the window and update the object values or click Help to obtain an on-line help.

.5.1.5 Node names and grounding

final step of building this circuit is to give data to nodes (node names and grounding). All nodes will automatically receive names from ATPDraw, so the user should normally give name to nodes of special interest only. It is advised in general to perform the node naming as the last step in building up a circuit. This is to avoid undesirable multiple node names (which is corrected by ATPDraw automatically, but results in irritating warning messages).

give data to a node, you simply have to click on this node once with the right mouse button.

.27-Fig.  3.30 show how to give data to four different nodes. Fig.

[此处图片未下载成功]

ATPDraw version 5.6

http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3

[此处图片未下载成功]

[此处图片未下载成功]

Introductory Manual

[此处图片未下载成功]

Fig.

[此处图片未下载成功]

3.27 - Click on a node with the right mouse button and specify a name in the dialog box. When you exit the window in Fig.  3.27 by clicking OK

[此处图片未下载成功]

, the circuit is updated as shown in Fig.

.28 and the node dot turns red. All node names are forced left adjusted, and as a general rule in

[此处图片未下载成功]

the ATP simulation, capital letters should be used. ATPDraw does accept lower case characters in the node data window, however this “feature” should be avoided, in particular if the node is connected with electrical sources.

.  3.28 - Click on a node with the right mouse button and specify a name in the node data

. The name ‘NEG’ will be assigned to all nodes visually connected.

.29 - Click on a node withhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 the right mouse button and check the Ground box indicating that Fig.

node is connected with the ground reference plane of the circuit. The button right to the

check box can be clicked to choose the ground symbol orientation.

ground symbol is drawn at the selected node when you exit the window as Fig.

[此处图片未下载成功]

3

[此处图片未下载成功]

.30 shows. The nodes not given a name by the user will automatically be given a name by ATPDraw, starting with XX for single phase and X for 3-phase nodes followed by a four-digit number. Nodes with a name specified by the user are drawn in a red color and the disabled check box User Named in their node dialog box is checked. Fig.  3.30 shows the final step in the drawing process.

.  3.30 - Click on the voltage source with the right mouse button and specify the node name.

version 5.6   47

Introductorhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3y Manual

.5.2 Storing the project file on disk

can store the project in a disk file whenever you like during the building process. This is done in the main menu with File | Save (or Ctrl S). If the current project is new, a Save As dialog box appears where you can specify the project file name and location on the disk. Two different styles of the Save As dialog boxes are available, depending on the Open/Save dialog setting in the Tools | Options | General menu: a Windows 9x standard dialog box and a Windows 3.1 style. The default extension is .acp in both cases and it is automatically added to the file name you enter.

the circuit is saved, the name of the disk file appears in the header field of the circuit window. Then if you hit Ctrl S or press the Save circuit icon in the Toolbar, the circuit file is updated immediately on the disk and the Modified flag in the status bar disappears. The Fihttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3le   Save As option or the Save As Toolbar icon allows you to save the circuit currently in use under a name other than that already allocated to this project. There are no project file name restrictions.

.5.3 Creating the ATP input file

ATP-file describes the circuit according to the ATP RuleBook. You can create this file by selecting Sub-process|Make ATP File command in the ATP main menu. The ATP-file is regenerated whenever you execute the run ATP command (or press F2). In the latter case the process is hidden for the user. By default the ATP file inherits its name from the project file.

, before you create the ATP input file or run the simulation, you must not forget to specify the miscellaneous parameters (i.e. parameters, that are printed to the Misc. Data card(s) of the ATP input file). The default values of these parameters are given in the ATPDraw.ini file. Changing these default values canhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 either be done in the ATP | Settings | Simulation sub-menu for the current project, or under the Tools | Options | View/ATP | Edit settings | Simulation for all new ATPDraw projects created henceforth.

.  3.31 shows an example of the 1st miscellaneous data card settings of an ATP simulation (specifying time step, time scale of the simulation etc.). This window appears if you select the Simulation tab of the ATP | Settings dialog.

:

Time step delta T in sec.

End time of simulation Tmax in

.

Xopt=0: Inductances in mH.

Copt=0: Capacitances in μF.

main characteristic of the

(time domain or frequency

) can also be set on this page.

Help to get more information or

[此处图片未下载成功]

OK to close the dialog box.

simulation settings are stored in the

filehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3, so you should save the file

changing these settings.

.  3.31 - Simulation settings.

version 5.6

Introductory Manual

on the first integer miscellaneous data card of ATP can be changed under the ATP | Settings / Output page. The next ATP | Settings/ Switch/UM tab is the home of control flags required by statistical switching or universal machine simulations.

the Format page the user can

precision mode and the ATP-file

criteria. If you select the

page, the window shown in

.32 appears: Fig.

:

; Sorting by cards: First /BRANCH,

/SWITCH and then /SOURCE.

; Printed Number Width request is

. Width is the total column

of ATP printed output LIS-

, Space is the number of blanks

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ween columns. This is not a

choice.

other check boxes are unselected

.  3.32 - The ATP-file format menu.

create an ATP-file without starting the simulation you must select the Sub-process|Make ATP File in the ATP menu. This selection will start the compilation, which examines your circuit and gives node names to circuit nodes. Then a standard Windows’ Save As file window appears, where you can specify the name and path of the ATP-file. The same name as the project  with extension .acp file is suggested default. As the ATP file is sent to the ATP solver, the file name should not contain space characters. You can edit this file or just display it by selecting the ATP | Edit ATP-file menu. The ATP-file (Exa_1.atp) you have just created will be as follows:  BEGIN NEW DATA CASE

--------------------------------------------------------

Generated byhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 ATPDRAW  November, Thursday 5, 2009

A Bonneville Power Administration program

by H. K. H&#248;idalen at SEfAS/NTNU - NORWAY 1994-2009

--------------------------------------------------------

NUMBER WIDTH, 10, 2,

Example 1

Your first circuit C Rectifier bridge

dT  &gt;&lt; Tmax &gt;&lt; Xopt &gt;&lt; Copt &gt;

.E-5     .05

1       1       1       1       0       0       1       0

1         2         3         4         5         6         7         8

345678901234567890123456789012345678901234567890123456789012345678901234567890 /BRANCH

&lt; n 1&gt;&lt; n 2&gt;&lt;ref1&gt;&lt;ref2&gt;&lt; R  &gt;&lt; L  &gt;&lt; C  &gt;

&lt; n 1&gt;&lt; n 2&gt;&lt;ref1&gt;&lt;ref2&gt;&lt; R  &gt;&lt; A  &gt;&lt; B  &gt;&lt;Leng&gt;&lt;&gt;&lt;&gt;0

33.          1.                       http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3            0   NEG                        33.          1.                                   0   XX0031POS                  .01                                               1   POS   NEG                             1.E3                                   3   NEG   POS                  20.                                               3   VS    XX0021                      1.                                         0   VS    XX0021              300.                                               0

version 5.6  49

NEG   VA                   33.          1.                                   0

XX0031               33.          1.                                   0

/SWITCH

&lt; n 1&gt;&lt; n 2&gt;&lt; Tclose &gt;&lt;Top/Tde &gt;&lt;   Ie   &gt;&lt;Vf/CLOP &gt;&lt;  type  &gt;

VA    XX0031                                                                 0

XX0031  http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3                                                               0

NEG   VA                                                                     0

NEG                                                                          0

VA                                            MEASURING                1

/SOURCE

&lt; n 1&gt;&lt;&gt;&lt; Ampl.  &gt;&lt; Freq.  &gt;&lt;Phase/T0&gt;&lt;   A1   &gt;&lt;   T1   &gt;&lt; TSTART &gt;&lt; TSTOP  &gt;

VS     0     167.7       60.      -90.                           -1.        1.

/INITIAL

POS               75.

NEG              -75.

POS   NEG                             150.

/OUTPUT

BRANCH

SWITCH

SOURCE

INITIAL

OUTPUT

PLOT

NEW DATA CASE

Manual

.5.4 Running the shttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3imulation

the ATP simulation is supported in ATPDraw in a user friendly way. The user just has to press F2 function key to create an ATP input file with the current project file as input and run the simulation. ATP|run Plot (F8) starts the default plotting program and sends the pl4 file as parameter. The default commands that is executed when the user selects run ATP or run Plot under the ATP menu can be specified under the Tools | Options /Preferences tab as it has been described in section  2.6 of the Installation Manual.

.6 Multi-phase phase circuits

ATPDraw version 5 a node can have up to 26 phases (A..Z node name extension). This applies also to MODELS nodes. A more generalized Connection is introduced with a special handling between single phase and n-phase nodes. Transpositions will only take place through 3-phase connections. In this case the phase sequence will be further inherihttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ted throughout the circuit. Special ABC or DEF reference components found under from Probes&amp;3-phase in the Selection menu can be placed on the reference node. The actual phase sequence of the node is written at the top right of the Node dialog box or in the PHASE field in the Component dialog box as shown in Fig.  3.2 (after ATP|run ATP or ATP|Sub-process|Make node names). A special component SPLITTER is available for connections between 3-phase and single phase nodes. Some special restrictions apply to the splitter objects (found under Probes &amp; 3-phase in the component selection menu):

Connecting splitter objects together on the 3-phase side or with connections on the 1-phase

is permitted, but transposition/disconnection is not allowed.

If the name NODEA is given to what you know is phase A on the single phase side, ATPDraw

not accept this and adds its own A at the end, creating thhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3e node name NODEAA. The general rule is that ATPDraw takes care of the phase sequence! The best solution is to specify a node name on the 3-phase side only.

version 5.6

Introductory Manual

, label, and phase properties are given to the

[此处图片未下载成功]

Connection as well as the possibility to force node dots on. The connection can also be turned into a Relation (no node connection only

.33 visualization of flow of information drawn as a dotted line) by the Relation check box. Fig.

the Connection dialog that appears after a right click on the connection and automatically when the user draws a connection between a single phase and a multi-phase node. The Phase index field is only enabled for single phase connections. 0-@ is used for connections between two single phase nodes.

[此处图片未下载成功]

Fig.  3.33 - The Connectionhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 dialog box.

.  3.34 illustrates the various options for (3-phase in this case) multiphase circuits in ATPDraw. The flag DEF set at the source node to the left. Consequently, all connections marked with 1 will carry the phase D and so on. The color of the connections is user selectable as shown in Fig.  3.33, but as default the color and phase sequence are inherited when the user clicks on one connection to draw a new one. Connections will inherit the phase number.

.  3.34 -  Illustration of various phase options in ATPDraw.

typical example of  connecting a single phase node to a 3-phase node is the case of a single phase ground fault as shown in Fig.  3.35. Place the switch, then draw the connection between the three phase node and the single phase node. Select 1-A to ground phase 'A' (regardless of transpositions involved).

version 5.6  51

Introductorhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3y Manual

.  3.35 -  Single phase ground fault.

-phase nodes are first of all important for MODELS and GROUPS. An n-phase connection could also be useful just to clear up the circuit drawing. As an initial example a 6-phase connection is shown in Fig.  3.36 for communication between a 6-pulse thyristor bridge and its control circuit. This will make the drawing much easier to read.

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

.  3.36 -  Communicating a 6-phase signal between a thyristor bridge and its control circuit. All n-phase nodes have only 5 characters available in the Node dialog box. ATPDraw adds the extension A, B and C (etc.) at the end of the node name. By default, the phase sequence is ABC; the first data card uses A, the second B and the last C. The only way to change the phase sequence is to use the available transposition objects (Transp1 - Transp4) sehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3lectable under Probes &amp; 3-phase in the component selection menu. Only 3-phase nodes can be transposed.

.  3.37/a - Illustrative three-phase circuit.

.  3.37/b - Equivalent ATPDraw circuit (Exa_2.adp).

[此处图片未下载成功]

ATPDraw version 5.6

Introductory Manual

circuit shown in Fig.

[此处图片未下载成功]

3.37 was built up in the same way as your first circuit. You can note that

[此处图片未下载成功]

connections between the three phase nodes appear to be thick. The circuit contains 3 special objects, the already mentioned transposition object (in this case from ABC to BCA), a Splitter object, which splits three phase nodes into three single-phase nodes and an ABC reference object. Fig.  3.38 shows the Node data dialog for a single phase and a three phase node.

.  3.38 – Default node names and phase sequencehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3. Top: single phase node. Bottom: 3-phase.

version 5.6  53

[此处图片未下载成功]

ATPDraw version 5.6  55

Manual         ATPDraw version 5.6

Reference Manual

part of the manual outlines all menu items and program options, and gives an overview of the supported ATP components, TACS, and MODELS features.

has a standard Windows user interface. The Main window of the program is shown in  Fig.  4.1. The Main menu, the Circuit window and the Component selection menu are the most important items of that window. Elements of the Main menu and supported ATP components in the Component selection menu will be referenced in this part of the manual.

.1 Main window

menu Tool barCircuit window

Window

modeStatus bar with menu option hints  http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3  Component

menu

.  4.1 -  Components of ATPDraw's main window.

you are unfamiliar with the use of ATPDraw, read the Introductory Manual to learn how to create a circuit or the Advanced Manual to learn how to create a new object in ATPDraw. The Introductory Manual starts with the explanation of operating windows and the mouse in ATPDraw, and shows how to build up a circuit and how to create an ATP-file to be used as input for a subsequent transient simulation.

version 5.6  57

Reference Manual

.2 Main menu

.2.1 File

field contains actions for input/output of ATPDraw projects. Selecting the

item in the main menu will result in a popup menu shown in Fig.  4.2.

.  4.2 - File menu.

.2.1.1 New

this menu item will open a new empty Circuit window. ATPDraw supports to worhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3k on several circuits simultaneously and copy information between the circuits. The number of simultaneous open windows is limited only by the available MS-Windows resources. The circuit window is much larger than the actual screen, as it is indicated by the scroll bars of each circuit windows.

.2.1.2 Open

menu performs a Windows standard Open dialog box. In this window the user can select a project file and load it into ATPDraw. Short key: Ctrl O. The default directory is the previously used directory and the first time the dialog is used the Project Folder set under Tools|Options/Files&amp;Folders (initially read from ithe ATPDraw.ini file) is suggested.

can read both circuit (.cir) files created by an earlier version of the program and project files (.acp and .adp). When opening a project file all data are stored in memory and no files are written to disk. The circuit files anhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3d project files are binary data files.

Open/Save dialog box is used for several different selections in the main menu. An alternative MS-Windows 3.1 style is also supported. There is a check box in the Tools | Options | General tab to switch between the two supported alternatives.

.2.1.3

[此处图片未下载成功]

Save

this menu item will save the project in the active circuit window into a disk file. If the name Noname.acp is shown in the circuit window a Save As dialog box will be performed, where the user can specify a new name for the current project file name. Short key: Ctrl S.

version 5.6

Reference Manual

.2.1.4 Save As

project in the active circuit window is saved to disk under a new name. The name of the file can be specified in the Save As dialog, which is similar to the Open Project. This command allows thttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3he user to save the project under a name other than that is already used. ATPDraw can read circuit files (.cir) created by earlier program versions, but the Save As command supports only the newest file format. The default extension of the project files on disk is (.acp).

.2.1.5 Save All

all modified projects to disk under their own project file names. If one or more open projects still have not got a name (Noname.adp), it will be requested in a Save As dialog boxes successively.

.2.1.6 Close

the active circuit window. If any changes to the circuit have not been saved yet, the user will be warned as shown in Fig.  4.3 to confirm before the circuit is closed. If the project has been modified, the user is given a chance to save it first.

.2.1.7 Close All

all circuit windows. If a project has been modified since the last save operation, a confirmhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ation dialog will be prompted giving a chance for the user to save it first.

.  4.3 - Confirmation prevents the

of unsaved project data.

.2.1.8 Import

command inserts a circuit from disk file into the active circuit window contrary to the Open command, which loads the circuit into a new circuit window. Selecting this menu will result in an Import Project dialog box where the user can select the file to load. The imported circuit appears in the circuit window as a group in marked moveable mode. Existing node names will be kept or rejected upon the selection of the user.

.2.1.9 Export

the selected objects of the active circuit to a disk file. Same as Save As, but only the selected objects (marked by a rectangular or polygon area) of the circuit are written to the disk file.

.2.1.10 Save Metafile

the selected objects of the active circhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3uit to a disk file in Windows metafile (.wmf) format. If no objects are selected, the entire circuit window content is written to disk. This way even graphics of large circuits can be exported to other applications without loss of resolution seen on

version 5.6  59

Reference Manual

screen when the Zoom option is used to fit the circuit to the screen size. Metafiles created by this command can be imported as picture into other applications (like MS-Word or WordPerfect) having filter available for this format.

.2.1.11 Print

the graphics on the currently selected printer.

.2.1.12 Printer Setup

and setup the printer.

.2.1.13 Exit

command closes all open circuit windows of ATPDraw. User will be asked to save any modified circuits before the application is terminated.

.2.2 Edit

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3rmenu contains the various edit facilities of circuit objects in

. The Edit popup menu is shown in Fig.  4.4.

object or group of objects must be selected before any edit

can be performed on them. If the user clicks on an object

the left mouse button in the circuit window the icon of the

will be enclosed by a lime colored frame indicating that it is

.

.  4.4 - Edit menu.

.2.2.1 Undo/Redo

Undo command cancels the last edit operation. The Redo cancels the last undo command. Short key for Undo/Redo:

[此处图片未下载成功]

Ctrl Z and Ctrl Y. The number of undo/redo operations depends on the Undo/redo buffers: setting on the Preferences tab of the Tools | Options menu. Default value is 10. Almost all object manipulation functions (object create, edit, delete, move, rotate, etc.) can

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ar60

version 5.6

Reference Manual

undone (or redone). Changes made to the circuit data in the component dialog box are also supported by the Undo/redo functions (this included also the extensive data in LCC, BCTRAN, XFMR). These functions also update the circuit's Modified state in the status bar to indicate that the circuit has been modified. During an undo operation, the modified state is reset its previous value. After Save/Save As the Undo/Redo buffer is cleared.

.2.2.2 Cut

the selected objects to the Windows clipboard and deletes them from the circuit window. The objects can later be pasted into the same or other circuit windows, or even other instances of ATPDraw. Short key: Ctrl X.

.2.2.3 Copy

selected objects are copied to the clipboard. Short key: Ctrl C. A single marked object or a group of objects can be copied to the clipboard. This commhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3and unselects the selected objects.

.2.2.4 Paste

contents of the clipboard are pasted into the current circuit when this menu item is selected. Short key: Ctrl V. The pasted object or objects appear in the current window in marked moveable mode. The node names are deleted when pasting components.

.2.2.5 Duplicate

the selected object or a group of objects to the clipboard and then duplicates them in the current circuit window. Duplicated objects appear in the current window in marked moveable mode. Short key: Ctrl D.

.2.2.6 Delete

objects are removed the from the circuit window. Short key: Del.

.2.2.7 Copy Graphics

selected objects are copied to the clipboard in Windows Metafile format. This way graphics of selected objects can be exported to other Windows applications. Short key: Ctrl  W.

.2.2.8 Select

menu has five sub-menus:://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3r: To cancels the object selection. Short key: Ctrl  N.

: Select all objects in the current circuit window. Short key: Ctrl  A.

: Enables object selection by a polygon shaped region. Short key: Ctrl  I (or    double-click with the left button in an empty region of the circuit window).  by Properties: Enables selection by objects' support file name or order number (see      below). Short key: Ctrl  P.

: Select component that overlap other components. First ATP|run ATP must

chosed to identify overlapping component.

selected object or group of objects can be subject of the most editing operations: Move (click left button, hold down and drag), Rotate/Copy/Duplicate/Delete or Export (in the File menu). To unselect a group, select None, or just click with the left mouse button in an empty space of the circuit window.

Inside mode, the mouse cursor icon chttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3hanges its style to a pointing hand and moves to the

version 5.6  61

Reference Manual

of the circuit window. The current action mode also changes to MODE:GROUP in the status bar. To draw a polygon around a group of objects move the cursor to the starting location and click the left mouse button. Then release the button and a rubber band line will be drawn between the starting point and the current mouse cursor location. And so forth: left click to create corners, right to complete the polygon. All objects with midpoint inside or connections with both endpoints inside the polygon will be included in the selection.

the by Properties selection mode the group of components can be selected by their type and/or Order number. The type here is the name of the support file and the Order number is the identifier specified in the component dialog box.

availahttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ble component Names and Order numbers are listed in two

.5. When you click on OK the combo boxes as shown in Fig.

with the selected order number and/or support file name

selected. Then all kinds of edit operation can be performed on

group (copy/paste, copy graphics, rotate, edit, grouping etc.).

[此处图片未下载成功]

Fig.  4.5 - Selecting objects by name or group no.

.2.2.9 Edit Text

menu is used to insert a new circuit text. In addition the

of texts, component labels or node names is

in this mode. An alternative to this last property is

press the Alt key. This is beneficial when texts, labels or

names are drawn overlapped by components. If you

on existing texts, labels or node names you can edit the

directly on screen or move them (click and hold).  Short://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3: Ctrl T.

.6 – The circuit text dialog box. It appears after a right Fig.

(or left double) on a circuit text.

the Edit Text menu item, the mouse cursor style will change to a pointing hand and forced to stay within the circuit window. The action mode indicator in the status bar will also change to MODE: EDIT TEXT. You can leave this mode by pressing the ESC key.

.2.2.10 Rotate R/L

command rotates the selected object(s) 90 degrees clockwise (R) counter-clockwise (L). The operation Rotate R can also be performed by clicking the right mouse button inside the selected group. Short key: Ctrl   R/L.

version 5.6

Reference Manual

.2.2.11 Flip

the icon left to right. For vector icons the texts are not flipped. This option is useful for instance for transformers since the primary and secondary nhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ode will be swapped. Short cut Ctrl F.

.2.2.12 Copy Graphics

the selected graphical content to the Windows clipboard in MetaFile format.

.2.2.13 Rubber Bands

this option is checked, connections with one endpoint inside a selected region and one outside are treated as a rubber band between the selected group and the rest of the circuit. Short key: Ctrl   B. This command does not work for short cut single component selections: e.g. left click on several components while the Shift key is pressed, because this way no connections are selected.

.2.2.14 Compress

command will replace a group of selected objects with a single icon having user selectable external data and nodes. ATPDraw supports real grouping or single icon replacement of sub-groups in unlimited numbers of layers. The process requires a group selection first. The Compress dialog box (see Fig.  4

[此处图片未下载成功]://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3

.7/a) appears where the user designs the new group object. The user can later modify a compressed group by selecting it and click Compress once more.

the Compress dialog box the user can specify the external data and nodes of the compressed circuit. The selected data and nodes appear as input to the group object that replaces the selected circuit and their values are automatically transferred. A nonlinear characteristic common for up to 3 components can also be selected as external data. Only the members of the group are shown in the Compress process and moved to the middle of the circuit window.

.  4.7/a - The Compress dialog box.

Objects: all the components in the group are listed with their name followed by their label. When the user clicks on one of the components' name the selected component is drawn in a lime

version 5.6  63

Reference Manual

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3par

in the circuit window. Its data and nodes also appear under Available: starting with data/node name and followed by their names and values. Here the user can select a parameter and click on the &gt;&gt; button to transfer it to the Added to group: list. Data and Nodes in the Available list that already are members of the Added to lists will be displayed there with a lime colored text. Selected node in the Available list will be drawn in a lime color. All data and nodes listed in the Added to group: will be an external attribute of the new group object. The selected external nodes are drawn enclosed by a red circle. The position of the external nodes are selected in the Position combo box. Positions 1-12 will be on the traditional border as shown in the graphic below, while position 0 will enable the user to specify positions in the Pos.x and Pos.y fields. You can change the Added to group: names by double clickinghttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 on them. Data with the same name are treated as a single data in the component dialog box (Fig.  4.7/b). Selected data and nodes can also be removed from the Added to group: by clicking on the &lt;&lt; button. The Keep icon check box can be used when Recompressing a group in cases where the user wants to keep its icon.

all other components, the group object is limited to 64 data and 32 nodes. When you later open

[此处图片未下载成功]

the component dialog box of the group-object, the selected data values and node parameters will appear as input possibilities. The values will automatically be transferred to the group members as

.7/b. Node that the 8 selected data are represented by two external data in Fig. shown in Fig.

.7/b since the names are duplicated.

.7/b - Component dialog box for a sub-group object. Fig.

.2.2.15 Extract

is the reverse operation ofhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 Compress. The group is extracted on the current circuit layer. To perform the operation, a compressed group (and only one!) must be selected first.

.2.2.16 Edit Group

command shows the group content. Short key: Ctrl G. The group is shown in a separate window. To perform the operation a compressed group (and only one!) must be selected first. It is possible to edit the group in a normal way, except deletion of the reference components. I.e. components having been referenced in one of the Added to group: lists cannot be deleted. If the

ATPDraw version 5.6

Reference Manual

tries a &quot;Marked objects are referenced by compressed group...&quot; warning message appears.

.2.2.17 Edit Circuit

the circuit to which the current group belongs. Short key: Ctrl   H. Actually the grouping structure can be taken as a multi-layer circuit, where the Edit Group brhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ings the user one step down in details, while Edit Circuit brings one step back. The group object (single icon replacement of objects) acts as the connection between the layers and transfers data between them.

.2.2.18 Comment...

a comment dialog box, where three text lines can be entered. These comments serve as a commentary section for the circuit in the header section of the .atp file. Selecting the Comment Line option checked in the View menu will display these comments at the bottom of the circuit window, as well. This menu also enables the user to change the circuit comment if it already exists.

.2.3 View

menu provides options for displaying and controlling the visibility of user interface and circuit window objects. The menu items are shown in Fig.  4.8.

.8 - View menu. Fig.

.2.3.1 Status Bar

bar on/off at the bottom of the main http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3window The status bar displays status information about the active circuit window. The mode field on the left hand side shows which mode of operation is active at present. Possible modes are:

Normal mode. Indicates no special type of operation.

.END  Indicates the end of a connection. The program is waiting for a left mouse

click to set the end-point of a new connection. To cancel drawing a

, click the right mouse button or press the Esc key.

a text edit mode. Add a new circuit text or favour text selection

(circuit text, labels and node names). Enter this mode also via the Alt key.

region selection. Double clicking the left mouse button in an

space of the active circuit window enables you to draw a polygon

region. To finish the selection click the right mouse button. Any

within the selehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3cted region is then marked for selection. To cancel

[此处图片未下载成功]

region selection, press the Esc key.

the start of relation drawing when the TACS | Draw relation was

EDIT TEXT  GROUP  INFO.START   ATPDraw version 5.6

Reference Manual

in the component selection menu. Clicking the left mouse button to

the drawing of a new relation. Relations drawn as blue connections,

do not influence the connectivity of components.

.END  Indicates the end of a relation. The program is waiting for a left mouse

to set the end-point of a new relation. To cancel drawing a relation,

the right mouse button or press the Esc key.

field to the right of the mode field displays the modified status of the active circuit. As soon as you alter the circuit (moving a label, deleting a connection, inserting ahttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 new component, etc.), the text Modified will show up to indicate that the circuit needs saving. The field will be empty when you save the circuit or undo all modifications. Note that the number of available undo buffers is  limited (default value is 10, but can be increased on the Preferences tab of the Tools | Options menu). In the default case, if more than 10 modifications are done, the field will indicate a modified status until you save the circuit.

rightmost field of the status bar displays the menu option hints and Drag-over information.

.2.3.2 Comment Line

or hides the comment line at the bottom of the active circuit window.

.2.3.3 Toolbar customize

toolbar can be customized by the user.

description of the user defined toolbar

stored in the file Toolbar.cfg located

with the ATPDraw.ini file in the

%APPDATA%direchttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3tory. The

and handling of the Toolbar.cfg is

by Delphi and there might be

(main menu items

/wrong) when changing ATPDraw

. Shutting down ATPDraw and

the Toolbar.cfg file will fix this

(but reset the toolbar to the default

). All main menu items (called

) can be member of the toolbar.

[此处图片未下载成功]

From the Customize dialog  shown in Fig.

.9 the user can drag items/actions on/off

[此处图片未下载成功]

the toolbar.

.  4.9 – Customize toolbar dialog.

default toolbar content is:

version 5.6

Reference Manual

the left the tools are:

Menu

File|New Open

|Open

File|Save

As File|Save As

File|Import

File|Exphttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ort

Edit|Undo

Edit|Redo

Edit|Cut

Edit|Copy

Edit|Paste

|Duplicate

|Edit text

|Select|All

|Rotate-R

|Rotate-L

|Flip

|Refresh

|Zoom in

|Zoom

|run ATP

|run Plot  Shortcut  -- CTRL O  CTRL S --  -- -- CTRL Z  CTRL Y CTRL X CTRL C CTRL V CTRL D CTRL T   CTRL A CTRL R CTRL L CTRL F CTRL Q NUM   NUM –  F2  F8 Description Open an empty circuit file. Loads a circuit file into a new window. Contains also a dropdown with the five recent opened projets. Saves the active circuit window to the current project file. Saves the active circuit window to a new project file. Inserts a stored circuit into the current circuit. Export the selected circuit to an external project file. Undo the previous operation. Redo the previous undo operation. Copy the currenthttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 selected circuit to the clipboard and then delete it. Copy the current selected circuit to the clipboard. Paste the ATPDraw-content from the clipboard into the circuit. Copy Paste. Go into Edit text mode for adding and selecting text. Required to add new text to the circuit window. Select the entire circuit. Rotate 90 deg. clock-wise. Rotate 90 deg. counter clock-wise. Flip left-to-right. The nodes changes postion. Vector text is not flipped. Redraw circuit. Zoom in 20 %. Zoom out 20 %. Make node names   write the ATP file  run ATP by executing the ATP command (Tools|Options/Preferences). Plot  Executed the Plot Command (Tools|Options/Preferences) and send

current PL4 file as parameter.

the right of the toolbar comes two items for controlling the zoom and the node sizes.

.2.4 Zoom In

the objects in the active circuit window by increasing the current zoom factor by 20 phttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ercent. Short key:   (plus sign on the numeric keypad or &quot;=/ &quot; alphanumeric key).

.2.4.1 Zoom Out

the icon size in the active circuit window by 20 percent. Short key: - (minus sign on the

[此处图片未下载成功]

numeric keypad or the &quot;-/_&quot; alphanumeric key).

.2.4.2 Refresh

command redraws all objects in the active circuit window. Short key: Ctrl Q. This command can also be activated by clicking the Toolbar icon:

.2.4.3 Set Circuit Font

you to select a font type and size for the node names and labels on the screen (and also for the metafile export). The default font is MS Sans Serif, regular, 8 pt size. This also becomes the default font for circuit text, but this can be adjusted individually.

.2.4.4 Options

this menu item will bring up the View Options dialog box. The View Options dialog can be used to control the visihttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3bility of the objects in the active circuit window.

version 5.6  67

Reference Manual

.10 - View Options dialog box. Fig.

default, all objects except node names are visible. The meaning of options assumed checked (;) are listed below:

All standard and user specified components are displayed.

All TACS components are displayed.

All MODELS components are displayed.

All connections (short circuits between nodes) are displayed.

All relations (to visualize connections between Fortran statements and

objects) are displayed.

Component labels are displayed on the screen.

dots  Node and connection end-points are displayed as filled circles.

names  Node names are visible on the screen (overrides the Display attribute of the

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3Node data window). This option is useful after a Make Names selection in

ATP menu.

over info List information about the component (name, number of data and nodes)

the mouse cursor. No clicking is required. Can slow down the

in case of large circuits.

color default Components and node dots are drawn with a red color until the component

node is opened for the first time.

branch output Small U/I symbols indicate the selected branch output requests. Branch

requests can be specified in most of the component dialog boxes.

circuit  Components can not be selected and moved only opened for input.

accept the current view options and return from the dialog, select the OK button. To set and view new options without returning, select the Apply button. If you want the current settings be applied to all current and future cihttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3rcuit windows, select the Apply All button before you exit the dialog box (this saves the selections to the ATPDraw.ini file).

version 5.6

Reference Manual

[此处图片未下载成功]

.2.5 ATP

ATP menu provides options to create, display and modify the ATP

files and to set circuit specific ATP options (e.g. ΔT, Tmax)

running the case by the run ATP command or the F2 function

. From this menu all output requests can be managed and the ATP

LIS files edited and inspected. The Find node and Find next node

tool is also available here. The Optimization module works

a cost function and perform multiple ATP runs. The Line Check

calculate sequential parameters of transmission lines and sub-

. Other components of the ATP-EMTP package (e.g. pre- and

-processors, http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3supporting programs and utilities) can also be launched

this menu. Besides the default commands, the user can add

commands (e.g. Run PlotXY / Run Analyzer / Run PCPlot /

TPPlot, etc.) to the existing program items, which are listed

below the Edit commands...as shown in Fig.  4.11.

.  4.11 - The ATP menu.

.2.5.1 Settings

the ATP Settings... dialog box several options for the active circuit window can be specified. These settings are used when ATPDraw generates the ATP input file. Options are sorted in six tabs, such as the Simulation and Output for the miscellaneous data card settings, Format

[此处图片未下载成功]

for specification of data-card sorting options and miscellaneous request, Switch/UM for statistical and Universal Machine studies, and Variables for specification of global $Parameter and Pocket Calculator options.

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3r

settings

type: Select between the

methods supported by

:

Time domain

Frequency Scan

Harmonic Frequency Scan (HFS)

domain

T: Time step of simulation in

.

: End time of the simulation in

.

: Inductances in [mH] if zero;

, inductances in [Ohm]

Xopt as frequency

: Capacitances in [mF] if zero;

, capacitances in

[Ohm] with Copt as frequency. Freq: System frequency in Hz.

Frequency: when checked the SYSTEM FREQUENCY request card is written in the ATP-file. The ideal transformer component uses this frequency.

scan

Frequency scan is selected the FREQUENCY SCAN option of ATP is enabled.  Fig.  4.12 - Simulation settings.

version 5.6  69

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3arReference Manual

: Starting frequency for the frequency scan

: Ending frequency for the frequency scan

: Frequency increment. Leave 0 for logarithmic frequency scale

: Number of frequency points per decade in logarithmic scan

Frequency Scan (HFS)

HFS will run the ATP data case so many times as specified in the Harmonic source component dialog box (see chapter  4.11.12). The frequency of the harmonic source will for each ATP run be incremented. The power frequency specification is mandatory for HFS simulations.

Frequency scan or HFS is selected the user must specify which component of the solution to print out:

[此处图片未下载成功]

Magnitude only: Default request

&amp; Angle: Results are printed in POLAR

&amp; Angle &amp; Real/Imag: Both POLAR and RECTANGULAR

/Imag: RECThttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ANGULAR output request. Other combinations are illegal and are

by button logic.

control

freq.: Frequency of LUNIT6

within the time-step loop. For

, a value of 500 means that

500thsimulation time step will

printed to the LIS-file. This

controls ATP's 1st misc. data

IOUT

freq.: Saving frequency of the

data to the .pl4 output

. A value of 5 means for example,

every fifth time step will be

to the PL4-file. This option

ATP's 1st misc. data

IPLOT

. 4 .13 - Output request tab.

output: If checked ATPDraw sets the 1st misc. data parameter ICAT=1 in the ATP input file which results in a .pl4 output file.

: Controls the dumping of EMTP memory to http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3disk at the end of simulation if START AGAIN request is specified. If checked indicates memory saving.

-detect simulation errors: If this option is selected, ATPDraw will analyze the output LIS-file of ATP following the completion of the simulation. If the specified Detect string is found, the corresponding section of the file is displayed in a text editor window. This feature helps the user to recognize the simulation errors/warnings generated by ATP during the time step loop or input data interpretation. The string or strings, which makes this function work, are user selectable and activating at least &quot;Error&quot; and &quot;Kill code&quot; are highly recommended.

connectivity: If checked connectivity table (description of the topology of the circuit) is written to the LUNIT6 output file. This option controls ATP's 1st misc. data parameter IDOUBLE. If unchecked, no such tablehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 is written. Output settings

version 5.6

Reference Manual

-state phasors: If checked complete steady state solution (branch flows, switch flows and source injection) is written to the LUNIT6 output file This option sets ATP's 1st misc. data parameter KSSOUT=1. If unchecked, no such output is produced by ATP.

values: If checked, extrema of each output variables will be printed at the end of the LIS-file. This option controls ATP's 1st misc. data parameter MAXOUT. If unchecked, no such output is produced by ATP.

printout control: Additional control for the frequency of LUNIT6 output within the time-step loop. If checked, the 1st misc. data parameter IPUN is set to -1 and a 2nd misc. data card will appear in the ATP input file. Parameters KCHG and MULT control the breakpoints and the new Print freq. value. If unchecked, IPUNhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 is set to 0 and LUNIT6 printout frequency will be constant throughout the simulation.

settings

[此处图片未下载成功]

The Format settings page contains four buttons for setting of ATP input file data format, a button for controlling the auto path generation and several other buttons for miscellaneous request cards. The Additional button supports the user to insert any request card or text strings in the ATP-file on precise location.

.  4.14 - ATP-file format settings.

request  Sorting Sorting by cards: The sequence ofATP input data follows the default sequence of / data sorting cards (i.e. BRANCH cards are written first, followed by SWITCH cards and the SOURCE cards). Sorting by order: The Ordernumber that can be specified in the component dialog box for each object determines the sequence of cards. The lowest Order number comes first. Sorting by X-pos: The leftmohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3st object in the circuit window is written first. Any combination of the three different sorting mechanisms can be specified. Force high resolution: Use $Vintage, 1 (if possible), for high precision data input.

$Prefix and $Suffix cards: If this option is checked, ATPDraw will assume that all $Inlude files (User Specified , LCC, external nonlinear characteristics, and Windsyn components) are located in the Result Directory and have the extension '.lib'. Two cards $Prefix and $Suffix will the be inserted into the ATP file and the $Include commands are specified without path and extension. This should be a preferred choice as this path and extension generally are used and that increased readability of the ATP file is obtained this way.

$PL4 Comments: If checked, ATPDraw writes the circuit comments in a $BEGIN PL4 COMMENTS...$END PL4 COMMENTS block. This may result in an error for some (older?) ATPhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 versions.

Exact Phasor Equivalent card: If checked, ATPDraw writes an EXACT PHASOR EQUIVALENT request in the ATP-file. This is recommended for Frequency Scan simulations including constant and distributed parameter overhead lines.

version 5.6  71

Reference Manual

TACS HYBRID card: Checking this button forces TACS HYBRID .. BLANK TACS to be written to the ATP-file. Useful when TACS objects are only present inside a User Specified Object.

Number width

[此处图片未下载成功]

: Enables the PRINTED NUMBER WIDTH request card, which controls the printout of the LUNIT6 device (output LIS-file). Width: is the total column width of printed output including blanks separating the columns. Space: is the number of blanks between columns of printed output.

/UM settings

study

study: Studyhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 with statistic

study: Study with systema-

switches

: Number of simulations. This

influences ATP's 1st misc. data

NENERG. ATPDraw sets the

sign of NENERG: i.e. &gt;0 for statistic or &lt;0 for systematic switch

.

controls

: If 1, printout of all switch closing/opening time appear in the output LIS-file. No such printout if the parameter is set to 0.

:Extra random delay using DEGMIN, DEGMAX and STATFR in STARTUP.

values are:

: Extra random delay for all switches.

: No random delay.

: Extra random time delay added to all closing switches.

: Extra random time delay added to all opening switches.

: Select probability distribution function of subsequent switching operations. Zero means Gaussian distribution and 1http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 means uniform distribution. IMAX: If 1, printout of extrema is written to the ATP output LIS-file for every energization. If 0 (zero), no such printout.

: Controls use of the random generator. A value of 0 implies computer-dependent random generator and a value of 1 means standard random generator. KSTOUT: If 0, extra printed (LUNIT6) output for each energization. Output of the time-step loop and variable extrema (if Extremal values is selected on the Output tab) will be printed. If -1, no such output.

: Repeatable Monte-Carlo simulations. Possible values are:

: Every simulation on the same data case will be different.

: Same result each time the data case is run on the same computer.

machines

the user specifies the global data for the Universal electrical machine models in ATP. The selections here apply to all universal machines in the  circuit.

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3Fig.  4.15 - Switch/UM settings.

version 5.6

Reference Manual

: Manual: Terminal quantities of all machines must be specified. Automatic: Initial conditions will be calculated by ATP. See section 9D1.5 for more details in the ATP Rule Book.

: Input variables are specified in SI units or Per unit (p.u.)quantities.

:

[此处图片未下载成功]

Compensation: The machine does appear to be a nonlinear element to the external network. Certain rules regarding connecting machines together must be followed. Inclusion of stub lines is often required. Preferred method.

: The machine does not appear to be a nonlinear element to the external network. This option is not available for single phase machines.

flow

the global variables of load flow

to RuleBook chapt. X.

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 Additional interactive output

load flow iteration.

Tabular printout for nodes

power constraints.

Maximum number of iterations.

500.

Buffer size convergence

, printout per line.

20.

Relative convergence

. Default 1/100.

Acceleration factor ref.

/dU. Default 2/10.

Acceleration factor ref.

/dTh. Default 2.5.

Voltage scaling factor. Use

.4142 to get rms values

. Zero=Unity.

=0: Constant acceleration

. =2 used also in

/DC26 examples.  4.16 – Global load flow settings. Fig.

Variables dialog box support the $PARAMETER feature of ATP-EMTP. The user is allowed to specify a 6-character text string instead of a numerical value in the component dhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ialog boxes as shown in

.17. A requirement Fig.

that property Param of

DATA is set to 1.

can be verified and

under Edit definitions

the component dialogs.

addition the data in

must not be

in subsequent

. This is the

for the phase angle

3-phase AC sources,

damping resistors of

version 5.6  73

Reference Manual

and capacitors, the advanced components LCC, BCTRAN, XFMR, Windsyn etc.

.17 - Using text string instead of variables in the RLC component dialog box. Fig.

numerical value can be assigned later to these text strings under Variables. The text strings (variables) specified by the user appear to the left and the user now has to assign their data values. This is done in free format in the column to the rihttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ght as shown by Fig.  4.18. Nested syntax (the Name is used in subsequent Value specifications) is allowed from version 5.6 as ATPDraw internally handles the variables as intermediate (a character 'I' is added to the Name and the request '$$' is added to the Value). The user can also add local variables. Users do not have to think about the number of characters in the final ATP-file since ATPDraw automatically adds

[此处图片未下载成功]

underscore characters to obtain the maximum resolution. A variable RES used both for high and low precision resistances will thus be declared twice with 3 and 13 underscore characters added. This process is hidden, but the result is seen in the final ATP-file after the $Parameter declaration. Also Models can utilize Variables and the default number of digits is set to 10 in this case. There is a limit in ATP on the number of internal variables.

variables RES and CAP are cirhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3cuit

(6 characters) while OMEGA is a

local variable. The ATP file becomes:

$PARAMETER

=10.*KNT $$

=TWOPI*50. $$

=RESI/OMEGAI $$

___=RESI

___=CAPI

$PARAMETER

is the simulation number (1..10 in this

).

! Always use a period  '.'

a number in the value field.

.  4.18 - Setting values to text strings

support some special syntax for loop control (variables as function of the simulation number KNT). These are:

=@[a b c … n]

run (KNT=1): MyVar=a

run (KNT=2): MyVar=b

...

item and beyond (KNT &gt;=n): MyVar=n

characters '@[' are used to identify this format. Space or comma can be used to separate the numbers (integer or floating point).

=@FILE Filhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3eName Col

'@FILE' is the keyword, FileName is the name of a text file assumed stored in the ResultDirectory (same as final ATP file) (enclose the file name within &quot; &quot; if it contains space), and Col is an

version 5.6

Reference Manual

parameter identifying which column in the text file to use. The text file can have integer or floating point values in free format space or comma separated. If Col is not specified the first column of the file is loaded. The length of the file does not need the match the chosen Number of Simulations.

run (KNT=1): MyVar=First value of column Col

run (KNT=2): MyVar=Second value of column Col

.

the '@[' and '@FILE' syntax requires a lot of intermediate variables and ATP puts a limit on this.

=@LIN Lo Hi

'@LIN' is the keyword. Creates a linear space. MyVar=http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3a*(KNT-1) b

=@LOG Lo Hi

'@LOG' is the keyword. Create a logarithmic space.  MyVar=10**(a*(KNT-1) b)

=@POW Lo Hi P

'@POW' is the keyword. MyVar = a*(KNT-1)**P b

=@EXP Lo Hi P

'@EXP' is the keyword. MyVar = a*P**(KNT-1) b

P ='e' this is replaced by exp(1)

and b are calculated based on Lo and Hi: First run (KNT=1) MyVar=Lo, Last run (KNT=Number of Simulations) MyVar=Hi. The last four options could easily be managed directly be the user.

[此处图片未下载成功]

user should normally not change the name of the variables listed by ATPDraw in the NAME column, but if you do you will be asked to take an Action regarding the old Variable still defined in the circuit, as shown in Fig.  4.19. The action can be to reset the parameter to zero or the default value or to assign a new variable name.

.  4.19 - Actions to take when http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3non-defined parameters are found.

version 5.6  75

Reference Manual

.2.5.2 Run ATP

the run ATP command at the top of the ATP menu will create the ATP input file (the project file name (with extension .atp) and the /ATP system folder are default, but changeable via Sub-process|Make ATP file). Then ATP is executed basded on the default ATP command (specified in the ATP field of the Preferences page under Tools | Options). The current ATP-file is sent as parameter to the ATP-EMTP. Note that users do not need to select Make Names and Make ATP File before running the simulation. These commands are internally executed before the ATP run. If the user needs to do manual changes of the ATP-file and run the modified case, use ATP|Sub-process|run ATP file. After executing ATP, ATPDraw examines the LIS-file and displays any error or warning messages if exist.

.2.5.3 Run http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3Plot

the Plot program (defined under Tools|Options/Preferences) with the current ATP file name and the extension .pl4.

.2.5.4 Sub-process

sub-menu contains the individual three parts of the run ATP command.

Run ATP file: Executes ATP and sends the current ATP file as parameters. This choice must be used if the user has manually modified the ATP file under ATP|Edit ATP file.

Make ATP file: Creates the ATP file from the circuit without executing ATP (but calls Make node names first). This choice must be used to change the current ATP file name and the Result Directory.

Make node names: Gives node names to all nodes in the circuit. Overlapping and/or connected nodes get the same name. Whenever a &quot;same name on different nodes&quot; or &quot;duplicate names on same node&quot; are found, ATPDraw produces a warning and the user is asked to confirm this operation. While ATPhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3Draw establishes the node names a Generating node names message is displayed in the middle of the current circuit window. Following Make Names, the node name and phase sequence attributes in the Component dialog box and in the Node data window will be updated. Make ATP file and run ATP perform this sub-process initially.

! All nodes will automatically receive names from ATPDraw, so the user should normally only give names to nodes of special interest, e.g. involved in output requests and displayed in the Output Manager.

.2.5.5 Output manager

Output Manager list “all” requested outputs in the data case in the order that they appear in the pl4 file. The sorting option of the components is taken into account. The Output Manager even goes into User Specified, Additional data cards and Windsyn components to find outputs requested there. There is a limit of 32 output requests per component (voltage&amp;http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3current counts as one). The sequence of the output is:

-Branch voltages and power

-Switch voltages and power

-Node voltages

-Switch currents and energy

-Branch currents and energy

-SM

-TACS

-MODELS

version 5.6

Reference Manual

-UM

launching the Output Manager it compiles the circuit to generate the node names and presents a list of the outputs as shown in Fig.  4.20. The Windows Manager is a stay-on-top window that lets the user go back to edit the circuit. Two additional features are available; Find and Edit. Both are linked to the current selected row in the grid. The Find button finds the involved component and displays it in the middle of the screen in a lime color. If necessary it goes down into groups to display internal components. The

[此处图片未下载成功]

Edit button brings up the inhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3volved

[此处图片未下载成功]

component’s input dialog where the user is allowed to edit the settings. However, the user has to leave the Output Manager and reopen it to actually refresh its content.

ATPDraw goes into User Specified components it lists the node names found in the expected columns. This could however be an argument in the $Include call, and this in not handled by ATPDraw.

.  4.20- Output Manager from Fig.  4.21 - Output Manager from an extension of

_9.acp Exa_12.acp as shown in Fig.  4.22.

the case of a statistical study (chosen under ATP|Settings/Switch) the Output Manager lists three additional columns as shown in Fig.  4.21. In the fourth columns in Fig.  4.21 the user can turn available output requests on and off for statistical tabulation. Only node voltages are on as default. In the sixth column the user can assign a group number to the http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3statistical output request and in the fifth column assign a scaling factor to this group. There is also a Preview button available in this mode that lets the user examine how the final statistical tabulation will look like. This text will appear under /STATISTICS in the final ATP file.

/STATISTICS

.MIDA  MIDB  MIDC  BEGA  BEGB  BEGC  ENDA  ENDB  ENDC

1.E6ENDA        ENDB        ENDC        BEGA        BEGB         CONT. -4        1.E6BEGC

version 5.6  77

Reference Manual

is one challenge related to SATURABLE TRANSFORMERS and the request of magnetizing branch outputs. This would require a very complicated identification of the transformer that is not handled in ATPDraw. The magnetization output is presented in the Output Manager (using an alias node name) but it is not possible to add this to a statistical tabulation.

[此处图片未下载成功]

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ar[此处图片未下载成功]

4.22 - Exa_12.acp requesting additional output (both side node voltages and arrester powers Fig.

energies).

.2.5.6 Edit ATP-file

selection calls a text editor, which enables the user to contemplate or edit the ATP-file. When the Edit File option is selected (or the F4 function key is pressed) a file having the same name as the active circuit file with extension .atp is searched for, and will be opened in the built in Text Editor as shown in Fig.  4.23.

.  4.23 - The main window of the built in text editor.

status bar at the bottom of the window displays the current line and column position of the text cursor, and the buffer modified status. Basic text editing facilities (Open/Save, Print, Copy/Paste, Find &amp; Replace) are supported. The default text font can be changed by selecting the Font option in the Character menu. A detailed description ofhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 all the available options can be found in the menu options help topic. The text buffer of this editor is limited to maximum 2 GB in

version 5.6

[此处图片未下载成功]

Reference Manual

[此处图片未下载成功]

. The user can specify his own favorite text editor (wordpad.exe, write.exe, notepad.exe) on the Preferences page of the Tools | Options dialog box. The right-click context menu offers 50 different request card templates via the Insert field..

Editor option in the Tools menu provides an alternative way of invoking this editor. In that case the text buffer will initially be empty.

.2.5.7 View LIS-file

selection calls the built-in text editor, which enables the user to contemplate the LUNIT6 output of ATP (often called as LIS-file). This file has extension .lis and can be found in the Result Directory (default the /ATP system folder) followhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ing a successful simulation. In certain cases when the simulation is halted by an operating system interrupt or a fatal error in the ATP input file (illegal file name, I/O-xx bad character in input field, etc.) the LIS-file does not exist and can not be displayed either.

.2.5.8 Find node and Find next node

Find node helps the user to find a node with a specific name in the circuit. You type in the node name in the Find node dialog. For multi-phase node you only type in the root name without phase extensions 'A'..'Z'. Find next node is used to proceed to the next node with the same name. Find node goes into groups as well, and (multiple) Edit|Edit circuit (Ctrl H) may be necessary to nagigate back into the main circuit.

.2.5.9 Optimization

use the optimization module there must be variables declared in the circuit and a cost function object must have been added to the circuit (MODELS|WriteMaxMin)http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3. The optimization module will change chosen circuit variables to optimize the cost function basen on either a Gradient Method, a Genetic Algorithm, or a Simplex Annealing method. This is further documented in the Advanced Manual, chapter 5.11.

.  4.24 – Finding the neutral grounding coil value giving resonance, Exa_18.acp.

.2.5.10 Line Check

, the user selects the line he wants to test and then clicks on ATP|LineCheck as shown in Fig.

.25 . Then the input/output selection dialog box shown in Fig.   4.26 appears.

version 5.6  79

Reference Manual

LineCheck feature in ATPDraw supports up to 3 circuits. ATPDraw suggests the default quantities. The leftmost nodes in the circuit are suggested as the input nodes, while the rightmost nodes become the output. The circuit number follows the node order of the objects. For all standardhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 ATPDraw components the upper nodes has the lowest circuit number. The user also has to specify the power frequency of the line/cable test. Finally, the user can check the Exact phasor equivalent button which will result in a slightly better results for long line sections.

.26 an ATP-file (/LCC/LineCheck.dat) is created and

[此处图片未下载成功]

When the user clicks on OK in Fig.

executed. For a 3-phase configuration 4 sequential data cases are created (Z , Y , Z0, Y0) while for a 9-phase configuration 24 cases are created (Z11 , Y11 , Z110, Y110, Z12…, Z22…, Z13…, Z23…, Z33…), since symmetry is assumed. Finally the entire LIS-file is scanned. The

[此处图片未下载成功]

calculated values are then presented in the result window shown in Fig.  4.25 . The user can switch between polar and complex coordinates and create a text-file of the result. The mutual data are presented on a separate page. Thttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3he unit of the admittances is given in Farads or Siemens (micro or nano) and the user can scale all values by a factor or by the length.

.  4.25 – Selecting a line.       Fig.  4.26 – Selecting the inputs and outputs.

series impedances are obtained by applying 1 A currents on the terminals while the output ends are grounded (the other circuits are left open and unenegized). For mutual coupling, 1 A is applied at both circuits. On the other hand the shunt admittances are obtained by applying a voltage source of 1 V at one terminal leaving the output end open. For mutual coupling, 1V is applied at one circuit while a voltage of 1E-20 is applied at the other.

attention must be paid to long lines and cables. This applies in particular to PI-equivalents. Usage of 'Exact phasor equivalent' is recommended, but is no guarantee of success. No attempt is made in ATPDraw to obtain a betterhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 approximation since the line/cable system to be tested in general is unknown. The mutual coupling in the positive sequence system is in symmetrical cases very small and vulnerable to the approximations made. Appendix 7.2 documents the calculation procedure.

version 5.6

Reference Manual

[此处图片未下载成功]

.  4.27 - Presentation of the results.

.2.5.11 Edit Commands...

feature enables to specify executable files (*.exe or *.bat) to run from the ATP menu. New commands will appear as menu items below the Edit Commands... After clicking on the New button of the dialog box as shown in Fig.  4.28, the user is requested to specify:

the Name of the command displayed under the ATP

name and path of the executable file(*.exe or *.bat),

Parameter is the file to send as parameter when

the executable file.://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3: No file sent as parameter

: A file open dialog box is displayed

the user can select a file

ATP: send the current ATP-file

PL4: send the current PL4-file

options can be selected by radio buttons. If

File is selected, ATPDraw performs an open dialog

, where the user can select a file name, to be sent as

when executing the command.

.  4.28 - Specifying your own executable commands.

you completed editing the batch job settings, click on the Update button and the new commands will be inserted into the ATP menu. This feature can be used for many different purposes in ATP simulation: e.g. running different ATP versions (Salford, Watcom, GNU-MingW32) within ATPDraw; running external post-processors like TPPLOT, PCPlot or PlotXY; or launching any other data assembler.

vhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ersion 5.6  81

Reference Manual

any other program options, the previous settings can be saved to the ATPDraw.ini file by using the Tools | Save Options command or by selecting the “Save options on exit” program options on the General page of the Tools | Options menu.

.2.6 Library

menu contains options for creating and customizing component support files. Support files contain definitions of data and node values, icon and help text. Circuit components in ATPDraw can be either:  1. Standard,

. User specified, or

. Model

component has a unique support file, which includes all information about the input data and nodes of the object, the default values of the input variables, the graphical representation of the object and the associated help file. Standard components has their support files stored in component inherit the properties from its shttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3upport file and the support file is not used anymore. Except for the help text of standard components. In order to define and use User Specified components a support file .sup is required. Models can optionally be managed without a support file since a default support &quot;file&quot; can be automatically created based on the Models text header.

components' support files can be edited in the Library menu. The user can create new MODELS and User Specified components as described in the Advanced Manual.

.2.6.1 New object

this menu the user can create new User Specified and Models Components.

.2.6.1.1 New User Specified sup-file

specified objects are either customized standard objects or objects created for the use of $INCLUDE and Data Base Modularization feature of ATP-EMTP. The Library|New Object|User Specified menu enables the user to create a new support file for a user specifiedhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 object or customize data and node values, the icon and the help text of an existing one.

files of USP objects are normally located in the /USP folder. The Edit Definitions dialog box opens with empty Data and Nodes tabs in this menu. Number of nodes and data must be in line with the ARG and NUM declarations in the header section of the Data Base Module (DBM) file. The number of data can be in the range of 0 to 64, and the number of nodes in the range of 0 to 32. Control parameters for the object data can be entered on the Nodes and Data pages of Fig.

.29.

the Data page of the Edit Object dialog box, control variables of the support file (one row for each object data) can be specified.

The name of the parameter. Used to identify the parameter in

Component dialog box. This name often reflects the

used in the ATP Rule Book.

value of http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3the parameter. Default

version 5.6

Units

/Max

12 character text string with the unit that appear in the Component dialog box. The units COPT and XOPT are defined keywords responding to the users choice of COPT/XOPT under the ATP|Settings/Simulation. Minimum/Maximum value allowed. Set equal to cancel range checking. If set equal to 1, a variable text string can be assigned to the data value. These values are assigned under ATP|Settings/Variables. Maximum number of digits allowed in the ATP-file. When high precision is checked, $Vintage, 1 is enabled and

[此处图片未下载成功]

Digits is split in two values for high and low precision.  Reference Manual

error message will appear in the Component dialog box if a parameter value is out of range. To cancel range checking, set Min=Max (e.g. set both equal to zero).

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db34.29 - Control page of a new user specified object. Fig.

name of the node. Used to identify the node in the Open Node

Component dialog boxes.

: 3-phase circuit number of the object. The number is used to handle

of 3-phase nodes correctly for objects having more

3 phases. Kind=1 for all nodes of single phase objects.

-phase nodes with the same Kind get the same phase sequence.

: 1st to 3rd phase

: 4th to 6th phase

: 7th to 9th phase   4: 10th to 12th phase

Circuit parameter has a different meaning for MODELS or TACS

nodes. It is used to specify the type of input/output.

node values:

: Current input node.

: Voltage input node.

: Switch status input node.

: Machine variable input node.

: TACS variable (tacs)

: Imaginary part of steady-state node vhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3oltage (imssv)

: Imaginary part of steady-state switch current (imssi)  Name:   On the Node page of the Edit definitions dialog box, the node attributes of the support file (one row for each component node) can be specified.

version 5.6  83

Output from other model. Note that the model, which produces

output, must be USEd before the current model. This can

done by specifying a lower Order number for the model and

select the Sorting by Order number option under

|Settings/Misc.

:    Global ATP variable input.

node values:

: Positive sum input node.

: Negative sum input node.

: Disconnected input node.

#Phases: Number of phases (1..26) for the component node. If #Phases is set

&gt;1 the length of the node name is limited to 5. The last

of nodes (in the proper phase sequence ahttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ccording to Kind)

be appended by ATPDraw.

:  Specifies the relative node position in steps of 10 pixels (grid).

standard border positions shown in the picture to the left of

.  4.29 have short cut keys Alt F1..Alt F12. The position (x, y)

in general be in the range -120,-110,..-10,0,10,..,110,120. The

-axis is oriented to the right while the y-axis is oriented

. The node positions should correspond with icon drawing.   8: Reference Manual

circuit object has an icon, which represents the object on the screen. This icon can be of bitmap type or vector graphic type as selected under Icon type. The conversion from Bitmap to Vector style is not possible so you should not unintentionally change the icon style. Vector graphic enables better zooming and graphic export, font handling and editing, but for simplicity reasons the Bitmap option ishttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 shown here. The leftmost of the three speed button on the right hand side of the Fig.  4.29 invokes the built in pixel editor where icons can be edited. Each icon has equal width and height of 41x41 pixels on the screen.

with the left mouse button will draw

current color selected from a 16 colors

at the bottom. Clicking the right button

draw with the background color. Dark red

lines indicate the possible node

on the icon border. Menu field items

the Icon Editor are described in the section

.2.7.1 of this manual. The user can draw

pixels and in additions line,

, circles, and fills. Text must be

put together by pixels. The Vecor

editor has far better text capabilities.

.  4.30 - Icon Editor.

component has a pre-definehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3d help file, which can be edited by a built in Help Editor accessible via the speed button on the middle speed button in the Edit definitions dialog in Fig.

.29. Using the help editor, users can write optional help file for the objects or add their notes to

existing help text. Available functions and menu field items of the Help Editor are described in the  4.2.7.2 section of this manual.

version 5.6

Reference Manual

the rightmost speed button in Fig.  4.29 the user can add a background bitmap/metafile image of any size to the icon. This should only be used in special cases since it could heavily occupy memory and increase the project file dramatically. No down-sampling of the imported image is performed.

the user has completed all modifications of the component data and of the icon and help, the new support file can be saved to http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3disk using Save (existing support file will be overwritten) or Save As (new file will be created in the folder) buttons.

.2.6.1.2 New Model sup-file

of MODELS [4] in ATPDraw is described in the Advanced Manual. When the user change the Model header (input, output or data section) in a circuit in ATPDraw the component and its icon is automatically updated. So for the usual case of a dynamic Model there is no point in pre-defining support and model files. These files can anyhow be exported from a finished Model. If you want a static Model, however, you can specify a support file under this menu item. To use this feature, you first must write a model file using the built in Model Editor as shown in section

.2.6.1.3. This file must have a legal MODELS structure (e.g. starting with MODEL name and

with ENDMODEL), have an extension .mod and stored in the system folder. ATPDraw is capablhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3e of reading such a .mod file, examining its input/output and data variables and suggesting a support file on the correct format (see in section  4.11.9 and  5.5.1). If the user wants a different icon or other node positions on the icon border, he is free to modify the default sup-file, or create a new one by selecting the Objects |

[此处图片未下载成功]

Model | New sup-file menu. This menu item will perform the Edit Definitions dialog as shown in Fig.  4.31.

.  4.31 - Control page for a New Model sup-file.

:   Identifies the node in the Node and Component dialog boxes. 12

maximum. Must be equal to the name used in the Model

.

:   Specifies the input/output type of the node.

#Phases:Number of phases can be from 1 to 26 and must be defined as V1[1..n]. Pos:    Specifies the relative node position in steps of 10 pixels (grid). The

bhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3order positions shown in the picture to the left of Fig.

.29 have short cut keys Alt F1..Alt F12. The position (x, y) can in

version 5.6  85

general be in the range -120,-110,..-10,0,10,..,110,120. The x-axis is

to the right while the y-axis is oriented downwards. on the

border. The node positions should correspond with icon drawing.

Kind values for MODELS objects are shown next: Reference Manual

: Output node.

: Current input node.

: Voltage input node.

: Switch status input node.

: Machine variable input node.

: TACS variable (tacs)

: Imaginary part of steady-state node voltage (imssv)

: Imaginary part of steady-state switch current (imssi)

: Output from other model. Note that the model which produces this

must be USEd before the current model. This cahttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3n be done by

a lower Order number for the model and then select the

by Order number option under ATP|Settings/Format.

: ATP global variable. MNT is for instance the simulation number and

Pocket Caculator KNT equivalent.

number of Nodes is the sum of inputs and outputs to the Model. The number of Data must be equal to the number of DATA declarations of the actual Model. The Kind parameter can be changed later in the Model node input window (right click on the node dot). All model nodes are assumed a single-phase one. The maximum number of nodes is 32 and the maximum number of data that can be passed into a Model is 64.

Save or Save As buttons can be used to save the new support file to disk. Default location of Model support files is the folder.

.2.6.1.3 New Model mod-file

addition to a support file and icon definition,http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 each Model component needs a text file which contains the actual Model description. This file may be created outside ATPDraw or using the built in Model Editor. Selecting the Library | New object| Model mod-file menu, the well-known internal text editor of ATPDraw pops-up.

supports only a simplified usage of MODELS. It is the task of the user to write the model-file and ATPDraw takes care of the INPUT/OUTPUT section of MODELS along with the USE of each model. The following restrictions apply:

INPUT, OUTPUT and DATA supported in the USE statement.

possible to specify expressions, HISTORY of DELAY CELLS under USE

possible to call other models under USE.

.2.6.2 Edit object

this menu item the user can edit existing support files for Standard, User Specified and Models components.

.2.6.2.1 Edit Standard

standard component support http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3files stored in the ATPDraw.scl file can be customized here. Selecting the Edit Standard field will first perform a select file dialog box of Fig.  4.32, where the

.33 appears. support file to be edited can be selected, then a dialog box shown in Fig.

version 5.6

Reference Manual

[此处图片未下载成功]

.  4.32 - Specify the support file of the standard component to be edited.

button to

Icon Editor

button to

Help Editor

button to

Picture

.  4.33 - Control page of object data.

.2.6.2.2 Edit User Specified sup-file

existing user specified object can be edited in the same way as any standard components as

.2.6.2.1. described in session

.2.6.2.3 Edit Model sup-file

model object can be edited like any other circuit objecthttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3. If the user clicks on the Library | Edit object | Model sup-file, the Edit Edfinitions dialog box appears with the model object controls. Here the user is allowed to customize data and node values, icon and help text of the object.

.2.6.2.4 Edit Model mod-file

the Objects | Model | Edit mod-file menu, the well-known internal text editor of

[此处图片未下载成功]

ATPDraw pops-up. Each model object has a .mod file which contains the description of the

[此处图片未下载成功]

model. This file can be edited inside ATPDraw using the built in Model Editor.

version 5.6

[此处图片未下载成功]

87

Reference Manual

.2.6.3 Syncronize|Reload Icons

and displays standard component icons from their respective support files. This function is useful when the user has redesigned one or more support file icons and wants the changes to be reflected ihttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3n the circuit window. User Specified and Models components icons are not updated.

.2.7 Tools

under the Tools menu enable you to edit component icons or help

, view or edit text files, customize several program options and save

to the ATPDraw.ini file.

.  4.34 shows the available commands of the Tools menu.

.  4.34 - Tools menu.

.2.7.1 Icon Editor

up an icon editor shown in Fig.  4.35 where the user can edit the icon of the component. It can be invoked either from the Edit Component dialog box or by selecting the Icon Editor option in the Tools menu

on how the editor was invoked, the

menu provides different options. When

from the Library menu (Edit Standard,

Specified or Edit Model sup-file), the user

allowed to import icons from other support

or cancel http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3the edit operation and close the

window. In this case, the Done option in

main menu is seen to accept and store the

icon in the .sup file as shown on

.30. Fig.

the icon editor is called from the Tools

, additional options like the Open and

appears in the File menu.

.  4.35 - Icon Editor menus.

[此处图片未下载成功]

At the bottom of the editor window there is a color palette with two boxes indicating the current foreground and background color selections, and the real-size image of the icon at right. In the color palette, the color marked with a capital letter T is the transparent color.

select a color from the palette, click either the left or the right mouse button in one of the color boxes. The selected color will be assigned to the mouse button you clicked until you use the same mouse button to select ahttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3nother color. The leftmost box displays the color currently assigned to the left mouse button. The one to the right displays the color assigned to the right mouse button.

version 5.6

Reference Manual

foreground color is normally used to draw with, and the background color to erase any mistakes made during the drawing. It is therefore convenient to assign the transparent color (indicated by T) to the right mouse button, and desired drawing color to the left button. Mistakes can then easily be corrected by alternating left/right mouse button clicks.

vertical and horizontal lines of dark red color indicate the icon node positions. These are in the same position as indicated on the Nodes pages of the Edit Component dialog boxes.

icon editor has a File menu, an Edit menu and a Tools menu. In addition, a Done option appears to the right of the Tools menuhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 if the editor has been called from the Edit Component dialog box. Selecting Done, changes made to the icon will be accepted. Available menu options are described below:

the icon of a support file into the icon buffer.

the contents of the icon buffer to disk.

the icon of a support file and inserts it into the

buffer.

Request an external support file and adds its icon to the                   current icon.

/Cancel Closes the icon editor window. If the option Exit is

and the icon buffer have been modified, you are

a chance to save the icon before closing. If the Done

is visible in the main menu, the name of this menu

is Cancel, and the icon editor window is closed without

warning with respect to loss of modified data.

options

Cancels the last edit operation.

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3o  Cancels the undo command.

Copies a bitmap version of the icon to the Clipboard and

the icon buffer. This bitmap can be pasted into other

(e.g. pbrush.exe).

Places a bitmap version of the icon in the Clipboard.

Inserts the bitmap in the Clipboard into the icon buffer. If

are different from those used in the original bitmap,

is because the icon editor calculates which color in its

color palette provides the nearest match to any bitmap

.

Clears the icon buffer.

options

Selects the pen drawing tool, enabling you to draw single icon pixels, or lines or shapes by pressing and holding down the left or right mouse button while you move the mouse. Selects the flood fill tool. Fills any shape with the current color. Selects the line drawing tool, enabling yhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ou to draw a rubber

line by pressing and holding down the left or the right

button while you move the mouse.

the circle drawing tool, enabling you to draw a

sized circle by pressing and holding down the

or the right mouse button while you move the mouse.

the box drawing tool, enabling you to draw a rubber

box by pressing and holding down the left or the right

button while you move the mouse. File options Open  Save  Import  Circle   Rectangle

.2.7.2 Help Editor/Viewer

the Help Editor where the current help text assigned to components can be modified. The Help Editor and the Viewer has actually the same window as the built-in Text Editor, but with different menu options and capabilities. To edit help file of standard objects, the user must select the Help Editor speed button in any Edit Component diahttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3log boxes. In this cases a Done option appears in the main menu and the File menu provides printing options and a Cancel choice. By

version 5.6  89

Reference Manual

Done you accept any changes made to the help text. To edit help file of a User Specified or Model object, the user has two choices: to select the Help Editor in the Tools menu or to click on the Help Editor speed button in any User Specified or Model dialog boxes.

the editor is called from the Tools menu, the File menu contains an Open and a Save option, as well. In that case the text buffer is initially empty, so the user must select the File | Open first to load the help text of a support file. The default font can be changed by selecting the Font option in the Character menu. This menu will bring up the Windows standard font dialog box where you can specify a new font name and character style, sizhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3e or color. Note that ATPDraw does not remember the current font setting when you terminate the program, so if you don't want to use the default font, you have to specify a new one each time you start ATPDraw. The Word Wrap option toggles wrapping of text at the right margin so that it fits in the window.

the built in editor is used as a viewer of component help text, editing operations are not allowed and the File menu provides printing options only. Additionally, the Find &amp; Replace option is missing in the Edit menu.

status bar at the bottom of the window displays the current line and character position of the text buffer caret, and the buffer modified status. This status bar is not visible when viewing component help. A more detailed description of menu options is given in the next sub-section.

.2.7.3 Text Editor

invoke the editor you may select the Text Editor optiohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3n in the Tools menu or the Edit ATP-file or Edit LIS-file in the ATP menu. In the latter case, the file having the same name as the active circuit file with extension .atp or .lis are automatically loaded. When the program is called from the Tools menu, the text buffer will initially be empty.

status bar at the bottom of the window displays the current line and character position of the text buffer caret, and the buffer modified status. The text buffer of the built in text editor is limited to 32kB therefore not be suitable for editing large files. However, any other text processor (e.g. notepad.exe or wordpad.exe) can be used, if Text editor: setting of the Preferences page in the Tools | Options menu overrides the default one.

detailed description of the menu options are given below:

options

Opens an empty text buffer. (Built-in text editor only!) Loads thehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 help text of a support file or the contents of a

file into the text buffer.

Stores the contents of the text buffer to disk.

As  Stores the contents of the text buffer to a specified disk

. (Built-in text editor only!)

Sends the contents of the text buffer to the default

.

Setup Enables you to define default printer characteristics.

/Cancel Closes the editor or viewer window.

the option displays Exit and the text buffer has been

, you are given a chance to save the text before

. If a Done option is available from the main menu,

option displays Cancel, and the window will close

any warning with respect to loss of modified data.

options

Cancels the last edit operation.

version 5.6

Copies selected text tohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 the Clipboard and deletes the text

the buffer.

Puts a copy of the selected text in the Clipboard.

Inserts the text in the Clipboard into the text buffer at

current caret position.

Deletes any selected text from the text buffer.

All Selects all the text in the buffer.

Searches the text buffer for the first occurrence of a

text string and jumps to and selects any matching

found. This option displays the Windows standard Find

box.

Next Searches for the next occurrence of the text string

specified in the Find dialog.

&amp;Replace Searches the text buffer for one or all occurrences of a

text string and replaces any instance found with a

replacement string. This option displays

standard Replace dialog bohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3x.

options

Wrap Toggles wrapping of text at the right margin so that it fits

the window.

From the Windows standard Font dialog box you can change the

and text attributes of the text buffer. Cut  Reference Manual

.2.7.4 Options

the Tools | Options menu several user customizable program options for a particular ATPDraw session can be set and saved to the ATPDraw.ini file read by all succeeding sessions. During the program startup, each option is given a default value. Then, the program searches for an ATPDraw.ini file in the current directory, the directory of the ATPDraw.exe program, the Windows installation directory and each of the directories specified in the PATH

[此处图片未下载成功]

environment variable. When an initialization file is found, the search process stops and the file is loaded. Any option values in this file override the defaulthttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 settings. The ATPDraw.ini file is stored under %APPDATA%/atpdraw (typically c:and settingsdata) and is unique for each user of the computer. The file is ATPDraw version independent.

.36 - Customizing program options. Fig.

version 5.6  91

Reference Manual

ATPDraw Options dialog enables you to specify the contents of the ATPDraw.ini file without having to load and edit the file in a text editor. As shown on Fig.  4.36 this dialog box has four sub-pages: General, Preferences, Directories and View/ATP.

General tab specifies the project file and ATPDraw main window options. The following list describes the available options:

Description          Autosave every

? minutes  Saves all modified circuits to a separate disk file every specified interval of minutes. The file name is thehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 same as

project file but with extension '.$ad'. Modified state

the circuit window does not change as a consequence of

operation.

backup  Changes the extension of the original project file to '.~ad'  files   each time the circuit is saved. This option does not apply

autosave operations.

window size Records the current size and position of the main window.  and position When ATPDraw is started next, it will be displayed with

same size and in the same position as the previous

.

window's  Records the current main window state (maximized or

state normalized). The next time ATPDraw is started, it will be

in the same state.

toolbar  Records the current view state (visible or hidden) of the  state   main window toolbar, so it can be redisplayed in the same

next time when AThttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3PDraw is started.

status bar  Records the current view state (visible or hidden) of the  state   main window's status bar, so it can be redisplayed in the

state next time when ATPDraw is started.

comment  Records the current view state (visible or hidden) of the  state   circuit window comment line, so it can be redisplayed in the

state next time when ATPDraw is started.

3.1  Causes the Open/Save dialogs to be drawn in the Windows 3.1  style   style.

options Causes program options to be automatically saved to the  on exit   initialization file when the program is terminated.

that the ‘save state’ options will have no effect unless program options are saved to the initialization file (ATPDraw.ini) by the Save command at the bottom of the ATPDraw Options dialog, or by selecting the ‘Save options on exit’ check box, or by the Tools | Save Ohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ptions menu.

the bottom of the ATPDraw Options dialog box the five buttons provide the following functionality:

Description           OK

Stores current settings into program option variables, updates the  screen and closes the dialog box. Changes made will only affect the current session. Saves the current settings to the ATPDraw.ini file. Loads settings from the ATPDraw.ini file. Same as OK, but does not close the dialog box. Displays the help topic related to the options on the current page.

version 5.6

Reference Manual

that, if no initialization file exists, ATPDraw will create a new file in its installation directory when the user selects the Save button or the Save Options in the Tools menu.

the Preferences page the user can

the size ohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3f undo/redo buffers,

the default text editor and

files to execute ATP-EMTP

(TPBIG*.EXE) and Armafit

.

.  4.37 - Customizable program

on the Preferences page.

Description          Undo/redo  Specifies the number of undo and redo buffers to allocate for each buffers:  circuit window. Changing this option does not affect the currently

circuit windows; only new windows will make use the specified

. Almost all object manipulation functions (object create,

, move, rotate, etc) can be undone (or redone). These

also update the circuit's modified state to indicate

the circuit needs saving. During an undo operation, the

state is reset its previous value, so if you undo the

first edit operation, the 'Modified' text in the status bar

disapphttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ear. Any operation undone can be redone. Since only a

number of buffers are allocated, you are never guaranteed

undo all modifications. For example, if the number of undo/redo

is set to 10 (default) and eleven successive modifications

the circuit are made, the first modification can no longer be

, and the modified state will not change until you save the

.

Selects the background color of circuit windows. The color list color: provides available system colors, but you may customize your own

the Windows standard Color dialog displayed by the Custom

. The current color selection is shown in the box to the

of the Custom button.

editor Holds the name and path of the text editor program to use for

: editing ATP-files (e.g. notepad.exe or wordpad.exe). If no program

specifhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ied (the field is empty), the built-in text editor will

used. Note that the program specified here must accept a

on the command-line; otherwise the ATP-file will not be

loaded by the editor.

:  Holds the ATP program command, which is executed by the run ATP

(or F2 key) at the top of the ATP menu. A batch file is suggested as default (runATP_S.bat for the Salford, runATP_W.bat

the Watcom and runATP_G.bat for the MingW32/GNU versions).

/GNU versions can also be executed directly as %WATDIR%

.EXE DISK $$ * -r or %GNUDIR%TPBIGG.EXE DISK $$ s -r where

$$ replaces the %1 sign normally used in a batch file.

:  Holds the name of the Armafit program used for NODA line/cable

. A batch file runAF.bat is suggested.

version 5.6  93

Plot:

: Holds the preferrehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3d plotting command. Executed under ATP|run Plot (F8). Holds the compatible Windsyn command. WindsynATPDraw.exe. Reference Manual

&amp;Folders

following table describes the available options on the Directories page:

Description          Project folder The directory where ATPDraw stores the project files (.acp). ATP folder  Specifies the directory in which .atp files are created.                   This is also the default Result Directory.

folder Directory containing support (.sup) and model (.mod) files

MODELS components.

folder  The user can write help text files for instance resistor.txt

(same name as the support file and extension txt) and store

in this folder. It will then automatically be added after

standard help text.

spec. folder Directory containing support (.sup), library (.lib) files

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3or user specified components.

/Cable folder Default folder for the line and cable models. This folder

contain .alc files (ATPDraw line/cable data),

.atp and .pch files, and .lib files (include).

the .alc files are stored in that directory, the

.lib files used in $Include statements in the

ATP input file are also stored in this directory. The

$Prefix/$Suffix option should in this case be turned off.

Noda format in ATP does not allow to specify the full

for $include files. Therefore, Noda lines (.alc files)

be stored in the same directory as the final ATP-file.

folder The default folder for BCTRAN multi-phase, multi-winding

transformer models. This folder will contain .bct

(ATPDraw Bctran data), intermediate .atp, .pch and

.lis files. In addition the Hybrid thttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ransformer (XFMR) files

be stored here (.xfm).

folder This is a user definedable folder that appears in the bottom

the Selection menu. The user can add project files (acp)

sub-folders to this folder structure.

/ATP

groups of options can be specified in the View/ATP page. These are the Default view options and the Default ATP settings.

Edit options button opens the View Options dialog, which enables you to specify view options to apply as default to all new circuit windows. Available options are described in section

.2.4.4. Note that all circuit windows maintain their own set of view options, and only the new

windows you open will use the options specified here. To change the view options of an existing circuit window, select the Options item in the View menu (section  4.2.4.4).

Edit settingshttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 button calls the ATP settings dialog described in section  4.2.5.1 of this manual. ATP settings specified here will be applied as default to all new project files. Note that all circuits have their own settings; stored together with the objects in the project files. The settings specified here will only be used by the new circuits you create. To customize ATP settings of an existing project select the Settings... item in the ATP menu or press F3 function key.

ATPDraw version 5.6

Reference Manual

[此处图片未下载成功]

prefix tags are text strings added in

of the $include file name. This is

User Specified (USP), Line&amp;Cable

(LCC), and Windsyn (WIS) components all

their $include file dumped to the

Directory (same as the ATP-file). In

case duplicate file names in these

, file conflicts will occurhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3e. The

option can then be used to avoid the

. If two UPS component have the

name for instance, the $include file is

forced to be equal.

.  4.38 - Setting default view and ATP options.

House-keeping options delete temporary files after the simulation or exit. In the case of debugging a Line&amp;Cable model the Delete temp-files after simulation option should not be checked.

.2.7.5 Save Options

program options into the ATPDraw.ini. This file is normally located in the program installation directory and can be used to store default options and settings.

.2.8 Window

Window menu contains options for activating or

circuit windows and showing or hiding

Map window.

.  4.39 - Supported options on the Window menu.

Tile cohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3mmand arranges the circuit windows horizontally in equal size on the screen. To activate a circuit, click the title bar of the window. The active circuit window is marked by a 9symbol in front of the circuit file name.

Cascade command rearranges the circuit windows so that they overlap such a way that the title bar remains visible. To activate a circuit click the title bar of the window.

Icons

Arrange Icons command arranges the icons of minimized circuit windows so that they are evenly spaced and don't overlap.

version 5.6  95

Reference Manual

.2.8.1 Map Window

Map Window command (Shortcut: Ctrl M) displays or hides the map window. The map window is a stay-on-top style window, meaning that it will always be displayed on top of all other windows. You can show or hide the map by pressing the Ctrl M character of the keyboarhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3d to enable it when you need it, or hide it when it conceals vital circuit window information.

map window displays the entire contents of the active circuit. The circuit

itself is represented by a map rectangle and the circuit objects are

as black dots.

.  4.40 - Map window.

you press and hold down the left mouse button in the map rectangle, you move the display of the circuit world continuously. If any circuit objects are currently selected when you reposition the map rectangle, they remain in the same position in the circuit window. This functionality can be used to quickly move a collection of objects a relatively large distance.

.2.9 Help

Help menu contains options for displaying the help of ATPDraw, and the copyright and version information. The help file ATPDraw.chm is distributed with ATPDraw and it follows the compressed HTML sthttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3andard compatible with Windows Vista.

.  4.41 - Help menu.

’s HTML help is displayed in a standard Windows dialog, which provides indexed and searchable help on all ATPDraw dialogs and options.

.2.9.1 Help Topics

Help Topics command invokes the MS-Windows standard help dialog box. Several links and a relatively large index register support the users in searching. Selecting the Contents tab you get a lists of available help functions as shown on Fig.  4.42.

page allows you to move through the list and select an entry on which you need help. To display an entry select one from the list by a simple mouse click and press Display, or double click on the entry with the mouse. Index and

[此处图片未下载成功]

Find tabs can be used to get help by the name of a topic. E.g. if you ask for help on topics “Circuit Window” type this phrase into the ihttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3nput field of the Index page and press the Display button. The ATPDraw help file consists of 136 topics.

version 5.6

Reference Manual

[此处图片未下载成功]

.  4.42 - HTML help of ATPDraw.

.2.9.2 On Main Window

menu item On Main Window displays help about the ATPDraw main window. 4.2.9.3 About ATPDraw

this menu item shows the ATPDraw copyright information and the program version

used.

. 4.43 - About window of ATPDraw.

.3 Shortcut menu

Shortcut menu provides access to the most frequently used object manipulation functions. To

and activate the shortcut menu, hold down the Shift key while you click the right mouse button on an object or a selected group of objects in the circuit window. Most of the items on this

version 5.6

Reference Manual://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ar

are identical with that of the Edit menu (section  4.2.2). The Open menu item at the top of the menu is an addition to these normal edit functions. If this command is performed on a single object, the Component dialog box appears. If you select this command for a group of selected objects, the Open Group dialog box appears.

: Enables the component customization by bringing up

Component dialog box of the object.

, Copy: Provides access to the standard clipboard functions

, Duplicate

, Rotate: Rotates and flips the objects’ icon Select/Unselect: Select/unselect the object(s)

.  4.44 - Available options in the Shortcut menu.

.4 Component selection menu

Component selection menu provides options for

new components into the circuit window. This menu is normally hidden. To open it you must clhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ick on the right mouse button in an empty area of the circuit window. The component selection menu collects all the available circuit objects of ATPDraw in a structured way as shown in Fig.  4.45. After selecting a component in one of the floating menus, the selected object is drawn in the circuit window.          Fig.  4.45 - Component selection menu.

[此处图片未下载成功]

[此处图片未下载成功]

The upper section of the menu provide access to the probe, splitter and transposition and reference objects, the next seven to many standard ATP components: linear and nonlinear elements, lines and cables, switches, sources, electrical machines and transformers. The next section is dedicated for the control systems MODELS and TACS components. User specified objects and Frequency dependent components for Harmonic Frequency Scan (HFS) studies are accessible in the next group followed by a list of all the standard supported compohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3nents (for instance older component replaced by new versions). The final menu item called Plugins points to a user defined folder structure for import of project files (sub-circuits).    98  ATPDraw version 5.6

Reference Manual

.5 Component dialog box

selecting a component in the Component selection menu the new circuit object appears in the middle of the circuit window enclosed by a rectangle. Click on it with the left mouse button to move, or the right button to rotate, finally click in the open space to unselect and place the object. The Component

[此处图片未下载成功]

dialog box appears when you click the right mouse button on a circuit object (or double click with the left mouse). Assuming you have clicked on the icon of an RLC element, a dialog box shown in Fig.  4.46 appears. These dialog boxes have the same layout for all circuit objects except probes, which can be edited from thhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3e Probe dialog box.

names Red=User defined

all data to  Windows clipboard

for sorting Label on screen Comment in the ATP file Not written to the ATP file

output

, local help,  node and data  definitions,

, low precision ATP input data

.  4.46 - The Component dialog box.

help text of the object

data can be entered in the Value field of the Attributes page. The Node, Phase and Name fields are initially empty and you can enter node names in the Name field (without phase extensions 'A'..'Z'). You have to run ATP|Sub-process|Make node names or (ATP|run ATP) to obtain the ATPDraw specified node names.

values in the data input fields can be specified as real or integer, with an optional exponential integer, identified by 'E' or 'e'. A period '.' is used ashttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 decimal point. Many data parameters have a legal range specified. To check this legal range, place the input caret in a data field and press the Ctrl F1 keys. If you specify an illegal value, an error message is issued when you move to another data field, or select the OK button. The legal range can be set under Edit definitions. Instead of a value you can also assign a 6 (or less) character text string as input data for most of the standard components. This requires the Param property of the data to be set to unity (see Edit definitions). Numerical values can later be assigned to these variables under

version 5.6

Reference Manual

|Settings/Variables using the $PARAMETER feature of ATP-EMTP (see in  4.2.5.1).

below the node input column, there is a Order input field. It can be used later as optional sorting criteria (the lowest order number will be written first in thttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3he ATP-file) on the ATP | Settings / Format page.

content of the Label input text field is written on the screen. The visibility of the component label is controlled by the Labels option in the View | Options dialog box. The label is movable and directly editable on the screen. The font of the Label is controlled vie View|Set circuit font. The component dialog box has a Comment input text field. If you specify a text in this field, it will be written to the ATP-file as a comment (i.e. as a comment line before the data of the object).

standard component such as branches, non-linear, switches and transformers contains an Output section for setting the branch output request in a combo box. Possible values are Current, Voltage, Current&amp;Voltage, Power&amp;Energy or none.

the Order, Label and Comment fields, the Hide button is common to all components. Hidden components are not included in the ATP-fhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ile and are displayed as light gray icons in the circuit window. All components where the high precision format is available has a $Vintage, 1 check button in the component dialog box. It is thus possible to control the precision format for each individual component. Selecting Force high resolution under the ATP | Settings/Format page will overrule the individual setting and force $Vintage, 1 for all components if possible. The components User specified, Models and Groups has also a Protect button for password protection of the their content.

OK button will close the dialog box and the object data and all properties are updated in the data structure. Then the red drawing color of the object icon will be turned off, indicating that the object now has user specified data. When you click on the Cancel button, the window will be closed without updating. The Help button calls the Help Viewer to show the help text of the objechttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3t. Further help about the Component dialog is also available through the Windows standard HTML help system of ATPDraw if you press the F1 key.

non-linear components (non-linear branches, saturable transformers, TSWITCH, and TACS Device 56) have a Characteristic page too, as shown in Fig.  4.47.

the Characteristic tab of the dialog box, you define the input characteristic for non-linear components. Data pairs can be specified in a standard string grid. To add new points after the cursor position, click on Add. Delete the marked point by clicking on Delete. You can manipulate the order of points by the Sort button (the characteristic for non-linear components is automatically sorted after increasing x-values, starting with the lowest number) or the &#207; and &#208; arrows. The user can edit the data points directly any time.

is possible the export the characteristic to an external file or to the Windowhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3s clipboard as text. The whole characteristic is copied (no marking is supported or required). You can also paste a characteristic from the clipboard. It is thus possible to bring an old .atp file up in a text editor, mark the characteristic (the flag 9999 is optional) and copy it to the clipboard, then paste it into the characteristic page. The number of points will automatically be adjusted (the pasted characteristic could be truncated to ensure that the number of data is less or equal to 64). Therefore, you do not have to click on Add or Delete buttons before pasting. ATPDraw uses fixed  100

version 5.6

Reference Manual

16 character columns to separate the numbers. Note! Pasting in from a text file with 'C' in

[此处图片未下载成功]

the first column is not possible; Delete leading 'C' characters first.

.  4.47 - The Characteristic page of non-linear http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3components.

.48 - The View nonlinearity window. Fig.

External characteristic section at the bottom of the page contains an Data source field where

[此处图片未下载成功]

ATPDraw version 5.6  101

Reference Manual

can specify the name of a standard text file containing nonlinear characteristic. If the 'Include characteristic' button is checked, this file will be referenced in the $INCLUDE statement in the ATP-file rather than including each of the value pairs from the points table. ATPDraw reads the specified file into memory and inserts it directly in the final ATP file.

nonlinear characteristic specified by the user can be displayed by clicking on the View button. In the View Nonlinearity window (Fig.  4.48) the min and max axis values are user selectable as well as the use of logarithmic scale (if min&gt;0). It is possible to left click and drag a rehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ctangle for zooming. Click right to restore.  The Add (0,0) check box will add the origo point, and 1st quad will display only the first quadrant. It is also possible to copy the graphic to the Windows clipboard in a metafile format with Copy wmf. Selecting Done will close the nonlinearity display.

following components deviate somewhat from the above description and will be referenced in the Advaced part of this Manual:

3-phase transformer (SATTRAFO)  Universal machine (UM_1, UM_3, UM_4, UM_6, UM_8)  Statistical switch (SW_STAT)  Systematic switch (SW_SYST)  Harmonic source (HFS_SOUR)  BCTRAN transformer (BCTRAN3)  Line/Cable LCC objects (LCC_x)  Windsyn UM component (WISIND, WISSYN)   Hybrid Transformer (XFMR)  Models&amp;Type 94

on the type of component opened, the group box in lower-left corner of the Attributes page may display additional options:

) For Models you can enter thehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 editor for inspecting or changing the Models text. In addition you can specify a Use As string and defined the output of internal variables RECORD.

) For the Fortran TACS components ATPDraw provides an extra OUT field here to specify the Fortran expression.

) For user specified components you specify the name of the library file in the $Include field. If Send parameters option is selected, the Internal phase seq. controls how the node names are passed. i.e. unselect this option if your library file expects 5-character 3-phase node names. If the library file name does not include a path, the file is expected to exist in the /USP folder.

.6 Connection dialog box

Connection dialog box appears if you draw a Connection between a single phase node  and a multi-phase node or double click on a Connection. This dialog allows you to select the number of phases in the Connection and the phase number of a sihttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ngle phase Connection (Phase index). A pure single phase connection between two single phase nodes should have the Phase index 0-@. You can also select the Color of the Connection and a text Label which can be displayed on screen. In addition you can choose to Hide the connection and transform it to a Relation (not a connection, only a dashed line). In both these cases the connection do not affect the node names. A special option is to force the Node dots on regardless of the Node dot size set in the main menu.   102

version 5.6

Reference Manual

[此处图片未下载成功]

.  4.49 – Connection dialog box

.7 Text dialog box.

Text dialog box appears if you right click or double click on a Circuit Text (not a Label or Node Name). In this dialog you can specify the Font, Size and Colors of the font used in the Circuit Text. You can edit Circuit Text, Label and Nodhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3e Names directly in the Circuit Window by a left, simple click on them. Circuit Texts can hold multiple lines and the entire text uses the same font. You can move the Circuit Texts, Labels, and Node Names by left click and hold. Press the Alt key to avoid selecting other circuit objects.    Fig.  4.50 – Circuit Text dialog box

.8 Node dialog box

the Node data dialog box you specify data for a single component node. Input text in this

boxes should contain only ASCII characters, but characters like * -   / $ etc. should not be used. Avoid using space in the node name and lower case letters, as well. The user does not need to give names to all nodes, in general. The name of the nodes without special interest are recommended to be left unspecified and allow ATPDraw to give a unique name to these nodes. The node dots given a name by the program are drawn in black, while those whose names were spehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3cified by the user are drawn with red color.

are four different kinds of nodes, each treated slightly different in this dialog box:

) Standard and user specified nodes 2) MODELS object nodes 3) TACS object nodes

) TACS controlled machine nodes  Fig.  4.51 - Node dialog box for standard components.  Parameters common to all nodes are:

[此处图片未下载成功]

A six or five (3-phase components) characters long node name. The

caption is read from the support file. If you try to type in a name on the reserved ATPDraw format (XX1234 for single phase or X1234 for three-phase nodes) you will be warned. Ignoring this warning can result in unintentional naming conflicts.

version 5.6

Reference Manual

If checked, the node name is written on screen, regardless of the

setting of the Node namehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3s option in the View | Options dialog box.  UserNamed  This checkbox shows whether this node name is specified by the user

ATPDraw. If the user wants to change a user specified node name he must do this where the UserNamed box is checked. If not, duplicate node name warnings will appear during the compilation. Node with UserNamed set are also drawn with a black node dot.

following list explains the type specific node parameters:

and USP components:

checked, the node is grounded. A ground symbol appears for rotation of the graphical grounding symbol.

node:

0=Output.

=Input current (i) 2=Input voltage (v)

=Input switch status (switch) 4=Input machine variable (mach) 5=TACS variable (tacs)

=Imaginary part of steady-state node voltage (imssv) 7=Imaginary part of steady-state switch current (imssi)

=Outpuhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3t from other model. Note that the model that produces this output must be USEd before the current model. This is done by specifying a lower Order number for the model and then select the Sorting by Order number option under ATP | Settings / Format. 9=Global ATP variable.

node:

0=Output.

=Input signal positive sum up. 2=Input signal negative sum up.

=Input signal disconnected. (necessary only if the node   name is user specified)

controlled machine node:

0=No control.

=D-axis armature current. Out. 2=Q-axis armature current. Out.

=Zero-sequence armature current. Out. 4=Field winding current. Out. 5=D-axis damper current. Out.

=Current in eddy-current winding. Out. 7=Q-axis damper current. Out.

=Voltage applied to d-axis. Out. 9=Voltage applied to q-axis. Out. 10=Zero-sequence voltage. Out.

=Voltage applied to field wihttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3nding. Out. 12=Total mmf in the machines air-gap. Out.

=Angle between q- and d-axis component of mmf. Out. 14=Electromagnetic torque of the machine. Out. 15=Not used.

=d-axis flux linkage. Out. 17=q-axis flux linkage. Out. 18=Angle mass. Out.

=Angular velocity mass. Out. 20=Shaft torque mass. Out. 21=Field voltage. In. 22=Mechanical power. In.

version 5.6

Reference Manual

.9

[此处图片未下载成功]

Open Probe dialog box

are components for output of node- or branch voltages, branch current or TACS values, and are handled differently than other components you open. In the Open Probe dialog you can specify the number of phases of a probe and which phases to produce output in the PL4-file. There are five different probes in ATPDraw:

_v: Node voltages output request. Probe_b: Branch voltage output request. Probe_i: Branch currenthttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 output request. Probe_t: TACS variable output request.   Type33. Probe_m: MODELS output nodes.  4.52 - Node dialog box for standard components. Fig.

Steady-state option is only available for Voltage and Current probes. ATPDraw reads the lis file and identifies the steady state ATP output. For multi-phase nodes only phase A is analyzed. The current probe also handles power and energy flow. ATPDraw divied the steady-state value with the Scale factor (816.4966-&gt; line voltages in kV RMS value) befor displaying it on screen or immediately below. The symbol '&lt;' is used to indicate the phasor angle. Remember that the number of phases is critical for a current probe and this has to match the circuit.

.10 Open Group dialog box

you double-click in a selected group of objects, the Open Group dialog box will appear, allowing you to change attributes common to all components in that group, such as data valueshttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3, Order number and Hide state. The common data parameters are listed in a dialog as of Fig.  4.53 where you can change the data for all the involved components, simultaneously. The data names from the definition properties are used to classify the data.

alternative way to change the data parameter for several component simultaneously is to use $PARAMETER feature (see

.17 in section  4.2.5.1). Fig.       Fig.  4.53 - Open Group dialog  box for simultaneous data setting

[此处图片未下载成功]

Every component has a an order number. By specifying a value in the Order field, all components in the selected group of objects are assigned the same number. The order number serves as an optional sorting criterion for the ATP-file (components with the lowest order number are written to the .atp file first).

version 5.6

Reference Manual

Hide state of multiple componenhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ts can also be specified. Hidden components are not included in the ATP-file and are displayed as gray icons. You can also choose to reset to the default values inherited from the support files by clicking on the now button. Selecting the Use default values check box will cause default values to be loaded automatically next time the dialog box is opened.

.11 Circuit objects in ATPDraw

Component selection menu provides options for creating and inserting new components into the circuit window. This menu is normally hidden. To show and activate the menu, click the right mouse button in an empty circuit window space. Following a selection in one of the floating sub-menus, the selected object will be drawn where you clicked the mouse button in the active circuit window enclosed by a rectangle. You can move (left mouse click and drag), rotate (right mouse button) or place the object (click on open space).

Cohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3mponent selection menu has several sub-menus; each of them include circuit object of similar characteristics as briefly described below:     Fig.  4.54 - Component selection menu.

&amp; 3-phase

Probes for node voltage-, branch voltage, current-, TACS, and Models output monitoring o Various 3-phase transposition objects

Splitter (coupling between 3-phase and single phase circuits) and Collector. o ABC/DEF Reference objects for specifying the master node for phase sequence Branches

Branch linear: 1-phase and 3-phase non-coupled components. RLC.

Branch nonlinear: 1-phase nonlinear R and L components. Single and 3-phase MOV. Type-93, 96 and 98 nonlinear inductors including initial conditions for the fluxlinked reactors o TACS controlled and time dependent resistor Lines/Cables

Lumped, PI-equivalents (type 1, 2...) and RL coupled components (type 51, 52...)

Distributed http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3lines of constant, frequency independent parameters. Transposed (Clarke) up to 9-phases, untransposed 2 or 3-phase (KCLee) line models.

LCC, the user can select 1-9 phase models of lines/cables. In the input menu of these

[此处图片未下载成功]

components, the user can specify a LINE CONSTANT or CABLE PARAMETER data case. The resulting include file contains the electrical model and the LIB-file is generated automatically if the ATP setup is correct. Bergeron (KCLee/Clarke), nominal PI, JMarti, Semlyen and Noda models are supported.

Read PCH-file. This is a module in ATPDraw to read the punch-files from Line Constants, Cable Constants or Cable Parameters and to create an ATPDraw object automatically (sup-file and lib-file). ATPDraw recognizes: PI-equivalents, KCLee, Clarke, Semlyen, and JMarti line formats.  106

version 5.6

Reference Manual

Time and volhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3tage controlled. 3-phase time controlled switch o Diode, thyristor, triac

Simple TACS controlled switch o Measuring switch

Statistic and systematic switches Sources

AC and DC sources, 3-phase AC source. Ungrounded AC and DC sources. o Ramp sources o Surge sources

TACS controlled sources Machines

Type 59 synchronous machine

Universal machines (type 1, 3, 4, 6, and 8) o Windsyn component

Single phase and 3-phase ideal transformer o Single phase saturable transformer

3-phase, two- or three-winding saturable transformer

3-phase, two winding saturable transformer, 3-leg core type of high homopolar reluctance o BCTRAN. Automatic generation of .pch file. 1-3 phases, 2-3 windings. Auto-transformers, Y-, and D- connections with all possible phase shifts. External nonlinear magnetizing inductance(s) supported.

Hybrid Transformer (XFMhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3R). Advanced topologically correct transformer with Test Report, Design data or Typical value input. MODELS

Under MODELS the user can either select a default model and write/update the Model text internally, or select an existing external model component by specifying a sup-file or a mod-file. If a .mod-file is selected the corresponding sup-file required by ATPDraw is created automatically (if the model is recognized successfully). A mod-file is a text file in the MODELS language. The mod-file must have a name equal to the name of the model. The following restrictions apply when ATPDraw reads a mod-file:

- Names of all input, output and data variables must be less than 12 characters.

input, output, data and variables declared in front of TIMESTEP, INTERPOLATION, DELAY, HISTORY, INIT and EXEC are recognized by ATPDraw when reading the mod-file.

Type 94: General, multi-phase type 94 component. Sphttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ecify the type; THEV, ITER, NORT, NORT-TR and the number of phases. Specify a mod-file describing the Type-94 models component (templates available). The same rules as specified under MODELS apply.  TACS

Coupling to Circuit. Input to TACS from the circuit must be connected to this object. o 4 types of TACS sources: DC, AC, Pulse, Ramp.

Transfer functions: General Laplace transfer function. If the Limits are not specified or connected, no limits apply. First order dynamic icon with limits. Simple Integral, Derivative, first order Low and High Pass transfer functions. o TACS devices. Type 50-66.

Initial condition for TACS objects (Type-77)

version 5.6

o o

Manual

statements: General Fortran statement (single line expression). Simplified Math statements or Logical operators.

relations. Relations are drawn in blue and are uhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3sed just to visualize connections between Fortran statements and other objects. Relations will not affect the ATP input file.

specified

Library: $Include is used to include the lib-file into the ATP input file. The user must keep track of internal node names in the include file.

Additional: Free format user specified text for insert in the ATP file. Selection of location. o Single and 3-phase reference: These objects are not represented in the ATP input data file and serve only as visualization of connectivity.

Files: Select a support file (sup). Import a lib-file (Data Base Module format) via the Edit menu. $Include is used to include the user specified lib-file into the ATP input file and pass node names and data variables as parameters.  Steady-state components

RLC Phasor component only present at steady state o Harmonic source for Harmonic Frequency Scan studies

Single anhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3d 3-phase frequency dependent loads in CIGR&#201; format o Single phase RLC element with frequency dependent parameters o Load flow components PQ, UP, TQ

Component..

Complete list of standard components in alphabetical order sorted by support file names. Plugins

User defined folder structure containing project files (.acp) for import.

.11.1 Probes &amp; 3-phase

menu Probes &amp; 3-phase  appears when the mouse moves over this item in the Component selection menu or when the user hits the P character.

are components for monitoring the node or branch voltage, branch current or TACS values. In the Open Probe dialog you can specify the number of phases to connect to and select phases to be monitored.       Fig.  4.55 – Drawing objects on the Probe &amp; 3-phase menu.

[此处图片未下载成功]

Volt

this field draws the http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3voltage probe to specify a node voltage-to-ground output request in the ATP-file.

version 5.6

Reference Manual

Branch volt.

this field draws the branch voltage probe to specify a branch voltage output requests in the ATP-file. ATPDraw inserts a 1E 9 ohm resistance. Probe Curr

this field inserts a current probe (measuring switch) into the circuit to specify current output request in column 80 in the ATP-file. The number of monitored phases are user selectable. Add current node: Two switches in series. Middle node available. Probe Tacs

Model

Splitter object is a transformation between a 3-phase node and three 1-phase nodes. The object has 0 data and 4 nodes. The object can be moved, rotated, selected, deleted, copied and exported as any other standard components.

[此处图片未下载http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3成功]

[此处图片未下载成功]

[此处图片未下载成功]

this field draws the Tacs probe to specify signal output and inserts TACS Type-33 object into the ATP-file.

this field draws the Model probe which can be added to Models output nodes. Inserts RECORDS cards into ATP-file.

a splitter is rotated the phase sequence of the single-phase side changes as shown left.

[此处图片未下载成功]

a name is given to the 3-phase node, the letters A B C are added automatically on the single-phase side of splitters.

! Do not give names to nodes at the single-phase side of splitters and do not connect splitters

[此处图片未下载成功]

together on the single-phase side (except all three phases). I.e. next two examples are illegal!

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

NODEANODEBNODEC

is illhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3egal this way!   This is leagal, however.

Collector object is a component with a single multi-phase node. It is only used in

added to, sinse only components can have external nodes, not connections.

1 ABC-BCA  ...Transp 4 ABC-ACB

objects can be used to change the phase sequence of a 3-phase node. The following transpositions are supported:

[此处图片未下载成功]

Change the phase sequence from ABC to BCA. Change the phase sequence from ABC to CAB. Change the phase sequence from ABC to CBA. Change the phase sequence from ABC to ACB.

of transpositions for objects with several 3-phase nodes can be accomplished by specifying a circuit number Kind under Objects | Edit Standard / Nodes (see in  4.2.6.2.1). 3-phase nodes having the same Kind will receive the same phase sequence.

version 5.6

Reference Manual

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3

reference ABCWhen attached to a 3-phase node in the circuit this node becomes the “master” node with

sequence ABC. The other nodes will adapt this setting. DEF reference DEFWhen attached to a 3-phase node in the circuit this node becomes the “master” node with

sequence DEF. The other nodes will adapt this setting. A combination of ABC and DEF references is possible for e.g. in 6-phase circuits.

.11.2 Branch Linear

sub-menu contains linear branch components. The name and the icon of linear branch objects, as well as a brief description of the components are given next in tabulated form. Data parameters and node names to all components can be specified in the Component dialog box (see

.46), which appears if you click on the icon of the component with the right mouse button in Fig.

circuit window.

Help button on the Component dialog boxeshttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 calls the Help Viewer in which a short description of parameters and a reference to the corresponding ATP Rule Book chapter is given. As an example, Fig.  4.57 shows the help information associated with the ordinary RLC branch.       Fig.  4.56 – Supported linear branch elements.

[此处图片未下载成功]

ATPDraw version 5.6

Reference Manual

[此处图片未下载成功]

Fig.  4.57 – Help information associated with the series RLC object.

.11.3 Branch Nonlinear

menu contains the supported nonlinear resistors and inductors. All the objects except the TACS controlled resistor can also have a nonlinear characteristic. These attributes can be specified by selecting the Characteristic tab of the Component dialog boxes as shown in Fig.

.47. The nonlinear characteristic of objects can be entered as piecewise

interpolation. The number of data points ahttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3llowed to enter on the current/voltage, current/flux or time/resistance characteristics are specified in the Help file of objects.

/I characteristics of nonlinear resistances are assumed symmetrical, thus (0, 0) point should not be entered. If the saturation curve of a nonlinear inductor is symmetrical start with point (0, 0) and skip the negative points. The hysteresis loop of Type-96 reactors is assumed symmetrical, so only the lower loop of the hysteresis must be entered. The last point should be where the upper and lower curves meet in the first quadrant. If you specify a metal oxide arrester with MOV Type-92 component, ATPDraw accepts the current/voltage characteristic and performs an exponential fitting in the log-log domain to produce the required ATP data format.

.  4.58 – Nonlinear branch elements.

[此处图片未下载成功]

[此处图片未下载成功]

ATPDraw version 5.6

[此处图片未下载成功http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3]

Reference Manual

[此处图片未下载成功]

.11.4 Lines/Cables

Lines/Cables menu has several sub-menus for different types of line models. Available line models are: Lumped parameter models (RLC π, RL coupled), distributed parameter lines with constant (i.e. frequency independent) parameters, lines and cables with constant or frequency dependent parameters (Bergeron, PI, Jmarti, Noda or Semlyen), calculated by means of the LINE CONSTANTS, CABLE CONSTANTS or CABLE PARAMETERS supporting routine of ATP-EMTP.

.  4.59 – Line models with lumped parameters.

.11.4.1 Lumped parameter line models

Pi-equiv. 1: These line models are simple, lumped, non-symmetric π-equivalents of ATP

1, 2, 3 etc. branches of ATP.

Coupled 51: These line models are simple, lumped, non-symmetric mutually RL coupled

of Type-51, 52, 53 etc. branches of ATP.http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3  112

version 5.6

Reference Manual

Sym. 51:      These line models are symmetric with sequence value input. The line models

special applications of the RL coupled line models in ATP. The following selections are available on the three pop-up menus:

[此处图片未下载成功]

4.11.4.2 Distributed parameter line models

Distributed opens a popup menu where two different types of line models can be selected: Transposed lines or Untransposed lines. Both types are distributed parameters, frequency independent lines of class Bergeron. Losses are concentrated at the terminals (R/4) and of the mid-point (R/2). The time step has to be less than half the travel time of the line.

.  4.60 – Distributed transmission line models.

version 5.6

Reference Manual

lines (Clarke): Thehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3se components can be characterized as symmetrical, distributed parameter and lumped resistance models (called as Clarke-type in the ATP Rule-Book). Six different types are supported:

[此处图片未下载成功]

[此处图片未下载成功]

Untransposed lines (KCLee): Parameters of these nonsymmetrical lines are usually generated outside ATPDraw. These components can be characterized as untransposed, distributed parameter and lumped resistance models with real or complex modal transformation matrix (called as KCLee-type in the ATP Rule-Book). Double-phase and 3-phase types are supported: 4.11.4.3 LCC objects

this part of the program, you specify the geometrical and material data for an overhead line or a cable and the corresponding electrical data are calculated automatically by the LINE CONSTANTS, CABLE CONSTANTS or CABLE PARAMETERS supporting routine of ATP-EMTP. The LCC module supports line/cable modeling up to 21 phases.

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3arTo use the LCC module of ATPDraw the user must first select a line/cable component. The number of phases is selected internally in the LCC dialog box. This will display an object (3-phases default) in the circuit window that can be connected to the circuit as any other component. Clicking on this component with the right mouse button will bring up a special input dialog box  114

version 5.6

Reference Manual

Line/Cable Data dialog box with two sub-pages: Model and Data, where the user selects between the supported System type:

o o

Line: LINE CONSTANTS

Core Cables: CABLE PARAMETERS or CABLE CONSTANTS Enclosing Pipe: CABLE PARAMETERS or CABLE CONSTANTS

Model type of the line/cable :

Bergeron: Constant parameter KCLee or Clark models o PI: Nominal PI-equivalent (short lines)

Jmarti: Frequency dependent model with constanhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3t transformation matrix o Noda: Frequency dependent model

Semlyen: Frequency dependent simple fitted model.

Line/Cable Data dialog box completely differs from the Component dialog box of other

.3 of the Advanced Manual.

[此处图片未下载成功]

components, therefore it is described in chapter

.11.4.4 Read PCH file...

is able to read the .pch output files obtained by external run of ATP-EMTP’s LINE CONSTANTS or CABLE CONTSTANTS supporting routines. Selecting the Read PCH file... menu item, the program performs an Open Punch File dialog in which the available .pch files are listed. If you select a file and click Open, ATPDraw attempts to read the file and if succeed in creates a .lib file and stores it in memory in the Data Base Module format of ATP. When the .lib file is successfully created the icon of the new LCC component appears in the middle of the circuit window.

.1http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db31.5 Switches

supports most of the switch type elements in ATP, such as ordinary time- or voltage-controlled switches, options for modeling diodes, valves and triacs, as well as measuring and statistical switches.

Switches sub-menu contains the following switch objects:      Fig.  4.61 – Supported switch type ATP components.

version 5.6

Reference Manual

[此处图片未下载成功]

[此处图片未下载成功]

.11.6 Sources

popup menu under Sources contains the following items:           Fig.  4.62 – Electrical sources in ATPDraw.

version 5.6

[此处图片未下载成功]

Reference Manual

[此处图片未下载成功]

4.11.7 Machines

categories of electrical machines are available in ATPDraw: Synchronous Machines and Universal Machines. ATPDraw does not support machines in parallel or back-thttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3o –back.

.  4.63 – Supported electric machine alternatives.

Synchronous Machine models in ATPDraw have the following features/limitations:

and without TACS control. Manufacturers data. No saturation.

eddy-current or damping coils. Single mass.

Universal Machine models in ATPDraw have the following features/limitations:

Manual and automatic initialization.   SM, IM and DC type supported.

version 5.6

Manual

coil data (internal parameters). Manufacturers data in Windsyn. Saturation is supported in d, q, or both axes.

five excitation coils, sum d and q axis. Network option for mechanical torque only. Single torque source.

Component dialog box of Universal Machines is significantly different than that of the other

.2.2 of the objects. http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3A complete description of parameters in this dialog box is given in chapter

Manual. The Windsyn component depends on a compatible, external program called WindsynATPDraw.exe developed by Gabor Furst. The component takes manufacturers data as input and calles the Windsyn program to fit these to electrical universal machine data. Windsyn supports the following machine types; Synchronous machines with salient or round rotor with damping options. Induction machines with wound, single cage, double cage, or deep-bar rotors. The Windsyn component is documented it chapter  5.2.5 in the Advanced Manual.  The popup menu under Machines contains the following items:

[此处图片未下载成功]

[此处图片未下载成功]

4.11.8 Transformers

supports the transformer components; Ideal transformer, saturable transformer, BCTRAN and the Hybrid Transformer. The BCTRAN model is documented in chapters  5.6 and the Hybrid Modelhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 in chapter  5.7 of the Advanced Manual.

.64 – Transformer models in ATPDraw.  Fig.

ATPDraw version 5.6

Reference Manual

popup menu under Transformers contains the following items:

[此处图片未下载成功]

The characteristic of the nonlinear magnetizing branch of the three saturable-type transformers can be given in the Characteristic tab of the component dialog box. The saturable transformers have an input window like the one in Fig.  4.47. In this window the magnetizing branch can be entered in IRMS/URMS or IA/FLUXVs coordinates. The RMS flag on the Attributes page select between the two input formats. If the Include characteristic check box is selected on the Attributes page, a disk file referenced in the $Include field will be used in the ATP input file. If the nonlinear characteristic is given in IRMS/URMS, ATPDraw will calculate the flux/current values automatically and use http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3them in the final ATP input file.

BCTRAN transformer component provides direct support of BCTRAN transformer matrix modeling. The user is requested to specify input data (open circuit and short circuit factory test data) in BCTRAN supporting routine format, then ATPDraw performs an ATP run to generate a punch-file that is inserted into the final ATP-file describing the circuit. The user can specify where the factory test was performed and where to connect the excitation branch. The excitation branch can be linear or non-linear. In the latter case, the nonlinear inductors must be connected to the winding closest to the iron core as external elements.

BCTRAN dialog and the Component dialog box of the Saturable 3-phase SATTRAFO differ in many ways from the input data window of other objects. A more comprehensive description of

.6 and  5.2.1 of the Advanced Manual, respectively. the input parameters is givhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3en in chapters

Hybrid Transformer model is based on development made by Dr. Bruce Mork and his group at Michigan Technological University. It offers both advanced and simplified usage. The XFMR dialog box and the implementation is documented in chapter  5.7.2 of the Advanced Manual.

version 5.6

Reference Manual

.11.9 MODELS

the standard components, the user can create his/her own models using the MODELS simulation language in ATP [4]. ATPDraw supports only a simplified usage of MODELS. The user writes a model-file and ATPDraw takes care of the INPUT/OUTPUT section of MODELS along with the USE of each model. The following restriction applies:

INPUT, OUTPUT and DATA supported in the USE statement. Not possible with expressions, call of other models or specification of HISTORY or DELAY CELLS under USE

this feature rhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3equires knowledge about the syntax and general structure of MODELS language. There are two options for creating a model object in ATPDraw:

a support file manually under Object | Model | New sup-file and a corresponding .mod file.

Create a .mod file externally or a Model text internally and relay on ATPDraw for automatic identification and layout/icon.

Advanced part of this Manual Chapter  5.5 gives detailed information about both procedures and a general overview about the use of MODELS in ATPDraw. In this chapter only the automatic support file generation is introduced. The process normally consists of two steps:  1. To create a model file (.mod) containing the actual model description.

. To load this file via the Files (sup/mod)... or Type 94 sub-menus under MODELS

.  4.65 – Options under the MODELS sub-menu.

model

will load a simple,http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 default model and display it in the circuit window. Its input dialog box

.66 (no data or nodes). Click on the Edit button to modify the Model will look as shown in Fig.

directly or to import a model text from file or clipboard. In the standard text editor that pops up you can modify the Model text and import text via File|Import or Edit|Paste

[此处图片未下载成功]

. Click on Done in the main menu of the Text Editor when finished. ATPDraw will then try to identify the model and create the component definitions, including icon, see Fig.  4.67. Inputs and outputs are placed to the left and right of the icon, respectively. You can whenever you want go back and modify the Model text, and if you change the number of input and outputs the icon will be recreated.

version 5.6

Reference Manual

[此处图片未下载成功]

[此处图片未下载成功]

Fig.  4.66 – Model component dhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ialog box. And Text Editor

(sup/mod)...

MODELS | Files (sup/mod)... in the component selection menu performs an Open Model dialog box where the user can choose a model file name or a support file name. These files are normally stored under the folder. If a .mod file was selected ATPDraw interprets the file as shown in Fig.  4.67 and a model component with the corresponding definition and icon appears. If a support file with the same name as the model file exist in the same folder, this file is used instead as basis for the model definitions. In this case the new model object appears immediately

.67 does not show up. in the circuit window, i.e. the Information dialog shown in Fig.

.  4.67 – Interpretation of the model.

Component dialog box of model objects has a new input section Models below the DATA and

attributes as shown in Fig.  4.68. This newhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 section has two fields: Model which is disabled (but automatically follows what is defined in the Model text found using the Edit button)  and a Use As field for specification of the model_name in the USE model AS model_name

[此处图片未下载成功]

statement of MODELS. The Record button is used for output of internal model variables. On the Library page the link to the original support file on disk is given and a Reload option is made available. Remember that the original support file on disk not necessarily match the present Model text if the user has changed this.

version 5.6

Reference Manual

[此处图片未下载成功]

.  4.68 – The component dialog box of model object FLASH_1.

input/output to MODELS, the use of the model and interfacing it with the rest of the circuit

handled by ATPDraw, automatically. Model descriptions are written direhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ctly in the ATP file instead of using $Include. Blank lines are removed when inserting the model file in the ATP-file. The general structure of the MODELS section in the .atp input file is shown below:

/MODELS INPUT

v(CR30A)   IX0002 v(CR20A)   IX0003 v(CRZ2A) OUTPUT   GAPA

FLASH_1

------------------------------------------ Description of the model is pasted here ------------------------------------------ ENDMODEL

FLASH_1 AS FLASH_1 INPUT

:= IX0001   V2:= IX0002   iczn:= IX0003 DATA

:=       1.   Eset:=       9.   Fdel:=       4.   Fdur:=      20. OUTPUT

:=trip ENDUSE

version 5.6

Reference Manual

94

MODELS | Type 94|THEV, ITER, NORT, NORT-TR will load a corresponding default model component. You can then open the component which will bring up the Tyhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3pe 94 component dialog box as shown in Fig.  4.69. As for simple models you can then click on the Edit button to inspect or modify the type 94 models text. When you click on Done in the Text Editor ATPDraw

.67. Be aware of that tries to identify the model and then displays a message box similar to Fig.

name of the models must be six characters or less.  The bottom section of the input dialog has to the right four radio buttons: THEV, ITER , NORT

[此处图片未下载成功]

and NORT-TR for specification of the solution method for ATP when interfacing the Type-94 object with the rest of the electrical network. The Data, Node fields and the icon will update dependent on the choice of type. You can also specify the number of phases (#Ph: 1..26) in the component. Branch output and Record of internal variable are also available.

.  4.69 – Component dialog box of Type-94 model objects.

ihttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3nput and data values for a Type-94 object are loaded by ATP and the output of the object

also used automatically by ATP. Interfacing it with other components of the circuit is handled by ATPDraw. A Type-94 compatible .mod files must have a fixed structure and the use of such an object also requires special declarations in the ATP input file as shown next: Structure of a Type-94 compatible .mod file:

ind1n

----------------------------------------------------------------  | Internal circuit:  1-ground : L1       |       |                      |  |                                      1 o       |                      |  |                                            -  ground                  |  | Built for use as a 1-phase non-transmission type-94 Norton component  |   ------------------------------------------------------------- endcomment

------------------------------------------http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3----------------------------  | First, declarations required for any type-94 iterated model                 |  |   (the values of these data and input are loaded automatically by ATP)      |  |   (the values of these outputs are used automatically by ATP)               |  |   (DO NOT MODIFY THE SEQUENCING OF THE DATA, INPUT, AND VAR IN THIS GROUP)  |  |   (the names may be modified, except 'n')      ‘ ’                          |  |   (when built for n=1, the array notation is not required)                  |   ------------------------------------------------------------------- endcomment  DATA  n                    -- number of phases

dflt: n*(n 1)/2 -- number – conductances

version 5.6

INPUT v          -- voltage(t) at terminal 1        v0         -- voltage(t=0) at terminal 1        i0         -- current(t=0) into terminal 1  VAR   i          -- current(t) into terminal 1://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ar        -- Norton source(t timestep) at terminal 1        g          -- conductance(t timestep) at terminal 1

-- set to 1 whenever a conductance value is modified  OUTPUT i, is, g, flag

----------------------------------------------------------------------  | Next, declarations of user-defined data for this particular model           |  | (values which must be defined when using this model as a type-94 component) |   ------------------------------------------------------------------- endcomment  DATA  L1     -- [H] reference value of inductance L

----------------------------------------------------------------------  | Next, declarations private to the operation of this model                   |   ------------------------------------------------------------------- endcomment  VAR   st    -- used for converting Laplace s to time domain        L     -- [H] variable value of indhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3uctance L  INIT

:= 2/timestep  -- trapezoidal rule conversion from Laplace   L := L1             -- initialize variable inductance value   g:= 1/(st*L)        -- conductance converted from Laplace 1/sL  ENDINIT

-- L is constant in this example   IF t=0 THEN

:= 1          -- conductance values have been changed    i    := i0         -- t=0 current through L

:= -i0 -g*v0  -- –istory term for next step   ELSE

:= 0          -- reset flag

:= g*v -is    -- –pplying trapezoidal rule, calculate from v(t)    is   := -i -g*v    --–history term from trapezoidal rule, for next step   ENDIF  ENDEXEC ENDMODEL

Manual

use of a Type-94 Norton model in the ATPDraw generated input file is shown next.

Time varying inductor

LEFT        IND1N NORT                                                       1  &gt;DATA  L1           http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db30.1  &gt;END

Max/Min

is a special cost function or reporting component using Models. The component extracts a value from a simulation by communication with the LIS file. As default the minimum or maximum value of a single input signal is extracted, but the user can add more sophistication to this. Only the signal after a user selectable time Tlimit are identified. The component supports multiple run via ATP|Settings/Variables and contains a View module for displaying the result. A data parameter AsFuncOf can be used to pass a loop variable from the global Variables (if a number is specified here, the simulation number is used instead). The component is used extensively in circuit optimization.

.11.10 TACS

TACS menu gives access to most type of TACS components of ATP. The TACS sub-menu on the component selection menu contains the following items:

version http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db35.6

Reference Manual

[此处图片未下载成功]

.  4

[此处图片未下载成功]

.70 - Supporte– TACS objects.

.11.10.1 Coupling to circuit

Coupling to circuit provides an interface for TACS HYBRID simulations. This

must be connected with an electrical node to pass node voltages, or the branch currents / switch status to TACS. The type of the variable sent to TACS is controlled by the Type settings in the EMTP_OUT component dialog box. Users are warned that only single-phase electrical variables can be interfaced with TACS input nodes, this way. In case of 3-phase modeling, a splitter object is also required, and the coupling to circuit object must be connected at the single-phase side of the splitter as shown in Fig.  4.71.

[此处图片未下载成功]

[此处图片未下载成功]

.  4.71 - Coupling a 3-phase electrical node to TACS.

version 5.6

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3par125

Reference Manual

.11.10.2 TACS sources

[此处图片未下载成功]

4.11.10.3 TACS transfer functions

the older TACS transfer functions of previous ATPDraw versions are supported in version 3, but some of them has been removed from the component selection menu and replaced by a more general component: the General transfer function. This object defines a transfer function in the s domain and it can be specified with or without limits. The Order 1 component offers order 0/1 transfer function with a dynamic icon containing values and optional limits. Four more simple transfer functions are also supported: Integral, Derivative, first order High and Low pass filters.

[此处图片未下载成功]

[此处图片未下载成功]

4.11.10.4 TACS devices

version 5.6

Reference Manual

[此处图片未下载成功]

4.11.10.5 Initial conditions

initial condition http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3of a TACS variable can be specified by selecting TACS object (type 77) under the TACS | Initial cond. menu. The name of this component is INIT_T and its icon isINIT. 4.11.10.6 Fortran statements

component dialog box of the Fortran statements | General object provides a Type field where the user is allowed to specify the type of the object (input, output, inside) and an OUT field for the single line Fortran-like expression. These statements are written into the /TACS subsection of the ATP input file starting at column 12.

Fortran statements | Math and Logic sub-menus include additional simple objects for the basic mathematical and logical operations. General

version 5.6

[此处图片未下载成功]

127

Reference Manual

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

Fortran statements / Math Fortran statements / Trigonom Fortran statements / Logihttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3c 128

version 5.6

[此处图片未下载成功]

Reference Manual

[此处图片未下载成功]

4.11.10.7 Draw relation

you select TACS | Draw relation, the mouse cursor will change to a pointing hand and the program is waiting for a left mouse click on a circuit node to set the starting point of a new relation. You can then draw multiple relations until you click the right mouse button or press the Esc key. Relations are used to visualize information flow into Fortran statements. These objects are drawn as blue, dashed connections, but have no influence on the component connectivity. You can work with relations exactly the same way as with connections: relations can be selected, rotated, deleted, or moved to another position.

.11.11 User Specified

the Library item will draw the predefined user specified object LIB.

object has no input data and cannot be connectehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3d with other objects because

has no input or output nodes.

.  4.72 - Supported user specified objects.

this object will result in a $Include statement in the ATP-file inserted in the LIBBRANCH part. No parameters are used in this case. The User specified section at the bottom contains an Edit button that brings up the Text Editor where the user can edit or import an external text. The user can type in the name of the component in the $Include field. The text will be dumped to a file with this name and extension .lib and location in Result Directory (same as ATP file) when the ATP file is created.

to the Library component but in addition it allows the user to choose under which REQsection in the ATP file to insert the text. The input dialog of this component contains a

memo field where the user can write in free format tehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3xt with a row and column indication below. The Additional section at the bottom contains an Edit button that brings up a more advanced Text Editor that allows the user to import a text from file of clipboard. This Text Editor also has a right-click context menu with an Insert option of 50 predefined request cards. There is no $Include field in this component because the text will be inserted directly into the ATP file. Instead the user can select the section; REQUEST, TACS, MODELS, BRANCH, SWITCH, STATISTICAL, SOURCE, INITIAL, OUTPUT, LOAD FLOW, MACHINE type 59/56, UNIVERSAL MACHINE, FREQUENCY COMP. The Order number can be used for fine tuning of the location within each section (together with ATP|Settings/Format-Sorting by Order). The three character text in the icon will adapt to the selected section.

version 5.6  129

Reference Manual

. 1-ph

Ref. 1-ph will draw http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3the object LIBREF_1. This object has zero parameters and two nodes. Reference objects are not represented in the ATP input data file, but serve only as visualization of connectivity.

. 3-ph

Ref. 3-ph will draw the object LIBREF_3. This object has zero parameters and two nodes. Reference objects are not represented in the ATP input data file, but serve only as visualization of connectivity.

...

the standard components, the user is allowed to create User Specified components. The usage of this feature requires knowledge about ATP's DATA BASE MODULARIZATION technique. The procedure that is described in the Advanced part of this Manual consists of two steps:

. Creating a new support file (.sup) using the Library | New object|User Specified menu.

. Creating a Data Base Module file (.LIB), which describes the object.

Files...http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 in the component selection menu executes the Open Component dialog and the existing support files in the directory are listed. If you select a .sup file from the list and click on the Open button, the icon of the object will appear in the middle of the active circuit window. In the dialog box of this component type there is a User Specified section with an Edit button which will bring up the Text Editor where a .lib file can be imported. A checkbox Send parameters is used if the library file is on the Data Base Module format with external parameters.

second checkbox Internal phase seq. is used if the phase extension 'A', 'B'… is hard coded inside the Data Base Module and only the five character root node name should be sent. Henceforth the user specified objects operate similarly than standard objects.

.11.12 Steady-state

frequency scan and load flow

.  4.7http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db33 - Supported HFS components.

Harmonic Frequency Scan (HFS) is one of the options under ATP | Settings / Simulation. General load flow specification is given under ATP|Settings/Load flow.

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

version 5.6

Reference Manual

[此处图片未下载成功]

[此处图片未下载成功]

Selecting HFS under ATP | Settings / Simulation will run

ATP data case so many times as specified in the

source component dialog box. The frequency

the harmonic source will for each ATP run be

. In the example shown at left, 5 harmonic

are specified in the F/n column, and the ATP

case will run 5 times.

.  4.74 - Specification of harmonic source frequencies.

the first run the source frequency will be 1x50 http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3Hz, the second run 5x50 Hz etc. up to the fifth run f = 11x50 Hz = 550 Hz. The Freq. value specified by the user under ATP | Settings / Simulation is used here as base frequency. The source frequency can also be specified directly in Hz and in such case the first F/n must be greater or equal to the Power Frequency. Specifying the

.74. frequencies F/n like 50, 250, 350, 450, and 550 would be equivalent to what is shown in Fig.

.11.13 Standard Component...

ATPDraw the standard component support files are stored in a single file called ATPDraw.scl. The Standard library dialog is the container of supported circuit objects in alphabetical order. Any component can be selected from this list, then the object's icon appears in the circuit window exactly the same way as after other selections in the component selection sub-menus.

files of the present and even all retired objects (whhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ich once were supported in earlier program versions, but have been removed from the component selection menu) are included in the standard library. An old circuit file may of course contain such an older object, which are also supported internally in ATPDraw and the program will produce correct output.

version 5.6  131

Reference Manual

.11.14 Plugins

Plugins Item points to a user defineable disk structure with project files (.acp) and sub-folders. This thus gives an easy access to a user defineable library of sub-circuits for import. This is similar to File|Import but enables the possibility of direct access. The Plugin directory is defined under Tools|Options/Files&amp;Folders.

.  4.75 – Example of Plugins menu.  ATPDraw version 5.6

[此处图片未下载成功]

ATPDraw version 5.6  133

Advanced Manual

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3s chapter gives an overview of several more advanced features in ATPDraw: Grouping,  special components, usage of the integrated LINE/CABLE CONSTANTS, BCTRAN and the UNIVERSAL MACHINE support, including the Hybrid Transformer model and Windsyn. This chapter also describes how to use MODELS in ATPDraw and how to create new user specified object by means of ATP's $Include and DATA BASE MODULARIZATION features. You will not be shown how to create the example circuits, but these project files (Exa_*.acp) are part of the ATPDraw distribution. To load these example circuits into ATPDraw, use the File | Open command (or Ctrl   O) and select the file name in the Open Project dialog box.

.1 Grouping: an ATPDraw feature for multilevel modeling

grouping feature in ATPDraw allows multilevel modeling by replacing a group of objects with a single icon in an almost unlimited numbers of layers. The grouping structure cahttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3n be imagined as a multi-layer circuit, where the Edit | Edit Group brings you one step down in details, while the Edit |

[此处图片未下载成功]

Edit Circuit menu brings you one step back. This feature increases the readability of the circuit and the feature is especially useful for TACS blocks or frequently reused circuit elements. The grouping feature is demonstrated by re-designing the circuit Exa_4.acp in the ATPDraw distribution. This circuit is an induction machine supplied by a pulse width modulated (PWM) voltage source. The induction machine is represented by a Universal Machine type 3 with a typical mechanical load.

.  5.1 - An induction machine supplied by a pulse width modulated voltage source.

process of creating a group is as follows:

Select a group of components (inside the polygon in Fig.  5.1). Edit|Select|Inside.

Select Edit| Compress in the main menu (or Shifthttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 right mouse click   Compress).

version 5.6  135

Advanced Manual

selecting a group the

[此处图片未下载成功]

Edit |Compress command will replace it with a single icon. First the selected sub-circuit is redrawn alone in the middle of the circuit window and the Compress dialog

.2.  appear as shown in Fig.

.  5.2 - The Compress dialog window.

the Compress dialog box the user can specify the external data and nodes of a group of components. The selected data and nodes appear as input in the group object that replaces selected group and their values are automatically transferred.

Objects all the components in the group are listed with their name (support file) followed by '/' and their Label (which is again specified in the Component dialog box). When you click on one of the components it's available data and nodes apphttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ears under Available listed by the data's/node's name followed by its value. The component is also drawn in a lime color in the circuit window. The already selected external data/node belonging to this component is also drawn with a lime color in the Added to groups.

can then select a parameter and click on the &gt;&gt; button to transfer it to the Added to list. Selected nodes in the Available node list is also draw in a lime color in the circuit window. If the data/node is already added the corresponding item in the Added to lists is highlighted, and you are not allowed to select it twice. Nodes in the Added to list are drawn enclosed by a red ring in the circuit window as shown for the 3-phase node of the Splitter chosen to the external in Fig.  5.2. The node position 2 is chosen for this node and this is the middle left standard position.

icon is chosen for this group object. The Grouphttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 name PWM is used in the icon and displayed as an indicator in the Component dialog, as shown in Fig.  5.5. The Auto pos option is available for vector icons only. Later in this example we will change the icon to bitmap style.

data and nodes listed in the Added to groups will be the external attribute of the new group object. You can also for each selected node specify it's position relative to the object's. The node positions different from the default 1-12 must be specified by selecting Position 0 and then give the relative coordinates of the node in the Pos.x and Pos.y fields. The x-axis is oriented to the right and the y-axis downwards. The Auto pos button is only available for Vector graphic icons. Selected data and nodes can also be removed from the Added to groups by clicking on the &lt;&lt; button. As all other components the group object is limited to 64 data and 32 nodes. When later

vehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3rsion 5.6

Advanced Manual

the component dialog box for the group object the selected data and node parameters will

[此处图片未下载成功]

appear as input possibilities and the values will automatically be transferred to the sub-group.

is also possible to change the data/node labels by double-clicking on the texts in Added to lists. Important! Two or more data labels with the same name are treated as a single data in the component dialog box.

.  5.3 - Name and position of the external nodes of the group.

Compress process continues in Fig. 5 .3 by selection of the external data all belonging to the PULSE_03 object. Click on OK when you have finished. If you need to change the group attributes, you can later selecte the group and once again choose Edit|Compress to reopen the Compress dialog. In such case a Keep icon checkbox enables you to preserve http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3the the groups icon.

selecting all the required data and nodes click on

, then a object will automatically be created. The

content disappears and the new group object is

in the circuit window as shown in Fig.  5.4. The

is then allowed to connect this group object to the

of the circuit.

.4 - On return from the Compress the circuit is redrawn. Fig.

objects operate like any other objects. You can drag and place the new group in the desired location. The component dialog of the group can be opened by a right or double mouse click and it appears as shown in Fig.  5.5. The data and node values are as specified under Fig.  5.2 and Fig.

.3.

changing the data parameter in this window the value will also be transferred to the member components. A change in the node name will be transferred in the same way. In this particuhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3lar case the Fortran TACS objects are connected to the single-phase side of a splitter. The name of the 3-phase node V will be transferred as real names

[此处图片未下载成功]

VC, VB and VA (from left to right) at the Fortran objects' output node. The user must follow this phase sequence in the PWM group object, too.

version 5.6  137

Advanced Manual

[此处图片未下载成功]

.  5.5 - Opening the new group dialog box.

[此处图片未下载成功]

Compress process for the mechanical load of the induction machine and the component dialog of the new group can be seen in Fig.  5.6 and Fig.  5.7, respectively.

.  5.6 - Selection of data values and external nodes for the mechanical load group.

version 5.6

Advanced Manual

[此处图片未下载成功]

.  5.7- Component dialog box of the mechanical load grouhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3p-object.

view/edit a group the user must first select it and then click Edit | Edit Group in the main menu (or Ctrl G). The group is then extracted on the current circuit window. Actually, the grouping structure can be taken as a multi-layer circuit, where the Edit Group brings the user one step down in details, while the Edit Circuit brings him one step back. The group is editable in normal way, but the user can't delete components with reference nodes or data in the mother group. I.e. components having been referenced in one of the Added to group: lists cannot be deleted. If the user attempts to do so, a &quot;Marked objects are referenced by compressed group...&quot; warning message reminds him that the operation is not allowed. Selecting the main menu Edit | Edit Circuit (or short key Ctrl H) will close the group edit window. It is possible with several levels of groups in the circuit. The maximum number of group levhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3els is 1000.

customize the icon, click the Edit definitions speed button in the lower left corner of the Component dialog box as shown in Fig.  5.5. The icon editor will appear where the user is free to modify the icon. Fig.  5.8 shows the Exa_4.acp circuit after grouping the PWM-source and the mechanical load and modifying their icons. Such process is convenient for documentation purposes, because increases the readability of the circuit.

[此处图片未下载成功]

5.8 - The icon of the PWM source and the load group has been customized. Fig.

version 5.6  139

Advanced Manual

[此处图片未下载成功]

[此处图片未下载成功]

Fig.  5.9 - Customizing the icon of the PWM source and TRQ mechanical torque model. The icon is oriented so that node connections fit with border position 2 (left, middle).

.1.1 Grouping nonlinear objects

non-linearity can also be extehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3rnal data in a group object. Up to three objects can share the same external nonlinearity. As an example, this section shows how to create a 3-phase, Type-96 hysteretic inductor. You can draw a circuit as shown to the left of Fig.  5.10. To create a group mark the 3 single-phase inductor and the splitter then select Edit | Compress. The data CURR, FLUX and RESID are set as external parameters for all the three inductors. The non-linearity button under Added to group is checked and the Add nonlinear button is checked, too for all three inductors.

you press OK the group object is created. The group dialog box shown in Fig.  5.11 contains only one entry for CURR, FLUX, RESID, and FL(0) which are used for all phases, although 3 copies of them are present in the data structure. This results in 26 free data cells available for the nonlinear characteristic (64-3*4)/2 = 26). Only one characteristic is entered in the grhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3oup's dialog box and it is later copied back to all the three inductors. If the 26 data points were insufficient to describe the characteristic as you wish, select the Include characteristic option and specify the characteristic in a disk file. The name of that file must be entered in the $Include field.

new 3-phase Type-96 group object can be stored as a project file in a special library location and later copied into any circuit using the File | Import command, or place in the Plugins library.

version 5.6

Advanced Manual

[此处图片未下载成功]

.  5.10 - Creating a 3-phase hysteretic inductor.

.  5.11 - Nonlinear characteristic of the 3-phase Type-96 group

(notice that only one characteristic is specified, that is used for all phases).

can customize the group icon as shown in Fig.  5.11 (vector icon illustrated in this casehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3). The hysteresis loop originates from the original inductor icon. This is done by executing the next sequence of operations: click on Edit definitions and go into the  vector icon editor (leftmost speed button). The default icon is shown as a box with the text 'GROUP' and 'nl96_3d'. Modify

version 5.6

[此处图片未下载成功]

141

Advanced Manual

'GROUP' text to 'GRP' and move it toward the upper left corner of the box. Modify the text 'nl96_3d' to 'D' and choose font 'symbol' (you may also increase the font size and pick a different color) and move it towards the lower right corner of the box. Now choose File|Append std and choose the standard icon NLIND96. Adjust the left and right node connections. Click on Done.

.2 Non-standard component dialog boxes

component dialog box in which the user is allowed to change the object's attributes shows a considerable similarithttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3y nearly for all components: on the Attributes page the components data and nodes can be specified, on the optional Characteristic page you specify the input characteristic of non-linear components.

following components deviate somewhat from the above description:

3-phase transformer (SATTRAFO)

machine (UM_1, UM_3, UM_4, UM_6, UM_8)

/ Systematic switch (SW_STAT, SW_SYST)

source (HFS_SOUR)

manufacturers data UM component.

additions comes Models and User Specified component, explained later.

.2.1 Saturable 3-phase transformer

component dialog box of this transformer model is shown in Fig.  5.12. This dialog box also has an Attributes and a Characteristic page, but the former is largely differs from the standard layout. The function of the Order, Label, Comment and Output fields arehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 the same as on any other component dialog boxes, the meaning of the other fields are given next. The pair Io, Fo defines the magnetizing branch inductance at steady state. Rm is the resistance of the magnetizing branch representing the hysteresis and eddy current losses of the iron core. Io, Fo, Rm may be left blank if the magnetizing branch is neglected in the simulation. Checking the 3-leg core turns the transformer into a TRANSFORMER THREE PHASE type with high homopolar reluctance that can be specified in the appearing R0-field. With the button 3-leg core unchecked, the model is a saturable transformer with low homopolar reluctance (e.g. a 3-phase transformer with at least one delta winding).

the RMS button enables specification of the saturation characteristic in rms values for current and voltage on the Characteristic page. A conversion to flux-current values is performed internally in ATPDraw. If thehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 button is unchecked, normal flux-current values should be entered. The tertiary winding can be turned on or off by checking the 3-wind. button. The nominal voltage of the transformer windings is given in volts. The short circuit inductances may be specified in

[mH] if Xopt. parameter is 0 (default) on the ATP | Settings / Simulation page. Otherwise, the impedance is given in [Ω] at frequency Xopt.

coupled in wye, delta, auto with all possible phase shifts are supported. In addition zigzag configuration can be selected with arbitrary phase shift from &lt;-60,0&gt; &lt;0,60&gt;. In this case the winding is split in two parts internally and the leakage inductance recalculated.

version 5.6

Advanced Manual

[此处图片未下载成功]

.  5.12 - General saturable transformer dialog.

Saturable 3-phase object is found under Transformhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ers in the component selection menu and it can be edited and connected to the main circuit as any other components.

Help button at the lower right corner of the dialog box displays the help file associated with the SATTRAFO object. This help text briefly describes the meaning of input data values: Name : SatTrafo - General saturable transformer. 3 phase. 2 or 3 windings.

, Delta with all phase shifts. Auto, and Zigzag.

: BRANCH

:    Io= Current [A] through magnetizing branch (MB) at steady state.

= Flux [Wb-turn] in MB at steady state.

pair Io, Fo defines the inductance in MB at steady state.

= Resistance in magnetizing branch in [ohm]. 5-leg core or 3-leg shell.               The magnetizing branch is always connected to the PRIMARY winding and Rm               is referred to this voltage.

= Reluctance of zero-sequence air-return path for flux. 3-lehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3g core-type          Vrp= Rated voltage in [V] primary winding (only the voltage ratios matter).           Rp= Resistance in primary winding in [ohm].

= Inductance in primary winding in [mH] if Xopt.=0

in primary winding in [ohm] if Xopt.=power freq.

= Rated voltage in [V] secodary winding.

= Resistance in secondary winding in [ohm].

= Inductance in secondary winding in [mH] if Xopt.=0

in secondary winding in [ohm] if Xopt.=power freq.

= Rated voltage in [V] tertiary winding.

= Resistance in tertiary winding in [ohm].

= Inductance in tertiary winding in [mH] if Xopt.=0

in tertiary winding in [ohm] if Xopt.=power freq.                   RMS= unchecked: Current/Flux characteristic must be entered.

:   Irms/Urms characteristic must be entered.

performs a SATURATION calculation.

-lehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3g core = checked: 3-leg core type transformer assumed. TRANSFORMER THREE PHASE               unchecked: 5-leg or 3-leg shell type assumed. TRANSFORMER.

-wind.= turn on tertiary winding.

specified the magnetization branch output (power&amp;energy not supported).      Node :     P= Primary side. 3-phase node.

version 5.6  143

S= Secondary side. 3-phase node.

= Neutral point primary side.

= Neutral point secondary side.

= Tertiary side. 3-phase node.

= Neutral point tertiary side.

= Internal node, connection of the magnetization circuit with saturation. The coupling is specified for each winding, with four coupling options: Y, D, A, Z   All phase shifts are supported.

note on Auto-transformers:

primary and secondary windings must be of coupling A(uto).

note on ZigZag-transformers:

thishttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 type the user can specify a phase shift in the range &lt;-60,0&gt;&amp;&lt;0,60&gt;.

that the values -60, 0 and  60 degrees are illegal (as one of the winding parts   degenerates).

phase shift is given relative to a Y-coupled winding.

the primary winding is Zigzag-coupled, all other windings will be shifted with it.   If the primary winding is D-coupled, 30 deg. must be added/subtracted to the phase     shifts.

negative phase shifts the phase A winding starts on leg 1 (called z with voltage   Uz) and continues in the opposite direction on leg 3 (called y with voltage Uy).

negative phase shifts the phase A starts on leg 1 and continues in the opposite    direction on leg 2.

normal situation is to specify a phase shift of  /- 30 deg. in which case the two   parts of the winding have the same voltage level and leakage impedance.

general the ratio between the http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3second part of the winding Uy and the first part Uz   is n=Uy/Uz=sin(a)/sin(60-a) where a is absolute value of the phase shift.

gives:

=U/(cos(a) n*cos(60-a)) and Uy=Uz*n

=L/(1 n*n) and Ly=Lz*n*n, Rz=R/(1 n) and Ry=Rz*n

Lz and Ly are the leakage inductance of each part of the winding (L is the       total leakage inductance) and Rz and Ry are the winding resistance of each winding     part (R is the total).

parameters Uz, Uy, Zz, and Zy are automatically calculated by ATPDraw based on     the equivalent parameters U and Z and the phase shift, a.

: It's possible to enter 23 points on the current/flux characteristic.

required menu is performed immedeately after the input menu.

points should be entered as increasingly larger values.

point (0,0) is not permitted (added internally in ATP).

: IV.E.1-2 or 3. Advancedhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 Manual

.2.2 Universal machines

of electrical machines in version 3 of ATPDraw has been updated substantially to provide a user-friendly interface for most of the electrical machine modeling options in ATP. Supported Universal Machine (UM) types are:

Synchronous machine (UM type 1) Induction machines (UM type 3 &amp; 4) DC machine (UM type 8) Single-phase machine (UM type 6)

component dialog box of the Universal Machine object is substantially differs to the standard dialog box layout, as shown in Fig.  5.13. In the UM component dialog box the user enters the machine data in five pages: General, Magnet, Stator, Rotor, Init. Several UM models are allowed with global specification of initialization method and interface. These Global options can be specified under ATP | Settings / Switch/UM.

the General page data like statorhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 coupling and the number of d and q axis coils are specified. On the Magnet. page the flux/inductance data with saturation are specified, while on the Stator and Rotor pages the coil data are given. Init page is for the initial condition settings.

version 5.6

Advanced Manual

[此处图片未下载成功]

Fig.  5.13 - Universal machine input dialog.

dialog boxes for all the universal machines are similar. The type 4 induction machine does not have the Rotor coils group, since this is locked to 3. None of the type 3 and 4 induction machine have the field node of course.

single-phase machine (type 6) and the DC machine (type 8) do not have the Stator coupling group. For the type 6 machine the number of d-axis is locked to 1. Even if the number of rotor coils or excitation coils can be set to maximum 3, only the first d-axis coils will have exterhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3nal terminals for a type 1, 6, and 8 machine. The other coils will be short circuited. Rotor coils are short circuited in case of type 3 machine, while the type 4 machine has an external terminal for all its 3 coils.

.  5.14 shows the various pages for universal machine data input (induction machine, type 3). The buttons under the Saturation on the Magnet. page turns on/off the various saturation parameters for the d- and q-axis. This is equivalent to the parameter JSATD and JSATQ in the ATP data format. Selecting symm is equal to having JSATD=5 and JSATQ=0 (total saturation option for uniform air gap).

the Stator page, you specify the Park transformed quantities for resistance and inductance for the armature winding. The number of coils on the Rotor page and on the Init page for manual initialization adapts the specification of the number of rotor coils. First the d-axis coils are listed then http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3comes the q-axis coils.

function of the Order, Label, Comment fields are the same as on any other component dialog boxes. The Help button at the lower right corner of the dialog box displays the help file associated with the UM objects.

version 5.6  145

Advanced Manual

[此处图片未下载成功]

.  5.14 - Data pages of the universal machines dialog box.

Help text briefly describes the meaning of input data values and node names as the example shows next for UM type 1 (Synchronous machine):

:

page:

pairs - Number of pole pairs

- Rotor-speed iteration-convergence margin.

- Override steady state frequency.

coupling

between Y, Dlead (AC, BA, CB) and Dlag (AB, BC, CA)

Y turns neutral node Neut on.

coils

the number ofhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 d- and q- axis rotor coils. Maximum total             number is 3. Only terminals for 1st d-axis coil. The other coils             are assumed short circuited.

of mode of initialization and interface.

under the main menu ATP|Settings/Switch/UM for each circuit.      Stator page:

version 5.6

Specify resistance and inductance in Park transformed

(d- q- and 0- system). All inductances in H or pu.

page:

total number of coils are listed and given data on the Rotor           page. First the d-axis coils then the q-axis coils are listed.

resistance and inductance for each coil. All the coils           except the first is short circuited. All inductances in H or pu.      Magnet. page:

- d-axis magnetization inductance.

- q-axis magnetization inductance.

on/http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3off the saturation.

. is equal saturation in both axis, specified only in d.

- d-axis saturated inductance.

- d-axis flux-linkage at the saturation knee point.

- d-axis residual flux-linkage (at zero current).

- d-axis saturated inductance.

- q-axis flux-linkage at the saturation knee point.

- q-axis residual flux-linkage (at zero current).

! All inductances in H or pu.

page:

conditions dependent on manual or automatic

is chosen under ATP|Settings/Switch/UM

:

- initial stator coil (phase) voltage [V].

- angle of phase A stator voltage [deg].

:

stator current in the d- q- and 0-system

rotor current inn all coils

- initial mechanical speed [mech rad/sec or unit]

- initial phttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3os of the rotor [elec rad]

:

=1: air gap torque

=2: 1   d-axis common flux

=3: 2   d-axis magnetization current

=1: rotor shaft speed in [rad/sec]

=2: 1   q-axis common flux

=3: 2   q-axis magnetization current

=checked: rotor position in [mech rad]

=checked: all physical coil currents

:

- 3-phase armature output terminal.

_NODE - air-gap tourque node.

- Pos. terminal of exitation rotor coil.

(the other coils are grounded)

- Neg. terminal of exitation rotor coil.

- torque-source node for automatic initialization.

- field-source node for automatic initialization.

- Neutral point of Y-coupled stator coils.

Manual

final section of the Help file describes the equivalent electrical network of the mechanical networkhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 for torque representation:

mass (moment of inertia)   Capacitance          (1kg/m2   1 Farad) Shaft section (spring constant)   Inverse inductance. (1 Nm/rad   1/Henry) Shaft friction (viscous damping)   Conductance.       (1 Nm/rad/s   1/ohm) Angular speed   Voltage      (1 rad/s   1 Volt)

Current             (1 Nm   1 Amp)

Charge               (1 rad   1 Coulomb)

version 5.6  147

__       __                     ____ ___oooo_______________

|  |     |  |                   |    |          |    |     |

|J1| K1  |J2|  --&gt; T           _|_   &lt;         _|_   &lt;     |

==|  |=====|  |====      ====&gt;   ___C1  &gt;R1      ___C2  &gt;R2  O I

|  |     |  |                   |    &lt;          |    &lt;     |

|__|     |__|                   |    |          |    |     |

D2

=J1, C2http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3=J2, R1=1/D1, R2=1/D2, L1=1/K1, I=T

Manual

.2.3 Statistic/systematic switch

of statistic/systematic switches in version 3 of ATPDraw has been made more general by introducing the independent/master/slave concept. The component dialog boxes of the statistical switches slightly differs however from the standard switch dialog box layout as shown in Fig.  5.15.

user can select the Switch type in a combo box out of the supported options: Independent, Master or Slave. This will also enable the possible input fields and change the number of nodes (note that slave switch has 4 nodes). The Distribution for the statistical switch takes into account the specification of the IDIST parameter on the miscellaneous switch card (ATP | Settings / Switch/UM). Selecting IDIST=1 will disable the Distribution group and force Uniform distribution. The Open/Close radio buttons select if the switchttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3h closes or opens with Ie as current margin for opening switches. The number of ATP simulations is set by the miscellaneous switch parameter Num. on the ATP | Settings / Switch/UM page. This value influences the 1st misc. data parameter NENERG of ATP. ATPDraw sets the correct sign of NENERG: i.e. &gt; 0 for statistic or

[此处图片未下载成功]

&lt; 0 for systematic switch studies. The function of the Order, Label, Comment and Output fields are the same as for any other standard components.

version 5.6

Advanced Manual

[此处图片未下载成功]

[此处图片未下载成功]

Fig.  5.15 - Dialog box of the statistic switch (top) and data windows of the systematic switch.

Help button at the lower right corner of the dialog box displays the help file associated with the object. This text briefly describes the meaning of input data values and node names as shown below:

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3_STAT -  Statistic switch.

: Select uniform or gaussian distribution.

IDIST=1 under ATP|Settings/Switch/UM only uniform is possible.    Open/Close: Select if the switch closes or opens.

margin available for opening switch.

= Average switch opening or closing time in [sec.]

Slave switches this is the average delay.

.= Standard deviation in [sec.].

Slave switches this is the deviation of the delay.

= Switch opens at a time T&gt;Tmean and the current through

switch is less than Ie.

type:

: Two nodes

: Two nodes. 'TARGET' punched. Only one is allowed.          SLAVE      : Four nodes. Specify node names of MASTER switch.          The icon and nodes of the objects adapt the switch type setting.    Node:  SW_F= Start node of switch.

_T= End node of switch.

_F= Sthttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3art node of the MASTER switch

_T= End node of the MASTER switch

_SYST -  Systematic switch.

= When ITEST=1 (ATP|Settings/Switch/UM)

= When ITEST=0 (ATP|Settings/Switch/UM)

= For SLAVE switches. If ITEST=0 : T=Tmid.

= Size of time increment in [sec.].

= Number of time increments.

type:

: Two nodes

: Two nodes. 'TARGET' punched.

: Four nodes. Specify node names of MASTER switch.          The icon and nodes of the objects adapt the switch type setting. Node :    SW_F = Start node of switch.

_T = End node of switch.

_F = Start node of the MASTER switch

_T = End node of the MASTER switch

.2.4 Harmonic source

component dialog box of the Harmonic source that is used in HFS studies deviates somewhat from the standard source dihttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3alog box layout as shown in Fig.  4.74.

version 5.6  149

Advanced Manual

HFS under ATP | Settings / Simulation the ATP will

the case so many times as specified in the Harmonic

component dialog box. The frequency of the harmonic

will for each ATP run be incremented. The user

the source type by the Voltage or Current radio

. In the example shown here, the data case will run 5

because the F/n column has 5 harmonics entered.

.16 - Harmonic source dialog box.  Fig.

base frequency here is the Freq. value specified under ATP | Settings / Simulation. The amplitude and angle of the F/n' th harmonic source is given in columns Ampl. and Angl.

.2.5 Windsyn component

is a program by Gabor Furst in Vancouver-Canada. It takes manufacturers machine data as inpuhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3t, makes a fitting and produced an electrical universal machine model with startup. This facilitates the usage of electrical machines in ATP/ATPDraw considerably. Seven electrical different machine types are supported by Windsyn; Induction machines (wound, single cage, double cage, and deep-bar rotors), Synchronous machines (salient rotor; d-damping, dq-damping, round rotor; dq-damping).

machine number is used in the control process of the machine, but this number is automatically assigned by ATP as the data file is processed (machine number=sequence in the file). The ATPDraw compatible version of Windsyn is completely transparent related to the machine number. In the newer ATP version all UM machines can have the header (INPU (units), INITUM (initialization method), ICOMP (solution method)) included, but only the settings of the first machine will be used.

ATPDraw compatible version of Windshttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3yn is modified to accept an input file on its command line and automatically update and jump to the input screen. The input file is a simple, free format, text based file starting with ‘WindSyn Data’ and ending with ‘End of WIS data’. ATPDraw creates an input file from scratch called atpdraw.wis and dumps it to the same directory as the windsyn.exe file. The Windsyn is called as Path.exe atpdraw.wis, INITUM, ICOMP. The Windsyn program is documented separately.

just dumps a dat-file, and ATPDraw calls  ATP to produce the lib-file in data base module format. The call to the lib-file is ‘$Include, Name, BUS, ROTM, TORQUE, EXFD, MachineNumber#’.

version 5.6

Advanced Manual

[此处图片未下载成功]

.  5.17 - Windsyn dialog box in ATPDraw.

.  5.17 shows the Windsyn input dialog in ATPDraw. It follows the same design as most compohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3nents. The input data consists of the standard Data grid to the left and a page control at the bottom. On the Windsyn page the user can select the type of machine and give the machine model a name that is used in the final $Inlude call. The current machine number is presented to the user, but this number could change as the circuit develops. As default an induction machine with wound rotor is assumed. If the user changes the machine type under Kind the Data grid is automatically updated. If the Kind is changed from induction to synchronous machine or vice versa new default values are read in. In the background there are actually two support files; WisInd.sup and WisSyn.sup, stored in ATPDraw.scl containing icon, help, default values, and units. On the ‘Run data’ page the user can set the start-up options for the machine dependent on the machine type and initialization INITUM set under ATP|Settings/Switch/UM.

order to use http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3the Windsyn component in a data case the user has to run the Windsyn program via the Run Windsyn button. Then the input file to Windsyn atpdraw.wis is created and Windsyn executed. While Windsyn is running the text &quot;Windsyn is running (ESC)&quot; is displayed. ATPDraw waits for Windsyn to terminate befor reading in the result files. The waiting process can be interupted by pressing the escape key. This might be needed if Windsyn terminates incorrectly. In Windsyn the user can change the machine model and in the end create new output files (Save Data followed by Exit). The output/result files are then automatically loaded by ATPDraw and a $include file is created as seen when clicking the Edit lib-file button. It is possible to directly import a lib-file here and thus omitting the Windsyn step. Both the wis-file and the lib-file are read and stored in memory in the data structure of ATPDraw. The final lib-file is dumped to diskhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 in the Result Directory with a name specified in the Name field (do not enter path or '.lib' as this is added automatically). The Result Directory is the same location as the ATP-file. As all lib-files (user specified, lcc and windsyn) are dumped to this directory file name

version 5.6  151

Advanced Manual

can occur if components of different class have the same name. See the prefix options under Tools|Options/View/ATP.

adds a TACS control module to the machine. In this model there are a number of predefined names not dummy declared. So watch out for unexpected name sharing. In all cases

[此处图片未下载成功]

the machine number is added at the end of the node names as indicated with the 'n#' character. This can be a two digit parameter.

.18. Setup of Windsyn in ATPDraw is done under Tools|Options/Preferences, as shown in Fig.

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3par.  5.18 - Windsyn ( ATP and Plot program) setup in ATPDraw.

.3 Using the integrated LCC object for line/cable modeling

integrated LCC objects in ATPDraw are based on the LINE CONSTANTS, CABLE CONSTANTS or CABLE PARAMETERS supporting routines of ATP-EMTP. The user must first describe the geometry of the system and the material constants and ATPDraw then performs an ATP run to process this data case and converts the output punch-file containing the electrical model of the line or cable into standard lib-file format. This lib-file will then be included in the final ATP-file via a $Include call. The idea in ATPDraw is to hide as much as possible of the intermediate ATP execution and files and let the user work directly with geometrical and material data in the circuit. Only those cases producing an electrical model of the line or cable are supported in ATPDraw.

use the built-in lhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ine/cable module of ATPDraw the user must first select a line/cable component under Lines/Cables | LCC item in the selection menu, as shown in Fig.  5.19. This will display a component in the circuit window that is connected to the circuit as any other component. Clicking on the LCC component with the right mouse button will bring up a special input dialog box called the Line/cable dialog. This window contains two sheets; one for the various model

.20. The user specifications and one for the data (geometry and materials) as shown in Fig.

the number of phases (and the number of cables) under the System type group. This choice will directly influence the grounding conditions in cable systems. The icon adapts setting of overhead line/single core cable/enclosing pipe and the number of phases.

version 5.6

Advanced Manual

[此处图片未下载成功]

.  5.19 http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3- Selecting a line or cable and connecting the LCC object to the rest of the circuit. When the required data are specified the user can close the dialog by clicking on OK. The user is also asked if ATP should be executed to produce the required punch-files. If the user answers No on the this question, ATP is not executed, and the user is prompted again later when creating the final ATP-file under ATP | run ATP or (ATP | Make File As...). You have to give a name to the component and if you click on the Run ATP button you will be asked to confirm the name. You do not have to specify path or extension as all data is stored in the Result Directory (same as the ATP file). If more than one component share the same name they are forced to be equal and the data is copied to the duplicates. When you click on OK you are warned about this as shown in Fig.  5.21. If you click on Yes the data of the current component will be copied to the otherhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 component with the same name. This cannot be undone directly, but you can undo the edit of the current component. If you then reopen it the old data will be copied to the other duplicates.

is very important to ensure a correct ATP installation and setup of the run ATP (F2) command in ATPDraw. This is done under Tools | Options / Preferences. It is recommended to use batch files. Three such files are distributed with ATPDraw (runATP_S.bat for the Salford version (DBOS required), runATP_W.bat and runATP_G.bat for the recommended Watcom or GNU versions of ATP). If the setup of the ATP command is incorrect, the line and cable models will not be produced.

punch-file output is transferred to a DATA BASE MODULE file by ATPDraw after the successful line parameter calculation, so that the node names are handled correctly. The lib-file required to build the final ATP-file is stored internally in memoryhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 and dumped to the Result Directory on demand. If something goes wrong in the generation of a electrical model an error message appear as shown in Fig.  5.22. Typical problems are missing or incorrect data. You can inspect the intermediate files in the Result Directory (c:in this case). File with extensions .dat (LINE/CABLE CONSTANTS or CABLE PARAMETER file), and .pch (result that is transformed into a .lib file) and the same name as the line/cable component should be present.

version 5.6  153

Advanced Manual

[此处图片未下载成功]

.  5

[此处图片未下载成功]

.20 - Line/Cable dialog box: Model specification. View-

[此处图片未下载成功]

feature.

.  5.21 – Duplicate line&amp;cable components.

.  5.22 – Model generation messages.

data is stored internally in memory and the user can choose to export this data to anhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 external library (typically the /LCC folder) by clicking the Export button. This data file is on a binary format and have extension .alc. You can click the Import button to load external data from disk. The Line&amp;Cable component can also be copied between project as all other components. Clicking on the View button, displays the cross section of the line/cable as shown in Fig.  5.20. The phase numbers (with zero as ground) can be displayed in a red color via View|Numbering. For cables, the grounded conductors are drawn with a gray color, while the ungrounded conductors are black.

version 5.6

[此处图片未下载成功]

Advanced Manual

phase number is according to the rule of sequence: first comes the cable with the highest number of conductors and the lowest cable number. The thick horizontal line is the ground surface. Zooming and copying to the Windows clipboard is supported in http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3metafile formats. The Verify button of the LCC dialog box helps the user to get an overview of the performance of the model in the frequency domain. This feature is described separately in sub-section  5.4.

creating a Noda line/cable model the Armafit program is executed automatically to create the required lib-file. The Armafit command is specified under Tools | Options / Preferences. The batch file runAF.bat is distributed with ATPDraw.

supports all the various electrical models: Bergeron (KCLee and Clarke), PI-equivalents, JMarti, Noda, and Semlyen. It is straightforward to switch between different models. Under System type the user can select between Overhead Line and Single Core Cable or Enclosing Pipe.

the Line/Cable dialog the user can select between:  System type:

Line: LINE CONSTANTS

Core Cables:

PARAMETERS   or

Chttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ONSTANTS

Pipe:

PARAMETERS   or

CONSTANTS

Line/Cable Data dialog of Fig.  5.20 really consists of three pages: Model page, Line or Cable page and Node page. The parameter names used in the LCC dialog boxes are identical with that of in Chapter XXI - LINE CONSTANTS and Chapter XXIII - CABLE CONSTANTS parts of the ATP Rule Book [3]. The Standard data of the Model page is common for all line and cable types and has the following parameters:

:The ground resistivity in ohmm of the homogeneous earth

(Carson's theory).

. init: Frequency at which the line parameters will be

(Bergeron and PI) or the lower frequency point

(JMarti, Noda and Semlyen) of parameter fitting.

:Length of overhead line in [m]/[km] or [miles].

length as a text in icon option. Model / Type: Bergeron: Constant parameter KCLee or Clahttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3rk PI: Nominal PI-equivalent (short lines)  JMarti: Frequency dependent model with constant transformation matrix Noda: Frequency dependent model (not supported in CABLE CONSTANTS)

[此处图片未下载成功]

Semlyen: Frequency dependent simple fitted model

.  5.23 - Standard data for all line/cable models.

.3.1 Model and Data page settings for Overhead Lines

overhead transmission lines the System type settings are as follows. High accuracy (FCAR=blank) is used in all cases. Specify the number of phases in the #Ph combo box.

: The overhead line is assumed to be transposed if the button is checked. Disabled for PI model type.

bundling: When checked this enables the automatic bundling feature of LINE CONSTANTS.

effect: If the button is checked skin effect is assumed (IX=4), if unchecked no skin effect correction. REACT option is set IX=0.

/English: Swihttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3tching between the Metric and English unit systems.

version 5.6  155

Advanced Manual

[此处图片未下载成功]

ground: Segmented ground wires. If

is unchecked then the ground wires are

to be continuously grounded.

trans. matrix:If checked the

matrix is assumed to be real.

eigenvectors of the transformation matrix

rotated closer to the real axis so that

imaginary part is assumed to become

. Recommended for transient

. Otherwise a full complex

matrix will be used.

for steady state calculations.

.  5.24 - System type options for

[此处图片未下载成功]

overhead lines.

.3.1.1 Model Type settings

: No additional settings are required.

: For nominal PI-equivalhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ent (short) lines the following optional settings exist under Data:

output: If selected the shunt capacitance, series impedance/admittance matrix of the unreduced system, and/or of the equivalent phase conductor system (after elimination of ground wires and the bundling of conductors), and/or of the symmetrical components will be calculated.

ω[C] print out: Selection between the capacitance matrix and the susceptance matrix (ωC).

.  5.25 - Optional settings for PI line models.

: The JMarti line model is fitted in a frequency range beginning from the standard data parameter Freq. init up to an upper frequency limit specified by the mandatory parameters number of Decades and the number of sample points per decade (Points/Dec). The model also requires a frequency (Freq. matrix) where the transformation matrix is calculated and a steady state frequency (Freq. SS) for calculation of http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3the steady state condition. Freq. matrix parameter should be selected according to the dominant frequency component of the transient study. The JMarti model needs in some cases modification of the default fitting data under the optional Model fitting data field, that can be made visible by unselecting the Use default fitting check box. For further details please read in the ATP Rule Book [3].

version 5.6

Advanced Manual

[此处图片未下载成功]

.  5.26 - Parameter settings for the JMarti line model.

: The Noda line model is fitted in a frequency range beginning from the standard data parameter Freq. init up to an upper frequency limit specified by the number of Decades with the resolution of Points/Dec. The model needs a frequency (Freq. veloc.), where the wave velocities

[此处图片未下载成功]

of the natural modes of propagation are calculated. A value highhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3er than the highest frequency of the frequency scan is usually appropriate. The Noda model needs in some cases modification of the default fitting data under the optional Model fitting data field, that can be made visible by unselecting the Use default fitting check box. For further details please read in the ATP Rule Book [3].

.27 - Parameter settings for the Noda line model. Fig.

: The Semlyen line model is frequency dependent simple fitted model. Fitting range begins at the standard data parameter Freq. init and runs up to an upper frequency limit specified by the parameter number of Decades. The model also requires a frequency (Freq. matrix) where the transformation matrix is calculated and a steady state frequency (Freq. SS) for calculation of

[此处图片未下载成功]

the steady state condition. Freq. matrix parameter should be selected according to the dominant frequency component of the tranhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3sient study. The Semlyen model needs in some cases modification of the default fitting data under the optional Model fitting data field, that can be made visible by unselecting the Use default fitting check box. For more details please read in the ATP Rule Book.

.  5.28 - Parameter settings for the Semlyen line model.

.3.1.2 Line Data page settings

data page contains input fields where the user can specify the geometrical or material data. For overhead lines, the user can specify the phase number, conductor diameters, bundling,

version 5.6  157

Advanced Manual

positions, as shown in Fig.  5.29. The number of conductors is user selectable. ATPDraw set the grounding automatically or gives warnings if the grounding conditions do not match the fixed number of phases. You can Delete last row

[此处图片未下载成功]

of the table using the gray buthttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3tons below or add a new one by clicking on the Add row command. Rows inside the table can also be deleted, but it must first be dragged down as last row. To drag a row click on its # identifier in the first column, hold the button down and drag the selected row to a new location or use the &#207; and &#208; arrows at right.

.29 - Line Data dialog box of a 3-phase line. 4 conductors/phase   2 ground wires. Fig.

.no.:phase number. 0=ground wire (eliminated by matrix reduction).

:   Inner radius of the conductor. Only available if Skin effect check box

selected on the Model page (see in

.  5.24). If unselected, the Rin column is removed and a React column

, where the user specifies the AC reactance of the line in

/unit length.

:  Outer radius (cm or inch) of the conductor.

: Conductor resistance (ohm/unit length) at DC (with Skin effhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ect checked)

AC resistance at Freq. init (if no Skin effect selected).

: Horizontal distance (m or foot) from the centre of bundle to a user

reference line.

:vertical bundle height at tower (m or foot).

:  vertical bundle height at mid-span (m or foot). The average conductor

calculated from the eq. h= 2/3*Vmid   1/3*Vtower is used in the calculations.

System type / Auto bundling is checked on the Model page (

.24): Fig.

: Distance between conductors in a bundle (cm or inch)

: Angular position of one of the conductors in a bundle, measured

-clockwise from the horizontal line.

:    Number of conductors in a bundle.

.3.2 Model and Data page settings for Single Core Cable systems

of CABLE CONSTANTS and CABLE PARAMETERS has been added to the LCC module of ATPDraw rhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ecently and the user can select between the two supporting programs by a single button switch. This enables a more flexible grounding scheme, support of Semlyen cable model instead of Noda and the cascade PI section. On the other hand in CABLE CONSTANTS enabled state ATPDraw does not support additional shunt capacitance and conductance input and Noda model selection. The CABLE CONSTANTS and CABLE PARAMETERS support in ATPDraw does not extend to the special overhead line part and the multi-layer ground model. For Class-A type cable

version 5.6

Advanced Manual

which consists of single-core (SC) coaxial cables without enclosing conducting pipe the System type settings are as follows. Specify the number of phases in the #Ph combo box.

in: Select if the cables are in the air, on

earth surface or in ground.

of cables: Specify the number of chttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ables in

system.

constants: Selects between Cable Constants

Cable Parameters option. If checked, the

conductance and capacitance option will

switched off and the Ground options on the Cable

page will be activated. The Semlyen model is

only with Cable Constants and the Noda

only with Cable Parameters.

.  5.30 - System type options for SC cables.

output: Check this button to enable printout of impedance and

matrix data (R, ωL and ωC).

: If checked the cables are assumed to be transposed.

G: Check this button to allow conductance between conductors.

supported for Cable Constants.

C: Check this button to allow additional capacitance between conductors.

supported for Cable Constants.

.3.2.1 Model Type settings for SC cables://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3, JMarti, Noda and Semlyen: The Model/Type and Data settings for these SC cable models are identical with that of the overhead transmission lines as described in section  5.3.1.1. Users are warned however, that the frequency dependent models may produce unrealistic results, due to neglecting the frequency dependency of the transformation matrix, which is acceptable in overhead line modeling but not for cables.

PI model:

the Cable Constants option is selected under the System

field, the PI model supports additional input

to produce cascade PI-equivalents. The

PI model is described in the ATP Rule Book [3].

Homogenous type can be used with all grounding

.

.31 - SC cable data for cascade PI output. Fig.

.3.2.2 Cable Data page settings for SC cables

data page contains input fields where the userhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 can specify the geometrical or material data for cables. The user can turn on sheath/armour by a single button and allowed to copy information between the cables. The cable number is selected in the top combo box with a maximum number specified in Number of cables in the Model page.

CABLE PARAMETERS (Cable Constants unselected) the Ground options are inactive and number of grounded conductors is calculated internally in ATPDraw based on the total number of conductors in the system and the number of initially selected phases. For CABLE C

[此处图片未下载成功]

ONSTANTS

[此处图片未下载成功]

(Cable Constants check box is On) the user must specify which conductor is grounded by checking the appropriate Ground buttons. A warning will appear if a mismatch between the number of phases and the number of ungrounded conductors is found. Grounded conductors are

version 5.6  159

Advancedhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 Manual

by gray color under

[此处图片未下载成功]

View. Selecting View|Numbering will show the phase number in red color (0=grounded). The cables will be sorted internally according to the sequence rule of ATP; the cable with most conductors comes first. To avoid confusion and mismatch between expected phase number and conductors the user should try to follow this rule also in the Cable/Data dialog. The Nodes page allows the user to rearrange the phase sequence.

.  5.32 - Cable Data dialog box for a 3-phase SC type cable system.

each of the conductors Core, Sheath and Armor the user can specify the following data: Rin: Inner radius of conductor [m].

: Outer radius of conductor [m].

: Resistivity of the conductor material.

: Relative permeability of the conductor material.

(ins): Relative permeability of the insulating material outside thttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3he

.

(ins):Relative permittivity of the insulating material outside the

.

radius: Total radius of the cable (outer insulator) [m].

/Armour On: Turn on optional Sheath and Armour conductors.

: Vertical and horizontal positions relative to ground surface and to

user selectable reference line for single core cables.

.3.3 Model and Data page settings for Enclosing Pipe type cables

selection specifies a cable system consisting of single-core (SC) coaxial cables, enclosed by a conducting pipe (referred as Class-B type in the ATP Rule Book [3]). The cable system might be located underground or in the air. The System type settings are identical with that of the Class-

type cables (see in sub-section  5.3.2). When the button Cable Constants is checked the shunt conductance and capacitance options are disabled andhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 a new check box Ground controls the grounding condition of the pipe. Transposition of the cables within the pipe is available via the

version 5.6

Advanced Manual

button. Cascade PI options can be specified similarly to SC cables (see Fig.  5.31). For cables with enclosing pipe, the following Pipe data are required:

.33 - System type and Pipe data settings for an Enclosing Pipe cable. Fig.

: Positive distance in meter between pipe center and ground surface.  Rin: Inner radius of the pipe in meter.

: Outer radius of the pipe in meter.

: Outer radius of outer insulation (total radius) in meter.

: Resistivity of the pipe conductor.

: Relative permeability of the pipe conductor.

(in): Rel. permittivity of the inner insulation (between cables and pipe). Eps(out): Rel. permittivity of the outer insulahttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3tion (around pipe).

and C: Additional shunt conductance and shunt capacitance between the pipe

the cables.

thickness: Infinit thick pipe. ISYST=0 and (uniform grounding).

cable Data page input fields for Enclosing Pipe type cable systems are identical with that of the SC cables (see sub-section  5.3.2.2). The only difference is the meaning of Position:  Position: Relative position to pipe center in polar coordinates

(distance and angle).

.3.4 Node page settings

Node page was introduced in ATPDraw version 5.3. Normally, the user does not need to specify anything on this page. It gives, however, access to the node names of the LCC component and offers the user to assign conductor numbers to the nodes. Conductor numbering can be desirable for cables since ATP requires a special sequence in this case; first comes the cores, then the sheaths then the armorhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3s. The cables with most conductors must be numbered internally in ATP as the first cable. To avoid too much confusion the user should also try to follow this rule. For overhead line the user specifies the conductor number directly in the data grid and there should be no need to alter this.

cable system consisting of 3 single core cables with sheaths and a fourth ground wire will as default receive an &quot;unexpected&quot; phase sequence. The core of the three cables will be numbered 1-2-3, then the ground wire will be numbered 4, and finally the three sheaths will be numbered 5-6-

. This does not fit well with the 3-phase layout used for this 7-phase system. The core of the cabes will all be a part of IN1/OUT1-ABC, but then the ground wire will become IN2A/OUT2A, the cable sheaths 1 and 2 will be IN2B/OUT2B and IN2C/OUT2C and the third cable sheats will be connected to the single phase nodes IN3/OUT3. To http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3let the ground wire be connected to the single phase node the conductor sequence 1-2-3-5-6-7-4 can be assign in the grid.

View module has a Number feature that displays the conductor numbers.

version 5.6  161

[此处图片未下载成功]

Advanced Manual

.4 Verification of the Line/Cable model performance

line or cable model can be verified in two different ways. Internally in the Line/Cable dialog there is a Verify module that supports both a frequency scaning option and a power frequency calculation. Externally under ATP|Line Check there is a module that enables the user to select several sequential line section (including transposition) and perform power frequency calculations of series impedance and shunt admittance. This modele is better for long lines.

.4.1 Internal Line/Cable Verify

Verify button of the LCC dialog box helps the http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3user to get an overview of the performance of the model in the frequency domain. This feature of ATPDraw enables the user to compare the line/cable model with an exact PI-equivalent as a function of frequency, or verify the power frequency benchmark data for zero/positive short circuit impedances, reactive open circuit line charging, and mutual zero sequence coupling. The Verify module supports two types of frequency tests:

) LINE MODEL FREQUENCY SCAN (LMFS) as documented in the ATP benchmark files DC51/52.dat. The LMFS feature of ATP compares the punched electrical model with the exact frequency dependent PI-equivalent as a function of a specified frequency range.

) POWER FREQUENCY CALCULATION (PFC) of zero and positive short circuit impedances and open circuit reactive line charging, and mutual zero sequence impedance for multi circuit lines.

the Verify dialog box as shown in Fig.  5.34 the user can choohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3se between a LINE MODEL FREQUENCY SCAN (LMFS) or a POWER FREQUENCY CALCULATION (PFC) case. Under Circuit specification, each phase conductor is listed for which the user should assign a circuit number. The phase order for overhead lines is from the lowest phase number and up to the one assigned under Data in the Line/Cable dialog box. For cables, the cable with the highest number of

[此处图片未下载成功]

conductors and the lowest cable number comes first (rule of sequence, ATP Rule Book - Chapter XXIII). A circuit number zero means that the conductor is grounded during the frequency test. For

[此处图片未下载成功]

the LMFS test the user must specify the frequency range (Min freq and Max Freq) along with the number of points per decade for the logarithmic space frequencies. For the PFC test, the input parameters are the power frequency and the voltage level (used to calculate the reactive line charging). Note! The LMFS fhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3eature of ATP does not work for Noda models.

.  5.34 - Frequency range specification for the LMFS run (left) and selecting

line voltage and system frequency for the PFC run (right).

version 5.6

Advanced Manual

will result in the generation of a LMFS data case called xVerify.dat and execution of ATP based on the settings of the default ATP command (Tools|Options/Preferences). The sources are specified in include files called xVerifyZ.dat, xVerifyP.dat, and xVerifyM.dat for the zero, positive and mutual sequence respectively. The individual circuits are tested simultaneously. The receiving ends are all grounded (over 0.1 mΩ) and all sending ends (if Circuit number &gt; 0) attached to AC current sources of 1 Amps. The phase angle of the applied current source for the ith conductor is -360 (i-1)/n where n is the total number of conductors belonhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ging to that circuit. Phase angle for the zero sequence tests are zero. The mutual coupling works only for 6-phase lines. For circuit one all phases are supplied with zero phase angle sources, while the phase conductors of the other circuit at the sending end are open. The View old case button will skip creation of the LMFS data case and trace the program directly to the procedure that reads the xVerify.lis file, which contains the input impedances of the electrical model compared to the exact PI-equivalent as function of frequency under various conditions. ATPDraw can read this file and interpretation of the results is displayed in the

[此处图片未下载成功]

LMFS results window as shown in Fig.  5.36 for the 4-phase JMarti line-model specified in Fig.  5.35.

.  5.35 - Specification of a 4-phase JMarti line model.

Fig.  5.36, the user can select the Mode and the Phase number of which the absolute vhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3alue of the input impedance is displayed to the left in a log-log plot. It is also possible to copy the curves to the windows clipboard in metafile format (Copy wmf). The absolute value of the input impedance of the model and the exact pi-equivalent can be compared for the following cases:

the other end of the line/cable is grounded. The zero-sequence impedance is thus equal to the voltage on the sending end of each phase.

*(i-1)/n is applied to all phases, where i is the current phase number in the specific circuit and n is the total number of phases in the circuit. (A 6-phase line/circuit will result in phase angles 0, -120, -240, 0, -120, -240 while a 4

version 5.6  163

Advanced Manual

circuit will result in 0, -90, -180, -270). The user specifies a circuit number for each phase under

[此处图片未下载成功]

Circuit specification of Verify Data dialog. Thehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 receiving end is grounded.

, while the other circuit is open. The receiving ends of all phases are grounded. Apparently this works only for 6-phase lines.

.36 - Verifying a JMarti line model 1 Hz to 1MHz. Model is OK for f &gt; 25 Hz. Fig.

for scaling of the reactive charging. Clicking on OK will result in the generation of a PFC data case called xVerifyF.dat and execution of ATP based on the settings of the ATP-Command (Tools | Options / Preferences). In this case, each circuit is tested individually (all other phases are left open while a specific circuit is tested). The library file describing the electrical model of the line/cable is included in a new ATP case an supplied by unity voltage or

[此处图片未下载成功]

current sources in order to calculate the steady state short circuit impedances and open circuit reactive line charging. The file xVerifyF.lis is read by ATPDhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3raw and the short circuit impedances together with the open circuit line charging is calculated in the zero-sequence and

.37 .  positive-sequence mode. The results of the calculations are displayed in Fig.

.  5.37 - Results of the PFC run.

version 5.6

Advanced Manual

the user clicks on Report the content in the string grids of Fig.  5.37 will be dumped to a user selectable text file. Further details about the operation of the Verify feature and PFC option can be found in the Appendix part of the Manual.

.4.2 External Line Check

, the user selects the line he wants to test and then clicks on ATP|Line Check as shown in Fig.

.38. Then the input/output selection dialog box shown in Fig.   5.39 appears.

LineCheck feature in ATPDraw supports up to 3 circuits. ATPDraw suggests the default quanthttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ities. The leftmost nodes in the circuit are suggested as the input nodes, while the rightmost nodes become the output. The circuit number follows the node order of the objects. For all standard ATPDraw components the upper nodes has the lowest circuit number. The user also has to specify the power frequency where the line/cable is tested. Finally, the user can check the Exact phasor equivalent button which will result in a slightly better results for long line sections.

.39 an ATP-file (/LCC/LineCheck.dat) is created and When the user clicks on OK in Fig.

executed. For a 3-phase configuration 4 sequential data cases are created (Z , Y , Z0, Y0) while for a 9-phase configuration 24 cases are created (Z11 , Y11 , Z110, Y110, Z12…, Z22…,

[此处图片未下载成功]

Z13…, Z23…, Z33…), since symmetry is assumed. Finally the entire LIS-file is scanned. The calculated values are then presented in result window as shownhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 in Fig.

[此处图片未下载成功]

5.40. The user can switch between polar and complex coordinates and create a text-file of the result. The mutual data are presented on a separate page. The unit of the admittances is given in Farads or Siemens (micro or nano) and the user can scale all values by a factor or by the length.

.38 – Select a line/cable sequence Fig.    Fig.  5.39 – Specify inputs and outputs

series impedances are obtained by applying 1 A currents on the terminals and the output ends are grounded (the other circuits are left open and unenegized). For mutual coupling, 1 A is applied at both circuits. On the other hand the shunt admittances are obtained by applying a voltage source of 1 V at one terminal leaving the output end open. For mutual coupling, 1V is applied at one circuit while a voltage of 1E-20 is applied at the other.

version 5.6  165

Advhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3anced Manual

attention must be paid to long lines and cables. This applies in particular to PI-equivalents. Usage of Exact phasor equivalent is recommended, but is no guarantee of success. No attempt is made in ATPDraw to obtain a better approximation since the line/cable system to be tested in general is unknown. The mutual coupling in the positive sequence system is in symmetrical cases very small and vulnerable to the approximations made.

.  5.40 –  Presentation of the results.

.5 Using MODELS simulation language

is a general-purpose description language supported by a set of simulation tools for the representation and study of time-variant systems. This chapter of the Manual is to a large extent an extract of the MODELS IN ATP -Language Manual, February 1996 [4] reference. Please consult this manual for more detailed information on the MODELS language.

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3rlanguage focuses on the description of the structure of a model and on the function of its elements. There is a clear distinction in MODELS between the description of a model, and the use of a model. Individual models can be developed separately, grouped in one or more libraries of models, and used in other models as independent building blocks in the construction of a system. The description of a model is intended to be self-documenting. A system can be described in MODELS as an arrangement of inter-related sub models, independent from one another in their internal description and in their simulation (e.g. individual models can have different simulation time step). Description of each model uses a free-format, keyword-driven syntax of local context, and does not require fixed formatting in its representation.

main description features of the MODELS language are the following:

The syntax ohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3f MODELS allows the representation of a system according to the system's functional structure, supporting the explicit description of composition, sequence, concurrence, selection, repetition, and replication;

version 5.6  166

[此处图片未下载成功]

Advanced Manual   The description of a model can also be used as the model's documentation; The interface of a model with the outside world is clearly specified; The components of a model can be given meaningful names representative of their function A system can be partitioned into individual sub models, each with a local name space; The models and functions used for describing the operation of a system can be constructed in programming languages other than the MODELS language.

main simulation features supported by the MODELS language are the following:

between the descriptihttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3on of a model and its use, allowing multiple independent replications of a model with individual simulation management (time step, dimensions, initial conditions, etc.);

Hierarchical combination of three initialization methods (default, use-dependent, and built-in), each contributing to the description of the pre-simulation history of a model by a direct representation of the pre-simulation value of its inputs and variables as functions of time;

Dynamically-controlled modification of the values of the inputs and variables of a model during the course of a simulation;

Dynamically-controlled modification of the structure of a model (both topological composition and algorithmic flow) during the course of a simulation.

supports only a simplified usage of MODELS. In general, ATPDraw takes care of the interface between MODELS and the electrical circuit (INPUT and OUTPUT of the MODEhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3LS section) and the execution of each model (USE). There can thus not be any expressions in the USE section. Creating a new Model in ATPDraw can follow two approaches:

. The automatic approach. Select the Models|Default model or open an existing .mod file and let ATPDraw take care the component definitions with icon and node connections. This is the best approach if the Model is supposed to change during the study.

. The manual approach. Select Models|Files mod/sup and choose a pre-existing support file (accompanioned with a compatible .mod file). This is the best choice if the Model will not change much (inputs/outputs fixed) during the study and the icon and node locations is crusial.

new MODELS object created in this chapter is part of the ATPDraw's example file Exa_14.adp. In this example the harmonic content of the line current on the 132 kV supply side of an industrial plan using a 24 pulsehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 AC/DC converter is calculated by MODELS.

.5.1 The automatic approach

a new Model to your circuit by selecting MODELS|Default model from the selection menu.

.41. Now, click A simple Model will appear with an empty dialog box shown as shown in Fig.

the Edit button and type in your model description, import a text from file with File|Import or paste in a text from the Windows clipboard. Anyway, this is the hard part of the process. In the listing below you will noticed that two indexed outputs are defined absF and angF as [1..26]. This will result in 26-phase nodes (which is the maximum allowed). The low index has to be 1 and the upper must be a number less or equal to 26. Indexed data is also allowed and these are then split in x[1], x[2] etc. The maximum number of data is 64 and the maximum umber of inputs plus outputs is 32.

on Done when the edit process is completed. ATPDhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3raw will then examine the Model description and identify the Input/Output/Data declarations. If the number of input or outputs have changed the icon is recreated. Inputs are positioned on the left side and Outputs on the right side

version 5.6  167

Advanced Manual

(from top to bottom). A message box then appears as shown in Fig.  5.42. Typically you should choose not to edit the file, but if you choose Yes the

[此处图片未下载成功]

Edit definitions dialog appears where you can relocate the nodes and change the icon. This might be a tricky process though. Anyway you can whenever click on Edit definitions an do this job later on. If yoy click on No, you will return to an

[此处图片未下载成功]

updated Component dialog box as shown in Fig.  5.43.

[此处图片未下载成功]

Fig.  5.41 –  Component dialog of the Default Model.

.  5.42 –  Identification of thhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3e Model text.

.  5.43 –  Component dialog of the FOURIER model.

version 5.6

Advanced Manual

the Models section in Fig.  5.43 you must also specify the Use As name for USE model AS model_name statement of MODELS. Record of local variable is also available in this section.

actual model file describing the calculation of harmonics is shown below:

FOURIER

X                    --input signal to be transformed

FREQ DFLT:50       --power frequency

DFLT:26           --number of harmonics to calculate

absF[1..26], angF[1..26],F0 --DFT signals

absF[1..26], angF[1..26],F0,reF[1..26], imF[1..26],i,NSAMPL,OMEGA

,F1,F2,F3,F4

DFLT:0

CELLS DFLT: 1/(FREQ*timestep) 1

:= 2*PIhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3*FREQ

:=1/(FREQ*timestep)

:=0

i:=1 to 26 DO

[i]:=0

[i]:=0

[i]:=0

[i]:=0

--window X?

:=delay(X,(NSAMPL 1)*timestep,1)

:=delay(X,NSAMPL*timestep,1)

:=delay(X,timestep,1)

:=X

:=F0 (f4 f3-f2-f1)/(2*NSAMPL)

i:=1 to n DO

:=1/(i*PI)*((f4-f2)*sin(i*OMEGA*T)-(f3-f1)*sin(i*OMEGA*(T-timestep))

(f4-f3-f2 f1)/(timestep*i*OMEGA)*

(cos(i*OMEGA*T)-cos(i*OMEGA*(T-timestep))))

[i]:=reF[i] D

:=1/(i*PI)*(-(f4-f2)*cos(i*OMEGA*T) (f3-f1)*cos(i*OMEGA*(T-timestep))

(f4-f3-f2 f1)/(timestep*i*OMEGA)*

(sin(i*OMEGA*T)-sin(i*OMEGA*(T-timestep))))

[i]:=imF[i] D

[i]:=sqrt(reF[i]**2 imF[i]**2)

imF[i]&lt;1E-10

[i]:=0

[i]:=atan2(imFhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3[i],reF[i])

.5.2 The manual approach

can create an external support file in two ways. Either by click on Edit definitions is the Component dialog box of your Model and then click on Save As (preferable to the /MOD directory). This will simply give you a copy of your Model component. The other way is to go via Library|New object|Model sup-file and create a support file from scratch. Both these options use the Edit definitions dialog. The end result is a support file that you load via MODELS|Files

version 5.6  169

Advanced Manual

(sup/mod).

manual approach requires that you have the mod file finished, or at least you need to know the number and name of all input, outputs and data. Enter the Library menu and select the New

|Model sup-file. This menu item will perform the Edit dhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3efinitions

. In the Standard data field, you specify the size of the model: number

nodes and number of data as shown in Fig.  5.44.

FOURIER.MOD text has four nodes (1 input   3 outputs) and two data,

(FREQ, n), so you must enter 4 and 2 in the Num. fields.

.  5.44 - Specify the size of the model.

you have specified the node and data values go to the tabbed notebook style part of the

.45. The Name of dialog box. Select the Data page where you specify the values shown in Fig.

data must be the same as those used in the DATA declaration part of the .mod file. The Default value appears initially in the models dialog. The default values are taken from the Use Model statements in

[此处图片未下载成功]

DC68.DAT (you can of course change these values individually for each use of the model). Min and Max restrict the legal input range. Nhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3o restriction is applied here to data values, so Min=Max.

.45 - Specify Data parameters. Fig.

is set to 0, which means that variable text string can not be assigned to the data value. Digits is the maximum number of digits allowed in the ATP input file. When high precision is checked, $Vintage, 1 is enabled and Digits is split in two values for high and low precision.

you have specified the data values click on the Nodes tab to enter to the node window as

.46. The Name identifies the node in the Node and Component dialog boxes. The shown in Fig.

you enter here must be the same as those used in the INPUT and OUTPUT declaration sections of the .mod file. The Position field is the node position on the icon border as shown at

right (Alt F1..F12 are short

), but other positions (-

..120) is possible. The Kind

specifies the input/ohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3utput

of the node. Number of

#Phases must be set to match the

size of the input/outputs.

.  5.46 - Specifying Node attributes.

[此处图片未下载成功]

Kind values for MODELS objects are:

: Output node.   3: Switch status input node.

version 5.6

[此处图片未下载成功]

170

: 2: 6: 7:

: Current input node.  4: Machine variable input node. Voltage input node.  5: TACS variable (tacs). Imaginary part of steady-state node voltage (imssv). Imaginary part of steady-state switch current (imssi). Output from other model. 9:   Global ATP variable.    Advanced Manual

Kind parameter of model object nodes can be changed

in the Node dialog box (input field Type), as shown in

.  5.47. This window appears when the user clicks on a

node with the right mouse buthttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ton.

.  5.47 - Model node dialog box.

! If a model output is used as input for another model, the model, which produces the output must be USEd before the use of the model that is supplied with this output. This can be done by specifying a lower Order number for the model with output signals and selecting the Sorting by Order option under ATP | Settings / Format.

objects also have an icon, which

the object on the screen and an

help, which describes the meaning of

. If no user supplied help text was

, the

[此处图片未下载成功]

Help Viewer displays the model

file (.mod) automatically. If you

need a help text, this feature can be

by opening the Help Editor

[此处图片未下载成功]

with the

at the right hand side of the dialog

.

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3Icon Editor appears similarly, by clicking

the  button. In this case Bitmap icon

is chosen. Here you can be creative and

a suitable icon for the new model object as

in Fig. 5.36. When you finished select the

menu item.

.48 - The icon of the new model objects. Fig.

Save or Save As buttons can be used to save the new support file to disk. Default location of Model support files is the folder. The .sup file does not need to have the same name as the model file, but it is recommended.

new model object has now been created is ready for use. You can reload and modify the support file of the model objects whenever you like.

MODELS |

[此处图片未下载成功]

Files (sup/mod)...

[此处图片未下载成功]

in the component selection menu performs an Open Model dialog box where you can http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3choose a model support file. If you select the file FOURIER.SUP the icon of the new model appears immediately in the circuit window and it can be connected with other object in normal way.

version 5.6  171

Advanced Manual

input and output interface for MODELS objects, the use of the model and interfacing it with the rest of the circuit are handled automatically by ATPDraw. The model description is written directly in the ATP input file. Blank lines are removed when inserting the .mod file. The general structure of the MODELS section in an .atp input file is shown below:

A i(HVBUSA)

A

B

...

Z

A

B

...

Z

------------------------------------------

FOURIER

...

of the model.

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3te copy of the

.MOD is pasted here.

...

------------------------------------------

FOURIER AS FOURIER

:= M0001A

:=        50.

:=        26.

A:=ABSF[1]

B:=ABSF[2]

…

Z:=ABSF[26]

A:=ANGF[1]

B:=ANGF[2]

…

Z:=ANGF[26]

:=F0

.5.3 Recording internal MODELS variables

supports the RECORD feature of MODELS to record any internal variable of a model object in the .pl4 output. The selection of internal variables is done by clicking the Record button in Fig.  5.43. This will bring of the Record dialog shown in Fig.  5.49. The available variables (VAR OUTPUT) is shown in the list to the left. Select the desired variable and click the &gt;&gt; button. The Record field to the right is a fhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ree format text field that allows you to easily edit the AS name. In the case of indexed variables you also need to specify the index as well (shown as reF[5]). Remove the variable from the Record list by the &lt;&lt; button. The Outputs from a Model

.49.    can alternatively be recoreded with the Model Probe as shown to the right in Fig.

version 5.6

Advanced Manual

[此处图片未下载成功]

[此处图片未下载成功]

Fig.  5.49 - Record of model variables. Right: Models Probe connected to Output node.

.6 BCTRAN support in ATPDraw

[此处图片未下载成功]

provides a user-friendly interface for the BCTRAN transformer matrix modeling, to represent single and three-phase, two and three winding transformers. After the user has entered the open circuit and short circuit factory test data, the ATPDraw calls ATP and executes a BCTRAN supporting rhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3outine run. Finally, ATPDraw includes the punch-file into the ATP-file. The windings can be Y, D or Auto coupled with support of all possible phase shifts. The nonlinear magnetization branch can optionally be added externally.

.  5.50 - The BCTRAN dialog box.

.  5.50 shows the BCTRAN dialog box, which appears when the user selects BCTRAN under Transformers of the component selection menu. Under Structure, the user specifies the number of phases, the number of windings, the type of core (not supported yet, except for single phase cores,

version 5.6  173

Advanced Manual

and three-phase shell type), and the test frequency. The dialog box format adapts the number of windings and phases. The user can also request the inverse L matrix as output by checking AR output. An Auto-add nonlinearities button appears when an external magnetizing branch is requested.

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3parUnder Ratings the line-voltage, rated power, and type of coupling must be specified. Supported winding Connections are: A (auto-transformer), Y (wye) and D (delta). The Phase shift menu adapts these settings with all types of phase shifts supported. If the connection is A or Y, the rated voltage is automatically divided by to get the winding voltage VRAT.

Factory tests, the user can choose either the Open circuit test or the Short circuit test.

the Open circuit tab the user can specify where the factory test has been performed and where to connect the excitation branch. In case of a three winding transformer one can choose between the HV, LV, and the TV winding. Normally the lowest voltage is preferred, but stability problems for delta-connected nonlinear inductances could require the lowest Y-connected winding to be used. Up to 6 points on the magnetizing curve can be specified. The excitationhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 voltage and current must be specified in % and the losses in kW. With reference to the ATP Rule Book, the values at 100 % voltage is used directly as IEXPOS=Curr [%] and LEXPOS=Loss

[kW]. One exception is if External Lm is chosen under Positive core magnetization. In this case only the resistive current is specified resulting in IEXPOS=Loss/(10   SPOS), where SPOS is the Power [MVA] value specified under Ratings of the winding where the test has been performed. If zero-sequence open circuit test data are also available, the user can similarly specify them to the right. The values for other voltages than 100 % can be used to define a nonlinear magnetizing inductance/resistance. This is set under Positive core magnetization:

) Specifying Linear internal will result in a linear core representation based on the 100 % voltage values.

) Specifying External Lm//Rm the magnetizing branch will be omitted in the BCTRAhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3N calculation and the program assumes that the user will add these components as external objects to the model.

) Specifying External Lm will result in calculation of a nonlinear magnetizing inductance first as an Irms-Urms characteristic, then automatically transformed to a current-fluxlinked characteristic (by means of an internal SATURA-like routine). The current in the magnetizing inductance is calculated as

[A]=(10 Curr[%] SPOS[MVA]/3)2 (Loss[kW]/3)2/Vref[kV]

Vref is actual rated voltage specified under Ratings, divided by 3 for Y- and Auto-

transformers.

user can choose to Auto-add nonlinearities under Structure and in this case the magnetizing inductance is automatically added to the final ATP-file as a Type-98 inductance. ATPDraw connects the inductances in Y or D dependent on the selected connection for actual winding for a 3-phase transformer. In this cahttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3se, the user has no control on the initial state of the inductor(s). If more control is needed (for instance to calculate the fluxlinked or set initial conditions) Auto-add nonlinearities should not be checked. The user is free to create separate nonlinear inductances, however. The Copy  button at the bottom of the dialog box allows the user to copy the calculated nonlinear characteristic to an external nonlinearity. What to copy is selected under View/Copy. To

version 5.6

Advanced Manual

the fluxlinked-current characteristic used in Type-93 and Type-98 inductances Lm-flux should be selected.

Short circuit data can be specified as shown in Fig.

.51. With reference to the ATP Rule Book; Imp [%] is

to ZPOS, Pow. [MVA] is equal to SPOS, and

[kW] is equal to P. These three values are

for all the windings. If zero-sequenchttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3e short

factory test data are also available, the user can

specify them to the right of the positive

values after selecting the Zero sequence data

check box.

.  5.51 - Short circuit factory test data.

Auto-transformer is selected for the primary and

winding (HV-LV) the impedances must be re-calculated according to Eq. 6.45, 6.46,

*6.50 of the EMTP Theory Book [5]. This task is performed by ATPDraw and the values ZH L,

**ZL T, and ZH T are written to the BCTRAN-file automatically.

VH *zHz=H L  L , V V

H2**zL T=zL T,zH T=zH LVHVLVH VL z zVH VL2H TVH VLL TVH VL

ZL-H, ZL-T, and ZH-T are the short-circuit impedances Imp. [%] referenced to a common Pow.[MVA] base.

the user clicks on OK the data structure is stored in a binary disk file with extension .bct and stored in thhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3e /BCT folder. This BCT-file is stored in the ATPDraw project file just like LCC-files for lines/cables. Then the user is offered to generate a BCTRAN-file and run ATP. This is really optional, since often a new BCTRAN-file will be required anyway during the final ATP-file generation. Trying to run ATP is a good practice however, since this will quickly warn the user about possible problems. The button Run ATP requests an ATP execution without leaving the dialog box. If the BCTRAN-file is correct, a punch-file will be created. This file is directly included in the final ATP-file and there is no conversion to a library file as for lines/cables. This means in practice that a new BCTRAN-file will be created and ATP executed automatically (when creating the final ATP-file) each times the transformer’s node names change.

is also an Import button available to import existing BCT-files. The user can also store the BChttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3T-file with a different name (Save As), which is useful when copying BCTRAN-objects. The View  and Copy  buttons are for the nonlinear characteristic. Copy  transfers the selected characteristic to the Windows clipboard in text format with 16 characters fixed columns (the first column is the current). View  displays the nonlinear characteristic in a standard View Nonlin window. The Help button at the lower right corner of the dialog box displays the help file associated with the BCTRAN object. This help text briefly describes the meaning of input data values.

. Excitation test data

under Factory test/Open circuit.

data required by BCTRAN are:

= Test frequency under Structure

= Curr for the 100% voltage value in

[此处图片未下载成功]

Open circuit, Positive sequence.        = Loss for the 100% voltage value divided by 10*SPOS when External Lm           requested.://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ar  = Power under Ratings for winding specified under Performed at.

version 5.6  175

LEXPOS = Loss for the 100% voltage value in Open circuit, Positive sequence. IEXZERO= Curr for the 100% voltage value in Open circuit, Zero sequence. SZERO  = Power under Ratings for winding specified under Performed at.

= Loss for the 100% voltage value in Open circuit, Zero sequence.  Advanced Manual

above input values can be derived from the factory test data as shown next:

= Iex*V*100/SPOS for single phase,

= Iex*√3*V*100/SPOS for 3-phase

Iex [kA] = excitation current,

[kV]   = excitation voltage.

[MVA]= power base

= 0 for single phase IEXZERO= 1/3*Iexh*√3*V*100/SZERO for 3-phase

Iexh [kA]= zero-sequence excitation current,

[MVA]= power base (normally equal to SPOS)

-connected windinghttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3s  (typical values):

-leg core type: IEXZERO= IEXPOS

-leg core type: IEXZERO= 4*IEXPOS

. Winding cards

under Ratings. The data required by BCTRAN are:

= L-L voltage [kV] for D-connection or single phase transformers          L-L voltage [kV] divided by √3 for A (Auto) and Y connections.

-phase only.

-   = The present node names of the transformer component in ATPDraw  BUS6      taking the connection and Phase shift [deg] into account.

the nodes will require a new BCTRAN execution performed           automatically upon ATP|Run ATP or Make File.

. Short circuit test data

under Factory test / Short circuit. The data required by BCTRAN are: Pij    = Loss (kW) under Short circuit, Positive sequence

= Imp (%) under Short circuit, Positive sequence

= Pow (MVA) under Short circuit,http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 Positive sequence

= Imp (%) under Short circuit, Zero sequence

= Pow (MVA) under Short circuit, Zero sequence

short circuit input data can be derived from the factory test reports, as shown next:

=  Usi/Isi*SPOS/Vri^2*100 for single phase,

=  Ush/√3*Ish)*SPOS/(Vri2)*100 for 3-phase

[kV] = short-circuit voltage at winding i

[kA] = nominal current at winding i

[MVA]= power base

[kV] = rated line voltage at winding i

= 0 for single phase

= Ush/Ish*SZERO/(Vri2)*300 for 3-phase

[MVA]= power base

-sequence tests must be performed with open Delta-windings.

BCTRAN component is found under Transformers BCTRAN in the component selection menu and it can be edited and connected to the main circuit as any other component.

.50 wilhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3l result in an icon at left with 3 three-phase terminals The data specified in Fig.  and one single-phase neutral point common to the primary and secondary autotransformer

. The label shows the transformer connection.

version 5.6

Advanced Manual

.7 Hybrid Transformer, XFMR

component called XFMR was added to version 4.2 of ATPDraw in June 2005. The model is then improved in several steps by extensive debugging. The XFMR component is an implementation and extension of the work performed by Prof. Bruce Mork at Michigan Tech and his co-workers Fransisco Gonzalez-Molina and Dmitry Ishchenko. This project called &quot;Parameter Estimation and Advanced Transformer Models for EMTP Simulations&quot; was sponsored by Bonneville Power Administration. A series of report documents this work and his here used as references MTU4, MTU6 and MTU7. The implementathttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ion in ATPDraw was also funded by BPA.

.7.1 Overview

principle of the modeling is to derive a topologically correct model with the core connected to an artificial winding on the core surface. Individual magnetizing branches are established for the yokes and legs dependent on their relative length and area (normally a value within limited range). A key feature is that magnetization is assumed to follow the Frolich equation which is fitted to Test Report data (using the Gradient Method optimization). This improves extreme saturation behavior since linear extrapolation above the Test Report data is avoided. The leakage inductance is modeled with an inverse inductance matrix (A-matrix), following the BCTRAN approach as documented in the Theory Book p. 6.21. Shunt capacitances and frequency dependent winding resistance is also considered.

transformer model consists of four parts (as shown in Fig.  http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db35.52) :

Inductance. Leakage reactance - &gt; A-matrix

[此处图片未下载成功]

Resistance. Winding resistance -&gt; R(f)

Capacitance. Shunt capacitance - C-matrix

Core. Individual magnetization and losses for legs and yokes.

.  5.52 - Duality model for a 3-phase, two-winding transformer from MTU4.

version 5.6   177

Advanced Manual

XFMR component support three sources of data:

Design parameters. Winding and core geometry and material properties.

Test report. Standard Test Report data like in BCTRAN. Capacitances and frequency dependent resistance added.

[此处图片未下载成功]

Typical values. Typical text book values based on transformer ratings. Be careful with this as both design and material properties have changed a lot the last decades.

.53. The overall node structure of the XFhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3MR component in the final ATP file is shown in Fig.

.  5.53 - Node structure in the ATP-file.

component can be connected as any other component in the circuit with the following exceptions.In both these cases switches should be used in order to maintain unique node names.   It is not legal to ground nodes directly

It is not  correct to connect several components to the same bus.

.7.2 XFMR dialog box

advance Hybrid Transformer component, XFMR, is found under Transformers in the selection menu. The model support 3-phase transformers with two or three windings coupled as Wye, Delta, or Auto. All possible phase shifts are supported. Triplex (single phase bank), 3- and 5-legged stacked cores and shell form cores are supported. The dialog box is shown in Fig.  5.54.

the input fields in the dialog box change dynamically with the user's selection of thehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 number of windings and type of core.

version 5.6

Advanced Manual

[此处图片未下载成功]

.54 – The XFMR component dialog box Fig.

the user presses OK the electrical model data (A and C matrices, R, and Core) are calculated and stored internally. The calculation of the core model might take up to one minute and a progress bar is shown (the user can press ESC to stop the calculation). The data can be exported (Export button) to an external library file (.xfm) for later import, but also copied between projects. Using the Import button it is possible to load a priviously created .xfm file.

radio buttons are available under Structure and Data based on that enables the user to set the source of data individually for each part of the model. Click the right mouse button to omit the part completely (inductance can not be omitted). Inductance, Resishttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3tance, Capacitance and Core. Under Type of core the user can select the core configuration. Triplex (single phase bank), 3- and 5- legged stacked, and shell form cores are supported. The type of core will influence the structure and calculation process of the core model. A 5-legged core will have a saturation characteristic also for the outer legs, while in the case of a 3-legged core this is replaced by a constant inductance representing the zero sequence behaviour.

Ratings &amp; Connections the user must specify the the line-to-line voltage in [kV], the rated power of the transformer [MVA] and the type of coupling and phase shift for each winding. These settings all refere to the Primary (P), Secondary (S), and Tertiary (T) notation. P is on the left side, S on the right side, and T on the top side of the transformer icon. There is no restrictions on the voltage levels here.

version 5http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3.6   179

Advanced Manual

phase-shift refered to the primary winding is specified in the drop down list. Only possible phase-shifts are listed. Other phase shift would require ZigZag couplings not supported here (use the Saturable Transformer component).

sequence of the winding on the core leg is set in the combo box Winding sequence. This is used establish the artificial winding where the core should be connected. If this sequence is unknown then remember that the inner winding usually has the lowest voltage. When the Ext. neutral connections button is checked, all neutral points become 3-phase nodes that the user has to connect manually.

design data the user must input the geometry and matrial data of the winding and core. For the core the user must choose a magnetic material. The list of available material data is very limited and only relatively new characterishttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3tisc are included. This means that a modeling of an old transformer using this approach would result in too low core losses. Uncertain aspects of the design data are the core losses and the zero-sequence data especially for 3-legged transformers.

test report data ATPDraw has an embedded BCTRAN-like routine for calculation of the A-matrix and winding resistance R. The core model is established by fitting the measured excitation currents and losses. The user can specify 9 points on an excitation characteristic. Some Insert and Delete buttons are available. ATPDraw will also sort the points by increasing voltage level. If the current and core loss do not increase with voltage an error message is displayed.

typical values some estimation is made based on textbook tables using the rated voltage and power. In the Typical data page there is a button Edit reactances, Edit resistances, Edit capacitances, or Edhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3it magnetization. When the user check this button, ATPDraw calculates the typical values based on the rated quantities and display the typical values. The values are then locked. To update the values based on a new setting of rated values the user must uncheck the button. There are basically two levels of sophistication available.

The default level requires no user input at all; the inductance, resistance, capacitance and core data is calculated based on typical values from tables. The user is allowed to specify a few data to improve the guessing; type of cooling for inductances (unknown=forced air), coupling factor for capacitances, and rated magnetic field intensity Bmax, loss density Pmax, and basic insulation level for core modeling. The user can examine the internally calculated data by checking an Edit button this also enables the second level. Once the button is checked the data are no longer updated when the rated http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3voltage or power is changed.

At the second level the user can directly specify the data.

buttons are available for viewing the winding and core design. If these buttons are checked a separate on-top window pops up with the information required to specify the input correctly. The Configuration image changes with the number and type of winding and the core type. The figures are fixed and are not scaled with the user specified dimensions.

on the Settings button on the core page  to set some parameters for the core model. This will bring up the Advanced core settings dialog. An important setting is the #points in saturation; the internal core model based on the Frolich equation (2 or 3 parameter option) is fitted to the test report with a fast Gradient optimization method by minimizing the different between the measured and calculated rms currents. This is then converted to a piecewishttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3e linear characteristic (type 93 or 98 inductors) assuming a certain number of points. Type 96 hysteretic inductors are also supported, and in this case half the core loss is assumed to be hysteresis losses and the core

version 5.6

Advanced Manual

is in general assumed to be proportional to the square of the flux density. Initialization is challenging for the type 96 inductors and ramping up the power supply with a controlled source might be necessary at lest for a 5-legged core. A very important parameter for inrush studies is the final slope inductance La. Design parameters are required here and L

[此处图片未下载成功]

a=μ0 N2 Aleg/lleg.

.  5.55 – The Advanced core settings dialog.

.8 Creating new circuit objects in ATPDraw

user specified objects (USP) are either customized standard objects or objects created for the use of $INCLUDhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3E and DATA BASE MODULARIZATION feature of ATP-EMTP. The Objects | User Specified | New sup-file menu enables the user to create a new support file for such a user specified object or customize data/node properties and the icon or the help text of an existing one. The number of nodes and data specified in the Edit Object dialog box for USP objects must be in line with the ARG and NUM

[此处图片未下载成功]

[此处图片未下载成功]

folder.

new circuit objects will be created in this section: a 6-pulse controlled thyristor-rectifier bridge that is used as building block for simulating a 12-pulse HVDC station (Exa_6.adp) in section  6.3 of the Application Manual, and a generator step-up transformer model with winding capacitances and hysteretic core magnetism included. The latter object is used in a transformer inrush current study (Exa_11.adp) in section  6.5.2 of the Application Manual.

.8.1 Creating a 6-http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3phase rectifier bridge

Data Base Module (DBM) file shown next describes a 6-pulse thyristor rectifier bridge (based on exercise 54 in [2]). The process of creating a DBM-file is certainly the most difficult part of adding new circuit objects to ATPDraw. The input file to the DBM supporting routine of ATP begins with a header declaration followed by the circuit description. The ATP Rule Book [3] chapter XIX-F explains in detail how to create such a file. The output punch-file of the DBM supporting routine can actually be considered as an external library file which is included to the ATP simulation at run time via a $INCLUDE call.

NEW DATA CASE --NOSORT--

BASE MODULE

version 5.6  181

$ERASE

,U____,POS___,NEG___,REFPOS,REFNEG,ANGLE_,Rsnub_,Csnub_

,ANGLE_,Rsnub_,Csnub_

,PULS1_,PULS2_,PULS3_,PULS4_,PULS5_,PULS6_,MID1__,MID2__,MIDhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db33__

,GATE1_,GATE2_,GATE3_,GATE4_,GATE5_,GATE6_,VAC___,RAMP1_,COMP1_

,DCMP1_,DLY60D

/TACS

DLY60D  .002777778

REFPOS

REFNEG

VAC___  =REFPOS-REFNEG

RAMP1_58 UNITY                                  120.00   0.0   1.0VAC___

COMP1_  =(RAMP1_-ANGLE_/180) .AND. UNITY

DCMP1_54 COMP1_                                       5.0E-3

PULS1_  = .NOT. DCMP1_ .AND. COMP1_

PULS2_54 PULS1_                                                   DLY60D

PULS3_54 PULS2_                                                   DLY60D

PULS4_54 PULS3_                                                   DLY60D

PULS5_54 PULS4_                                                   DLY60D

PULS6_54 PULS5_                                                   DLY60D

GATE1_  = PULS1_ .OR. PULS2_

GATE2_  = PULS2_ .OR. PULS3_

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3par98GATE3_  = PULS3_ .OR. PULS4_

GATE4_  = PULS4_ .OR. PULS5_

GATE5_  = PULS5_ .OR. PULS6_

GATE6_  = PULS6_ .OR. PULS1_

/BRANCH

$VINTAGE,0

___U____A            Rsnub_      Csnub_

___U____BPOS___U____A

___U____CPOS___U____A

____ANEG___POS___U____A

____BNEG___POS___U____A

____CNEG___POS___U____A

/SWITCH

U____APOS___                                                  GATE1_

U____BPOS___                                                  GATE3_

U____CPOS___                                                  GATE5_

NEG___U____A                                                  GATE4_

NEG___U____B                                                  GATE6_

NEG___U____C                                                  GATE2_

NEW DATA CASE

&lt;= &quot;C&quhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ot; in the 1st column is mandatory here!

$PUNCH

NEW DATA CASE

Manual

header section of the DBM-file starts with an ARG declaration after the special ATP request card DATA BASE MODULE. It's function is to specify the external variables (numerical   node names) and the sequence of arguments for the $INCLUDE procedure. The NUM card tells what arguments are numerical. DUM card lists the dummy or local variables, which are typically internal node names. ATP gives dummy nodes a unique name and thus let you use the same DBM-file several times in a data case avoiding node name conflicts. The rest of the DBM-file describes the rectifier bridge in a normal ATP data structure, except that sorting cards /TACS, /BRANCH, /SWITCH etc., are used in a special way. Sorting cards are required, but no BLANK TACS, BLANK BRANCH, etc. indicators are needed.

3-phase thyristor http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3bridge has a 3-phase AC input node and two single phase DC output nodes. The firing angle is taken as input data and the snubber parameters are also practical to consider as numerical input to the model. The model created here accepts external reference signals for the zero crossing detector (alternatively the DBM module file could have detected its own AC input), thus the new USP object will have 5 nodes and 3 data:

version 5.6

Advanced Manual

____ :

___:

___:

:

:

_:

_:

_:  The AC 3-phase node The positive DC node The negative DC node Positive reference node.  Negative reference node. The firing angle of the thyristors. The resistance in the snubber circuits. The capacitance in the snubber circuits.

the importance of the number of characters used for each parameter. The U____ pahttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3rameter has only 5 characters, because it is a 3-phase node and the extensions A, B and C are added inside the DBM-file. Underscore characters ‘_ ‘ has been used to force the variables to occupy the 6 characters space for node names and 6 columns ($VINTAGE, 0) for the snubber data. Running the DBM-file through ATP will produce a .pch punch file shown below:

3  4  5  6  6  6  7  7  8  8  8  9  9 10 10 10 11 11 11 12 12 12 13 13 13      14 14 14 15 15 15 16 16 16 17 17 17 18 18 18 19 19 19 20 20 20 21 21 21 24      24 24 24 25 25 25 25 26 26 26 26 27 27 27 27 28 28 28 28 29 29 29 29 31 31      31 32 32 32 33 33 33 34 34 34 35 35 35 36 36 36

4  5  4  5-16-16-17  6-17-18-18-19 -1-18-19 -1 -2-20 -2 -3-20 -3 -4-20      -4 -5-20 -5 -6-20 -1 -2-10 -2 -3-11 -3 -4-12 -4 -5-13 -5 -6-14 -1 -6-15  1       2  7  8  1  1  2  2  1  1  2  2  1  1  2  3  1  1  2  3  1  1  2  3  1  2     -10  1  2-12  1  2-14  1 http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 3-13  1  3-15  1  3-11

3  3  3 12 19  3 69  3 20 13  3 12  3  3 32 19 12  3 69 12  3 69 12  3 69      12  3 69 12  3 69 13 25  3 13 25  3 13 25  3 13 25  3 13 25  3 25 13  3  9       3 27 39  9 21  3 15  9 21  3 15  3 21 15  9  3 21 15  9  3 21 15  9  3  9      65  3  9 65  3  9 65  9  3 65  9  3 65  9  3 65

8  8  8 17 24  8 74  8 25 18  8 17  8  8 37 24 17  8 74 17  8 74 17  8 74      17  8 74 17  8 74 18 30  8 18 30  8 18 30  8 18 30  8 18 30  8 30 18  8 13       8 32 44 13 25  8 20 13 25  8 20  7 25 20 14  7 25 20 14  7 25 20 14  7 14      70  7 14 70  7 14 70 13  8 70 13  8 70 13  8 70

1  1  1  1  1  1  1  1  0  1  1  1  1  1  1  1  1  1  1  1  1  1  1  1  1       1  1  1  1  1  1  1  1  1  1  1  1  1  1  1  1  1  1  1  1  1  1  1  1  1       1  0  0  1  1  1  1  1  1  1  1  1  1  1  1  1  1  1  1  1  1  1  1  1  1       1  1  1  1  1  1  1  1  1  1  1  1  1  1  1  1

$ERASE

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3/TACS

DLY60D  .002777778

REFPOS

REFNEG

VAC___  =REFPOS-REFNEG

RAMP1_58 UNITY                                  120.00   0.0   1.0VAC___ 98COMP1_  =(RAMP1_-ANGLE_/180) .AND. UNITY

DCMP1_54 COMP1_                                       5.0E-3

PULS1_  = .NOT. DCMP1_ .AND. COMP1_

PULS2_54 PULS1_                                                   DLY60D 98PULS3_54 PULS2_                                                   DLY60D 98PULS4_54 PULS3_                                                   DLY60D 98PULS5_54 PULS4_                                                   DLY60D 98PULS6_54 PULS5_                                                   DLY60D 98GATE1_  = PULS1_ .OR. PULS2_

GATE2_  = PULS2_ .OR. PULS3_

GATE3_  = PULS3_ .OR. PULS4_

GATE4_  = PULS4_ .OR. PULS5_

GATE5_  = PULS5_ .OR. PULS6_

GATE6_  = PULS6_ .OR. PULS1_

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3par/BRANCH

$VINTAGE,0

___U____A            Rsnub_      Csnub_

___U____BPOS___U____A

___U____CPOS___U____A

____ANEG___POS___U____A

____BNEG___POS___U____A

____CNEG___POS___U____A

version 5.6  183

/SWITCH

U____APOS___                                                  GATE1_

U____BPOS___                                                  GATE3_

U____CPOS___                                                  GATE5_

NEG___U____A                                                  GATE4_

NEG___U____B                                                  GATE6_

NEG___U____C                                                  GATE2_

$EOF   User-supplied header cards follow.         31-May-02  15.46.06

,U____,POS___,NEG___,REFPOS,REFNEG,ANGLE_,Rsnub_,Csnub_

,ANGLE_,Rsnub_,Csnub_

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3arDUM,PULS1_,PULS2_,PULS3_,PULS4_,PULS5_,PULS6_,MID1__,MID2__,MID3__

,GATE1_,GATE2_,GATE3_,GATE4_,GATE5_,GATE6_,VAC___,RAMP1_,COMP1_

,DCMP1_,DLY60D

Manual

file is very similar to the DBM input file, but with a different header and with the original DBM-file header given at the bottom instead. This file is ready to $INCLUDE into an ATP input file by ATPDraw. The file must be given a name and extension .LIB and stored in the default directory. The name HVDC_6.LIB is used here as an example.

the punch-file from the DBM-file has been created, the next step is to create a support file for the new HVDC_6 object in the the Objects | User Specified menu. The process of creating a new object consists of two steps: create parameter support and create the icon.

select the New sup-file in the popup menu. A notebook-style dialog box shown in Fig.  5.http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db356 appears where you specify the number of data and nodes. The number of arguments on the NUM card(s) of the DBM-file tells you the Number of data, which is 3 in this example. The number of arguments on the ARG card(s) minus number of arguments on the NUM card(s) specifies the total Number of nodes, which is 5 in this example.

the Data tab, you specify the names of the data parameters, number of digits (it must be less or equal the space used in the DBM-file, which is 6 in this case) a default value, and the Min/Max values. The name of data need not be equal to the names used in the DBM punch-file, but the sequence of data must be the same as on the ARG and NUM card(s). After specifying data properties, click on the Node tab and set the node control parameters as shown in Fig.  5.56. The Name of nodes, the number of Phases (1/3) and the node position on the icon border (1-12) are to be given here. Codes for the ahttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3vailable node positions are shown in the icon at right. Kind is not used here. It must be left unity (default) for all nodes. The name of the nodes need not be identical with the names used in the DBM-file, but the node sequence must be the same as on the ARG card.

writes all three names of a 3-phase node in the $INCLUDE statement. In this example only the core name of the 3-phase node is expected on the argument list, because the phase identifiers A-B-C are added internally in the DBM-file. This option requires the Internal phase seq. checked box be selected in the component dialog box of the HVDC_6 object, as shown in Fig.  5.59. If it is selected, ATPDraw writes only the 5-character long core names in the $INCLUDE statement and let the extensions A, B and C be added inside the DBM library file.

that ATPDraw does not perform any diagnosis of the include file before sending the node names. Moreover, the http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3Internal phase seq. option may result in conflict with transposition objects. As a result, this option should in general not be used in transposed circuits. To avoid the conflict use three input names for 3-phase nodes in DATA BASE MODULE files.

version 5.6

Advanced Manual

[此处图片未下载成功]

.  5.56 - Properties of the new HVDC_6 object.

user specified objects might have a unique icon, which represents the object on the screen and an optional on-line help, which describes the meaning of parameters. These properties can be edited using the built in

[此处图片未下载成功]

Help and Icon Editors. Fig.  5.57 shows an example file that can be associated with the user specified 6-phase rectifier bridge.

.  5.57 - Help file of the HVDC_6 object.

.  5.58 shows the icon editor window. The red lines in the background indicate the poshttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3sible node positions on the icon border. Connecting lines to the external nodes of the object should be drawn from the symbol in the middle and out to the node positions specified in Fig.  5.56. The completed icon of the 6-pulse rectifier bridge is shown in Fig.  5.58.

version 5.6  185

Advanced Manual

[此处图片未下载成功]

.  5.58 - The icon associated with the new HVDC_6 object.

.  5.59 - Component dialog box of the new user specified HVDC_6 object.

, the just created support file must be saved to disk using the Save or Save As buttons. User

[此处图片未下载成功]

ATPDraw version 5.6

Advanced Manual

sup-files are normally located in the folder and their default extension is .sup. You can reload the support file of any user specified objects whenever you like, using the User Specified http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3| Edit sup-file option of the Objects menu.

User Specified | Files in the component selection menu provides access to the user specified objects. The component dialog box of the HVDC_6 object is very similar to that of the standard objects, as shown in Fig.  5.59. The name of the DBM-file which is referenced in the final ATP input file must be specified in the $Include field under User specified. The Send parameters check box is normally selected, if the USP object has at least one input node or data.

.8.2 Creating a user specified, nonlinear transformer model

routine BCTRAN can be used to derive a linear representation of a single or 3-phase multi-winding transformer, using excitation and short circuit test data. If the frequency range of interest does not exceed some kHz, the inter-winding capacitances and earth capacitance of the HV and LV windings can be simulated by addinghttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 lumped capacitances connected to the terminals of the transformer. Although BCTRAN produces only a linear representation of the transformer, connecting nonlinear inductances to the winding closest to the iron core as external elements, provides an easy way to take the saturation and/or hysteresis into account. It is noted that the BCTRAN object is now supported by ATPDraw in a user friendly way (see in section  5.6), but the procedure described here gives more flexibility in handling of the iron core nonlinearities and allows incorporation of winding capacitances in the USP object, if needed. Further advantage of the USP based modeling is that users do not need to run the BCTRAN supporting routine as many times as such kind of transformers present in the circuit before the execution of the time domain simulation. Creating such a user specified component however requires some experience in two ATP supporting routines: DATA BASE MODhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ULE and BCTRAN.

BCTRAN model requires easily available input data only, like the name-plate data of a generator step-up transformer shown below:

/15 kV  Voltage rating Vhigh/Vlow

connection:      Ynd11

rating:       155 MVA

losses:     74 kW

current:     0.3%  / 2.67 A

circuit losses:      461 kW

circuit reactance:    14 %

zero sequence excitation current and losses are approximately equal to the positive sequence measurements because the presence of delta connected secondary winding. Taking that the nonlinear magnetizing inductance is going to be added to the model as an external element, only the resistive component of the excitation current (0.05%) must entered in the BCTRAN input file shown next:

NEW DATA CASE

MODULE BCTRAN

$ERASE

50.     0.0http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db35       155.       74.     0.05       155.       74. 0 2 2   1     76.21           HVBUSASTRPNTHVBUSBSTRPNTHVBUSCSTRPNT

15.0           LVBUSALVBUSCLVBUSBLVBUSALVBUSCLVBUSB

2      461.      14.0      155.      14.0      155. 0 1

$PUNCH

NEW DATA CASE

version 5.6  187

BLANK

Manual

this file through ATP will produce an output punch-file that can be used as input for the Data Base Module (DBM) run. The process of creating a DBM-file is certainly the most difficult part of adding new circuit objects to ATPDraw. The input file to the DBM supporting routine of ATP begins with a header declaration followed by the circuit description. The ATP Rule Book [3] chapter XIX-F explains in detail how to create such a file. The output of the DBM supporting routine is a .lib file, that can actually be considhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ered as an external procedure which is included to the ATP simulation at run time via a $INCLUDE call.

.8.2.1 Creating a Data Base Module file for the BCTRAN object

DBM-file begins with a header declaration followed by the ATP request card DATA BASE MODULE and ends with a $PUNCH request. The ARG declaration together with the NUM card (if needed) specifies the external variables (numerical   node names) and the sequence of arguments for the $INCLUDE procedure. The rest of the file describes the BCTRAN model. Note that data sorting card /BRANCH is part of the file, but no BLANK BRANCH indicator is required.

ARG declaration of the DBM-file includes 7 node names in this example:

, HVBUSB, HVBUSC: The 3-phase node of the high voltage terminal

, LVBUSB, LVBUSC: The 3-phase node of the low voltage terminal

:    The 1-phase node of the HV neutral

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3

rest of the DBM-file is the transformer model description as produced by the BCTRAN supporting routine of ATP. The structure of the DBM input file is shown below:

NEW DATA CASE --NOSORT--

BASE MODULE

$ERASE

,HVBUSA,HVBUSB,HVBUSC,LVBUSA,LVBUSB,LVBUSC,STRPNT

&lt;&lt;&lt;&lt; The .PCH file generated by the &gt;&gt;&gt;&gt;

&lt;&lt;&lt;&lt; BCTRAN supporting routine must &gt;&gt;&gt;&gt;

&lt;&lt;&lt;&lt; be inserted here               &gt;&gt;&gt;&gt;

NEW DATA CASE

!!! This comment line here is mandatory !!!

$PUNCH, MYTRAFO.LIB

NEW DATA CASE

the DBM-file through ATP will produce a file mytrafo.lib  that must be stored in the folder of ATPDraw.

3  3  4  4  6  6 10 10 11 11 13 13 16 16 20 20 25 25

4  6  4  5  5  6  1  7  4  6  2  7 http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 4  5  3  7  5  6

3  9  9  3  9  3  3  9  3  9  3  9  9  3  3  9  9  3

8 14 14  8 14  8  8 14  8 14  8 14 14  8  8 14 14  8

1  1  1  1  1  1  1  1  1  1  1  1  1  1  1  1  1  1

$ERASE

&lt;      &gt;  Cards punched by support routine on  28-Jan-02  14.10.13  &lt;      &gt;

ACCESS MODULE BCTRAN

$ERASE

2       50.     0.05       155.       74.     0.05       155.       74. 0 2 2

1     76.21           HVBUSASTRPNTHVBUSBSTRPNTHVBUSCSTRPNT

2      15.0           LVBUSALVBUSCLVBUSBLVBUSALVBUSCLVBUSB

1 2      461.      14.0      155.      14.0      155. 0 1

BLANK

$VINTAGE, 1,

version 5.6

1LVBUSALVBUSC             9121.6157726436

LVBUSBLVBUSA             0.0

.6157726436

LVBUSCLVBUSB             0.0

.0

.6157726436

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 AR

HVBUSASTRPNT             19.966704093183 .16716783247242

LVBUSALVBUSC             -101.4441679294             0.0

.41471986794 .00647606659729

HVBUSBSTRPNT                         0.0             0.0

.0             0.0

.966704093183 .16716783247242

LVBUSBLVBUSA                         0.0             0.0

.0             0.0

.4441679294             0.0

.41471986794 .00647606659729

HVBUSCSTRPNT                         0.0             0.0

.0             0.0

.0             0.0

.0             0.0

.966704093183 .16716783247242

LVBUSCLVBUSB                         0.0             0.0

.0             0.0

.0             0.0

.0             0.0

.4441679294             0.0

.41471986794 .00647606659729

$VINTAGE, 0,

$UNITS, -1.,-1.

RL

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3arC ----------------- &lt;&lt; case separator &gt;&gt;&gt; -----------

$EOF   User-supplied header cards follow.         28-Jan-02  14.28.28

,HVBUSA,HVBUSB,HVBUSC,LVBUSA,LVBUSB,LVBUSC,STRPNT Advanced Manual

.8.2.2 Creating new support file and icon

step is to create a new user specified object via the Object | User Specified | New sup file menu of ATPDraw. The process of creating a new object consists of two steps: creating parameter support and creating an icon. Since no NUM card exists in the DBM header the number of data is

.60. 0, the number of nodes is 3 in this example as shown in Fig.

the Nodes tab, a Name can be assigned to each nodes. The number of phases and the node position on the icon border must also be specified here. The name of the nodes may differ from the name used in the .lib file, but the node sequence must be the same as specified on the http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ARG list. Each user specified component might have an icon and an optional on-line help, which describes the meaning of input parameters. The appearance of this icon is up to the users' creativity, but it is recommended to indicate three phase nodes with thick lines and to locate them according to the Pos (1..12) setting on the Nodes tab. Finally, the support file of the object must be saved to disk using the Save button (the default location is the /USP folder), to make the new USP object accessible via the User Specified | Files option of the component selection menu.

version 5.6  189

Advanced Manual

[此处图片未下载成功]

.  5.60 – Creating support file for the new BCTRAN object.

user specified components can be used in combination with the new grouping feature of ATPDraw as shown in Fig.  5.61. In this example, the linear part of the transformer model has been complethttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ed with winding capacitances as external components and three nonlinear Type-96 hysteretic inductors in delta connection at the 15 kV terminals, which represent the nonlinear magnetic core.

Compress feature of ATPDraw supports single icon replacement of these 7 objects. The inter-winding and winding-to-earth capacitances are input parameters to the group object. As shown below, the group object's icon can be customized, as well. An artistic icon may improve the readability of the circuit and help in understanding of the circuit file for others.

[此处图片未下载成功]

C_hgC_lg

[此处图片未下载成功]

.  5.61- Compressing the transformer model into a single object.

.9 Vector graphic editor

ATPDraw all icons of standard components are in vector graphic style. This enables better zooming and dynamic icon capabilities. A component can have either a bitmap or a vector icon, but nhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ot both. The building block of the vector graphic format is the Element (maximum 93). An Element has a Visible flag and can belong to a Layer, it is thus possible to easily turn on/off element as a respons to user settings. Further an element can either be a Shape or a Text. A shape can be of various standard Windows types (lines, rectangle, ellipses, poly-lines, polygons, arcs,

ATPDraw version 5.6

[此处图片未下载成功]

Advanced Manual

, and Bezier curves), while a Text is simpler. A Shape can consist of maximum 255 points which  is very beneficial for poly-lines, polygons and Bezier curves. The vector graphic editor has been developed from scratch utilizing an internal graphic format for fast drawings. The editor is shown in Fig.  5.62.

.62 – Vector graphic editor (400 % zoom). Fig.

element can be selected by clicking in the icon window or by specifying thhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3e Edit element spin edit field to the top right. The selected element is shown with its properties below. In the Properties grid the pen and brush colors and styles can be selected. The colors are codes with numbers 0-255. The numbers 240-255 are used for the standard colors and lower values to match the closest possible color when selecting the full color palette. The present color of the pen (frame) and brush (fill) is shown by the squares to the right. A shortcut to the standard colors (240-255) is to click the palette to the right (rfor pen, right for brush). This is the same is in the old Bitmap editor. In the Points grid the co-ordinates for the points are shown as well as rotation angle of rectangles and ellipses and rounding of rectangles.

.  5.62 also shows the components Nodes and the Frame. These are turned on/off via the checkboxes in the very top right corner. The Frame is the selection area ofhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 the icon; mouse clicks inside this area in the circuit will select or open the component. A too large Frame will result in overlapping conflicts with other icons. The Frame is not changeable with the mouse; the user has to specify the coordinates in the Frame string grid. The External point drawn as red is used for branch output of some of the components. The Nodes are drawn as gray dots with their node names oriented relative to the Frame. The Node positions and name can be specified in the Nodes string grid. The nodes can also be moved with the mouse selecting Tool|Move nodes. The nodes

version 5.6  191

[此处图片未下载成功]

Advanced Manual

to be on the grid so the nodes are only moved in steps. The grid is also drawn in Fig.  5.62 with the red lines indicating the centre. The grid can be turned on/off via Edit|Node grid.

the editing process is completed the user chttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3licks on Done.

.9.1 Properties

.63-Fig.

[此处图片未下载成功]

5

[此处图片未下载成功]

.64 shows the properties grids. Most of the properties have combo boxes and pup-Fig.

[此处图片未下载成功]

up dialogs attached as shown in Fig.  5.65 for selection of possible values.

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

5.63 – Properties grid. Left and centre: Shapes. Right: Texts. Fig.

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

Fig.  5.64 –  Shape properties alternatives.

.  5.65 – Text properties.

Shape points are given in the co-ordinate system -128..127. The Text point P is specified in the centre of the text. The Node co-ordinates have to be rounded off to the nearest 10.

ATPDraw version 5.6

Advanced Manual

are described by a code 0http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3..255, where 240-255 are the old standard ATPDraw colors used in the bitmap styles icons. These colors are found in the color grid to the right. For the color

[此处图片未下载成功]

properties there is a button available when pressed shows the basic color palette available in Delphi as shown in Fig.

[此处图片未下载成功]

5.66. The user can choose a color here which then is mapped to the closest color. The Custom color palette is the same as the standard ATPDraw colors. True 24 bit colors are not supported.

.  5.66 – The Basic color palette.

ATPDraw colors.

.9.2 Editing: Selecting, moving, resizing and clipboard

element is selected by clicking on it in the icon window. If the brush color is clear the user has to click on the visible border (does not apply to arcs and pies). Extensive code is added to support clicking on Bezier curves. If an element is already selected ihttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3t is given priority in the selection process. Click in open space to unselect the element. Several elements can be selected by holding down the shift key or by clicking in open space and draw an enclosing rectangle. A single element or a group of elements can be moved clicking and holding down the left mouse key. Elements can be resized by clicking on one of the eight black marking squares (the mouse cursor changes style in this case). Also a group of elements can be resized.

is possible to move all elements via the Tool|Move all menu, and this is the same as Edit|Select all   normal move.

position of elements can be fine tuned by holding down the shift key and use the arrow keys to move the selected group one pixel. The point position can also be typed directly into the points grid shown in Fig.  5.63.

order of elements can be changed via the Edit|Arrange menu where the fohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ur choices, send up/down, send to back/front are available. Elements or groups of elements can also be rotated 90 deg. and flipped left to right or top to bottom via the Edit|Flip&amp;Rotate menu.

is possible to copy selected elements to the windows clipboard. This can then be pasted into other icons (or duplicated). To place the graphical content in metafile format on the clipboard select Edit|Copy Graphics.

version 5.6  193

Advanced Manual

.9.3 Drawing new elements

new element is drawn be selecting the proper tool under Tools. The following tools are available:

selecting the tool click with the left mouse button to place points and with

right mouse button to place the final point. Line, rectangles, ellipses, arcs,

pies take a fixed number of points so the left/right clicking does not really

in thhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3is case. For polylines, polygons, and (Bezier) curves the number of

can range up to 255 maximum. When drawing Bezier curves only the

points follow the mouse clicks (point 1-4-7-10 etc.) while the

control points (2-3, 5-6 etc.) are calculated internally.

.  5.67 – Available modes and tools

shape points can be edited later by entering the Tool|Edit points mode. The shape points are then drawn as green squares which can be moved directly. It is also possible to add or delete points by clicking the right mouse button and choose from the pop-up menu. Bezier curves are handled in a special way as shown in Fig.

[此处图片未下载成功]

5.68. The curve points are drawn in a lime color while the control points are drawn in read with a line to their curve points. The curve points lies on the curve while the control points sets the curve derivative. (In thttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3he drawing tool in Windows office (Word and Power points) the left and right control points are forced to lie on the same tangent and this will force a smooth curve). When points are added to or deleted from Bezier curves this directly affects the curve point while the control points are automatically added/removed. The Bezier curve can be closed by selecting Brush style solid.

.  5.68 – Bezier curve drawn in Edit points mode. Green squares: curve points, red squares:

points.

.9.4 Layers and visible

element can belong to a specific layer as specified in the properties grid in Fig.  5

[此处图片未下载成功]

.63-Fig.

.64. The layers can be shown individually by changing the Show layer item in Fig.   5.62. Elements with Layer=0 are always drawn. The practical usage of this for user specified icons is limited to separation of elements in the drawing process. Fohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3r standard elements though, the Layer property is used to turn on/off elements dynamically. This is hard coded in the source code of

version 5.6

Advanced Manual

an affects RLC elements, transformers, time controlled and statistical switches, TACs devices, sources (current/voltage), LCC transmission lines (overhead line, single core cables, enclosing pipe   length), and universal machines. The Layer information is used to control the Visible property. Elements with Visible=false are not drawn in the circuit window, but they are drawn in the icon editor.

.9.5 Example of complex icons

the new vector graphics editor quite complex icons can be created. There is however still a limit of the size of the icon (41x41 bytes inherited from the old bitmap icon). This restricts the size to 93 elements. The occupied space of the current icon is shown in the stahttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3tus bar at the bottom shown in fig. 8 (13 % full in this case).

of the benefits with vector graphic icons is that it is possible to create larger and much more complex icons. Fig.  5.69 shows an example of a created windmill and transformer icons.

[此处图片未下载成功]

.  5.69 – Windmill and transformer icon with connecting universal machine and load in

size.

.10 Bitmap background

is possible to add a standard graphic background to any component in ATPDraw. This comes in addition to the icon itself. The graphic is included via the Edit definitions dialog shown in Fig.

.70. This dialog in shown from the Library menu item in the main menu for support files on disk,

from the Edit definition button in all component’s dialog box. A button for adding graphic background is shown as the rightmost speedbutton. This brings up the Graphic Backgrhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ound dialog

.71 where a standard bitmap or metafile can be loaded and scaled (Width), as shown in Fig.

relative to the icon centre and be forced to rotate with the icon (only bitmaps can be rotated). This option must be used with care, as graphic backgrounds significantly increase the project file size and the redraw time of circuits.

version 5.6  195

Advanced Manual

[此处图片未下载成功]

.  5.70 – Edit definitions dialog.

.71 – The graphic background dialog.  Fig.

.11 Optimization

module was added to ATPDraw version 5.6 as part of a co-operation with Schneider Electric. The user has to add a cost function object found in the selection menu under MODELS|Write Max/Min. This component will extract a single value from the simulation. In addition variables must be assigned to data in the circuit. These variables cahttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3n then be tuned to optimize the cost function. The optimization problem is defined as the minimization or maximization of the object

(x1,x2,…,xn) function OF in n dimensions with variables x.    min

variables x are can be selected by the user among the global variables.

ATPDraw version 5.6

[此处图片未下载成功]

Advanced Manual

.11.1 Optimization routines

different optimization routines are supported:

Gradient Method (GM) is the L-BFGS-B routine [16] (limited memory algorithm for bound constrained optimization) which is a quasi-Newton method with numerical calculation of the gradient. The gradient is calculated based on the two-point formula:

ff(x h) f(x h)≈                               x2h

the discretization point h is calculated as h=max(x,10 6) dx where dx is a  user selectable parameter (dhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3elta X).

n is the number of variables in the optimization problem the cost function thus has to be evaluated 2n 1 times for each solution point. This is calculated in a single ATP run utilizing PCVP. The iteration number is somewhat loosely defined in the Gradient Method. If the solution is poorer than the previous point the algorithm steps backwards along the gradient until an improved solution is found and only then the iteration number is incremented.

Genetic Algorithm (GA) is based on the RiverSoft AVG package (http://www.wendangwang.com), but modified to better handle the variable constraints. This optimization routine might need further improvement and development. The evolvement of the solution with GA is to more or less randomly select solutions (individuals) and mate these to obtain new solutions. The selection process can be Random, Roulette (using cumulative distribution), Tournamenhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3t (competition between a user selectable number of randomly selected rivals), Stochastic Tournament (combination of Roulette and Tournament), and Elitism (select only the user defined best percentage of the population). Tournament with 5-10 rivals is a reasonable starting point. The user has to select the size of the population (maximum 1000) and this is a critical parameter which depends on the problem and the number of variables. The user must also select the resolution with 8, 16 and 32 bits available. This part needs further development to allow integer values and arbitrary resolutions. Up to twenty cost function evaluations are performed in parallel using PCVP of ATP.

Simplex Annealing (SA) method is implemented from Numercal Recipies [17]. It is based on the Nelder-Mead simplex algorithm with an added random behaviour gradually reduced (simulated annealing). The algorithm also uses a possible larger set ofhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 points (called population) and can support mutation. With all control parameters set to zero the algorithm simply reduces to the classical Nelder-Mead simplex method. The method relies only on function evaluations and POCKET CALCULATOR of ATP is thus not used. Since a single case is run through ATP for each cost function evaluation, the method thus has potential to be extended to include other variables than those defined within the global variables ($Parameter).

.11.2 Cost function

general purpose Cost Function in MODELS called WRITEMAXMIN is introduced in ATPDraw version 5.6. The idea is to extract a single value from a simulation and write this to the lis-file and read it back when the simulation is finished. The single value is either the maximum or minimum of the signal xout from time Tlimit and out to the end time of the simulation. The Model has one input but this can be expanded. The Model also tahttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3kes in one DATA parameter AsFuncOf and if this is assigned to a variable WRITEMAXMIN writes output as function of this data parameter. If AsFuncOf is a number it is simply replaced by the simulation number.

version 5.6  197

Advanced Manual

supports multiple run though POCKET CALCULATOR. The selection of the component and its input dialog is shown in Fig. 5.72.

. 5.72 - Cost Function WRITEMAXMIN.

.11.3 Optimization dialog

Optimization dialog is found under ATP|Optimization. The user has to set up the data case which is not stored with the project. The variables x1..xn are chosen by clicking in the Variables column and selecting the available variable in the appearing combo box as shown to the left in Fig. 5.73. The user also has to specify the constraints Minimum and Maximum. The Object function must be selected among the avaihttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3lable WRITEMAXMIN components in the circuit. The user can then select to minimize or maximize and select a solution method (Genetic Algorithm, Gradient Method or Simplex Annealing). The Max iter field is the maximum number of iterations in the solution algorithm.

the Genetic Algorithm there are several, special selections. The size of the Population is a critical parameter. A low number will produce a degenerated result, while a too high number will waste computation time. The maximum allowed number is 1000. The required Resolution depends on the selected range (Max-Min). Since it anyhow is recommended to switch to the Gradient Method for fine tuning a 8-bit resolution (255 steps) is normally sufficient.  The Population count and Resolution can not be changed in the optimization process (Continue). The Crossover probability should be set to a high number (&lt;1) as the alternative is cloning. The Inversion and Mhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3utation probabilities should be set to low numbers but this depends on the complexity of the problem. High numbers will slow down the convergence considerably. The Rival count for Tournaments should be set to a medium value (2-10). A large number here will approach strong elitism and possible degenerated solutions. The Preserve fittest option will simply copy the fittest individual to the next generation (weak elitism). The preferred Selection method is one of the Tournament types. Elitism can be selected towards the end of the optimization process.

[此处图片未下载成功]

198  ATPDraw version 5.6

Advanced Manual

[此处图片未下载成功]

Fig. 5.73 - Optimization dialogs.

the Gradient Method the user has to specify a convergence limit eps_x and a dicretization step in per unit delta X. Intermediate trial steps do not count as part of the Max iter. The user also has to specify thehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 starting point in the Best fit column (if blank the average of Minimum and Maximum is assumed).

the Simplex Annealing method the user has to choose the Population (number of points evaluated for membership in the simplex) which is internally restricted to Population=max (Population, n 1). The Mutation probability parameter controls if the new points in the simplex is found at random or with the classical methods reflection, expansion or contradiction. The Max Climbs parameter controls how many steps in a negative direction that is accepted by the method. This should be a moderate value 0-3. The parameter beta (&lt;1) controls annealing schedule (temperature reduction), and the parameter ratio (controls the annealing schedule when a local minima is found.  For a rough surface with many local minima the beta and ration parameters needs to be increased. Ftol is the convergence criterion (the downside of this methohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3d). The

fmax fminiteration stops if Ftol&gt;. With all the other parameters set to zero the Simplex fmax fmin

method becomes equal to the Nelder-Mead simplex method.

user can press ESC to stop the optimization algorithms. When the user clicks on Exit the result of the optimization are written back to the VALUE field in ATP|Settings/Variables.

.11.4 Example: Resonance grounding (Exa_18.acp)

. 4 shows a resonance grounding circuit which could be extended to any complexity. The variable REACT is assigned to the neutral inductor and the unit is set to ohms as XOPT is 50. An intermediate variable CURR is used in Fig. 5.75 to vary the current linearly between 1 and 20 Amps with the special syntax @LIN 1 20 as this is the standard way of quantifying a resonant grounding.

[此处图片未下载成功]

ATPDraw version 5.6  199

Advanced Manual

[此处图http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3片未下载成功]

[此处图片未下载成功]

Fig. 5.74 - Resonant grounding circuit.  Fig. 5.75 - $Parameter selections @LIN

new, special Model component WRITEMAXMIN is used to write the maximum value of the neutral voltage as function of the neutral current CURR for all the 51 simulations specified in Fig.

.75. The input dialog of the Model component is shown in Fig. 5.76. It takes one input and writes the max or min value of this after an onset-time Tlimit to the lis-file. After the simulation the results are automatically read back from the lis file and a View button is available for charting the results as shown in Fig. 5.77.

.0kNEUT

.0

.0

.0

.0

.0

.08.012.016.020.0     Fig. 5.76 - Input dialog of the new WRITEMAXMIN  Fig. 5.77 Neutral voltage as function

.        of neutral current.

exact value of current that correspohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3nds to resonance can be found via the new Optimization module of ATPDraw. This is obtained under ATP|Optimization with an input dialog as shown in Fig. 5.73. Fig. 5.73 shows the optimum value found for the GA and GM solution methods. This case with a single variable involved, and a pure convex object function as shown in Fig. 5.77 is simple to solve.

[此处图片未下载成功]

ATPDraw version 5.6

.

[此处图片未下载成功]

Application Manual

chapter begins with some simple examples. You will not be shown how to create these circuits, but the circuits files Exa_*.adp are part of the ATPDraw distribution. To load these example circuits into the circuit window of ATPDraw, use the File | Open command (or Ctrl   O) and select the file name in the Open Project dialog. The resulting ATP-files will be given at the end of each description. Simulhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ation results and/or comparison with measurements are also presented in some cases. These figures have been obtained by processing the .pl4 output file or field test records with prost-processors PlotXY or ATP_Analyzer.

.1 Switching studies using JMarti LCC objects

LCC modeling features of ATPDraw are described in detail in section  5.3 of the Advanced Manual. Line modeling by LCC objects means that user specifies the geometrical arrangement and material constants, then ATPDraw executes ATP's Line/Cable Constants routine and converts the output punch-file to DBM library format. The resulting LIB-file will then be included in the final ATP-file via a $Include call. The JMarti option is one out of the five alternatives supported by ATPDraw's LCC object. Here two switching transient simulation examples are presented.

.1.1 JMarti model of a 750 kV line

JMarti line models introducehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3d in this section will be used in the subsequent single-line-to-ground fault study on a 750 kV shunt compensated transmission line with total length of 487 km. Transpositions separate this line into four sections. Each section of the line is represented by 3-phase un-transposed LCC object with JMarti option enabled. The ATPDraw project of the SLG study includes four such objects with name LIN750_x.ALC, where x runs from 1 to 4. The line

.1. configuration is shown in Fig.

.  6.1 - Tower configuration of the 750 kV line.

line parameters are given in Metric units. The Auto bundling option is enabled to simplify the data entry for this 4 conductor/phase in rectangular arrangement system. Tubular assumption has been applied as in the previous example with the following parameters:

[此处图片未下载成功]

ATPDraw version 5.6 203

Application Manual

resistance =http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 0.0585 Ω/km

diameter of the conductors = 3.105 cm.

radius of the tube = 0.55 cm

calculates the thickness/diameter value internally (T/D = 0.32).

wires are made from steel reinforced conductors, thus tubular assumption applies here, too:

resistance = 0.304 Ω/km

[此处图片未下载成功]

Outside diameter of the sky wire = 1.6 cm

radius of the tube = 0.3 cm

[此处图片未下载成功]

ATPDraw calculates the thickness/diameter value internally (T/D = 0.187).

resistivity of the soil equals to 20 Ωm. The conductor separation in the bundle is 60 cm.

the geometrical, material data and model options of the line, then executing Run ATP will produce a LIB-file in the /LCC folder. Since the length of each section is different, four LCC objects with different name are needed. The Save As button of the LCC dialog box can be used to save thehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 .ALC file with the new length, thus the line parameters need not be entered from scratch.

.  6.2- LCC Model and Data tab of the 1st section of the 750 kV line.

version 5.6

NEW DATA CASE

SETUP

$ERASE

IN___AOUT__AIN___BOUT__BIN___COUT__C

CONSTANTS

.323  0.0585 4             3.1   -17.5    27.9     13.     60.   45.       4   20.323  0.0585 4             3.1     0.0    27.9     13.     60.   45.       4   30.323  0.0585 4             3.1    17.5    27.9     13.     60.   45.       4   00.313   0.304 4             1.6   -13.2   41.05   26.15     0.0   0.0       0   00.313   0.304 4             1.6    13.2   41.05   26.15     0.0   0.0       0 BLANK CARD ENDING CONDUCTOR CARDS

.      1.E3                              84.6                 1

.       50.                     http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3         84.6                 1

.     0.005                              84.6         7 10    1

CARD ENDING FREQUENCY CARDS

CARD ENDING LINE CONSTANT

$PUNCH

CARD ENDING JMARTI SETUP

NEW DATA CASE

CARD

Manual

.1.2 Line to ground fault and fault tripping transients (Exa_7a.adp)

-phase to ground fault transients on a 750 kV interconnection are investigated in this study. The one-line diagram of the simulated network is shown in Fig.  6.3. At the sending end of the line shunt reactors are connected with neutral reactors to reduce the secondary arc current during the dead time of the single phase reclosing. The staged fault has been initiated at the receiving end of the line.

[此处图片未下载成功]

.  6.3 - One line diagram of the faulted line.

.4. Along the route three The layohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ut of the completed ATPDraw circuit is shown in Fig.

exist, so each LCC object represents a line section between two transpositions with length 84.6 km, 162.7 km, 155.9 km, 75.7 km, respectively.

[此处图片未下载成功]

6.4 - Line-to-ground fault study (Exa_7a.acp) Fig.

version 5.6 205

Application Manual

supply network model is rather simple: a Thevenin equivalent 50 Hz source and a parallel resistor representing the surge impedance of the lines erected from the 400 kV bus. An uncoupled series reactance simulates the short circuit inductance of the 400/750 kV transformer bank. The single-phase shunt reactors are represented by linear RLC components. Nononlinearities need not been considered here, because the predicted amplitude of the reactor voltage is far below the saturation level of the air gapped core. The impedance of the fault arc is considered as http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db32 ohm constant resistance.

ATPDraw generated ATP-file for this 750 kV example circuit is shown next:

NEW DATA CASE

--------------------------------------------------------

Generated by ATPDRAW  July, Monday 1, 2002

A Bonneville Power Administration program

Programmed by H. K. H&#248;idalen at SEfAS - NORWAY 1994-2002

--------------------------------------------------------

$DUMMY, XYZ000

dT  &gt;&lt; Tmax &gt;&lt; Xopt &gt;&lt; Copt &gt;

.E-5      .5

3       0       0       1       0       0       1       0

1         2         3         4         5         6         7         8

345678901234567890123456789012345678901234567890123456789012345678901234567890 /BRANCH

&lt; n 1&gt;&lt; n 2&gt;&lt;ref1&gt;&lt;ref2&gt;&lt; R  &gt;&lt; L  &gt;&lt; C  &gt;

_A                      http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 2.                                               0         XX0008                1.  300.                                         0   X0012CX0014C                5.  180.                                         0   X0012AX0014A                5.  180.                                         0   X0012BX0014B                5.  180.                                         0   X0012CX0014C              150.                                               0   X0012AX0014A              150.                                               0   X0012BX0014B              150.                                               0   X0022CX0021C                5.  300.                                         0   X0022AX0021A                5.  300.                                         0   X0022BX0021B                5.  300.                                         0   X0022CX0021C              150.                                               0   http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3X0022AX0021A              150.                                               0   X0022BX0021B              150.                                               0         RECVC                20.  6.E3                                         0         RECVA                20.  6.E3                                         0         RECVB                20.  6.E3                                         0   X0014CX0017C                2.  200.                                         0   X0014AX0017A                2.  200.                                         0   X0014BX0017B                2.  200.                                         0   SENDC XX0008               10.  3.E3                                         0   SENDA XX0008               10.  3.E3                                         0   SENDB XX0008               10.  3.E3                                         0 $INCLUDE, D:_2.LIB, TRAN1B, TRAN1C, http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3TRAN1A, TRAN2B $$

, TRAN2C, TRAN2A

$INCLUDE, D:_1.LIB, LN1C##, LN1A##, LN1B##, TRAN1C $$

, TRAN1A, TRAN1B

$INCLUDE, D:_3.LIB, TRAN2A, TRAN2B, TRAN2C, TRAN3A $$

, TRAN3B, TRAN3C

$INCLUDE, D:_4.LIB, TRAN3C, TRAN3A, TRAN3B, RECVC# $$

, RECVA#, RECVB#

/SWITCH

&lt; n 1&gt;&lt; n 2&gt;&lt; Tclose &gt;&lt;Top/Tde &gt;&lt;   Ie   &gt;&lt;Vf/CLOP &gt;&lt;  type  &gt;

SLG_A      .0285      .225       10.                                   0   X0017CSENDC        -1.      .075                                             0   X0017ASENDA        -1.        1.                                             0   X0017BSENDB        -1.        1.                                             0   SENDC LN1C                                          MEASURING                1   SENDA LN1A                                     http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3     MEASURING                1   SENDB LN1B                                          MEASURING                1   RECVC X0022C       -1.      .075                                             0   RECVA X0022A       -1.        1.                                             0   RECVB X0022B       -1.        1.                                             0 /SOURCE

&lt; n 1&gt;&lt;&gt;&lt; Ampl.  &gt;&lt; Freq.  &gt;&lt;Phase/T0&gt;&lt;   A1   &gt;&lt;   T1   &gt;&lt; TSTART &gt;&lt; TSTOP  &gt;

version 5.6

X0012C 0   612300.       50.                                     -1.        1. 14X0012A 0   612300.       50.     -120.                           -1.        1. 14X0012B 0   612300.       50.      120.                           -1.        1. 14X0021C 0   612300.       50.       10.                           -1.        1. 14X0021A 0   612300.       50.     -110.                   http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3        -1.        1. 14X0021B 0   612300.       50.      130.                           -1.        1. /INITIAL

/OUTPUT

SENDA SENDB RECVC RECVA RECVB

BRANCH

SWITCH

SOURCE

INITIAL

OUTPUT

PLOT

NEW DATA CASE

Manual

.  6.5 shows the results of the simulation. The upper curve is the phase-to-ground voltage at the receiving end of the line. Following the secondary arc extinction an oscillating trapped charge appears on the faulty phase, which is the characteristics of the shunt compensated lines. The blue (lower) curve shows the line current at the faulty phase during the fault and henceforth. Fig.  6.6 shows the recorded phase voltages and line currents obtained by a high-speed transient

[此处图片未下载成功]

upper curve: phase to ground voltage, lower curve: line current

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3TPDraw version 5.6 207

[此处图片未下载成功]

Application Manual

.  6.6 - SLG fault and fault clearing transients. Phase currents and voltages recorded at a staged fault test by a variable sampling frequency disturbance recorder.

.2 Lightning overvoltage study in a 400 kV substation (Exa_9.adp)

example demonstrates the use of ATPDraw in a lightning protection study. The one-line diagram of the investigated 400 kV substation is drawn in Fig.  6.7. The numbers written on the top of the bus sections specify the length in meters. The simulated incident is a single-phase back-flashover caused by a lightning strike to the tower structure 900 m away from the substation. Severe lightning parameters were chosen with 120 kA amplitude and 4/50 μs front/tail times. In the investigated cases, only Line1 and Line2 are connected with the transformer bus. The transformer is protected by convenhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3tional SiC arresters.

version 5.6

Application Manual

LINE3LINE4LINE5

.  6.7 - One-line diagram of the substation

[此处图片未下载成功]

. 6 .8 - Example circuit (Exa_9.acp)

ATPDraw circuit of the complete network (substation incoming line) is shown in Fig.  6.8. The Copy&amp;Paste or Grouping (Compress) feature of ATPDraw could be used effectively when creating such a model because the circuit has many identical blocks. I.e. the user needs to define the object parameters only once and copy them as many times as needed.

to the lightning strike, the line spans are represented by 4-phase JMarti LCC objects (phase conductors   sky wire). The surge propagation along the tower structure has been taken into

version 5.6 209

[此处图片未下载成功]

Application Manual

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ccount in this model by representing the vertical pylon sections as single-phase constant parameter transmission lines. The R-L branches below the tower model simulate the tower grounding impedance. The front of wave flashover characteristic of the line insulators plays a significant role in such a back-flashover study. It can be simulated quite easily using a MODELS object - like the Flash of this example-, which controls a TACS/MODELS controlled switch. The influence of the power frequency voltage on the back-flashover probability can't be neglected either at this voltage level. In this study case, it was considered by a Thevenin equivalent 3-phase source connected to the remote end of Line2.

ATP-file created by ATPDraw is shown below. Note! This case exceeds the storage cell limit of ATP if the program runs with DEFAULT=3.0 table size (default LISTSIZE.DAT setting). To run the simulation successfully the userhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 must increase this limit from 3.0 to 6.0.

NEW DATA CASE

--------------------------------------------------------

Generated by ATPDRAW  July, Thursday 4, 2002

A Bonneville Power Administration program

Programmed by H. K. H&#248;idalen at SEfAS - NORWAY 1994-2002

--------------------------------------------------------

$DUMMY, XYZ000

dT  &gt;&lt; Tmax &gt;&lt; Xopt &gt;&lt; Copt &gt;

.E-9  2.5E-5

3       0       0       1       0       0       1       0

/MODELS

v(TWR4A )

v(XX0016)

Flash

--------------------------------------

| Front of wave flashover characteristic    |

| of the HV insulator.                      |

| Input: Voltage accross the insulator.     |

| Output: Close command for http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3the TACS switch |

-----------------------------------endcomment

UP, UN

CLOSE

UINF DFLT:650e3, UO DFLT: 1650e3, TAU DFLT:8.e-7, UINIT DFLT:1E5

CLOSE, TT, U, FLASH

:=0

:=0

:=INF

:= ABS(UP-UN)

(U&gt;UINIT) THEN

:=TT timestep

:=(UINF   (UO-UINF)*(EXP(-TT/TAU)))

(U&gt;FLASH) THEN CLOSE:=1 ENDIF

FLASH AS FLASH

:= IX0001

:= IX0002

:=    1.4E6

:=     3.E6

:=    8.E-7

:=    3.5E5

:=CLOSE

version 5.6

.U AS U

.CLOSE AS CLOSE

1         2         3         4         5 http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3        6         7         8

345678901234567890123456789012345678901234567890123456789012345678901234567890 /BRANCH

&lt; n 1&gt;&lt; n 2&gt;&lt;ref1&gt;&lt;ref2&gt;&lt; R  &gt;&lt; L  &gt;&lt; C  &gt;

&lt; n 1&gt;&lt; n 2&gt;&lt;ref1&gt;&lt;ref2&gt;&lt; R  &gt;&lt; A  &gt;&lt; B  &gt;&lt;Leng&gt;&lt;&gt;&lt;&gt;0

XX0010XX0167               10.  200. 2.5E5  .008 1 0                         0 -1XX0012XX0010               10.  200. 2.5E5  .007 1 0                         0 -1XX0014XX0012               10.  200. 2.5E5  .018 1 0                         0 -1XX0016TOP                  10.  200. 2.5E5  .008 1 0                         0 -1      XX0019               20.  600. 2.9E5    .3 1 0                         0 -1XX0020XX0016               10.  200. 2.5E5  .007 1 0                         0     Application Manual           XX0014               40.                                               0    http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3     XX0014               13.  .005                                         0 -1XX0026XX0171               10.  200. 2.5E5  .008 1 0                         0 -1XX0028XX0020               10.  200. 2.5E5  .018 1 0                         0 -1X0032AX0033A               20.  650. 2.4E5    3. 1 0                         0 -2X0032BX0033B                2.  400. 2.9E5    3. 1 0                         0 -3X0032CX0033C                                                                 0         XX0028               40.                                               0 -1XX0036                     20.  600. 2.9E5    .3 1 0                         0         XX0028               13.  .005                                         0 -1XX0040XX0179               10.  200. 2.5E5  .008 1 0                         0 -1XX0042XX0040               10.  200. 2.5E5  .007 1 0                         0 -1XX0044XX0042               10.  200. 2.5E5  .018 1 0   http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3                      0         XX0044               40.                                               0         XX0044               13.  .005                                         0 -1XX0054XX0183               10.  200. 2.5E5  .008 1 0                         0 -1XX0056XX0026               10.  200. 2.5E5  .007 1 0                         0         LIGHT               400.                                               0 -1XX0060XX0054               10.  200. 2.5E5  .007 1 0                         0 -1XX0062XX0056               10.  200. 2.5E5  .018 1 0                         0 -1XX0064XX0060               10.  200. 2.5E5  .018 1 0                         0         XX0064               40.                                               0 -1XX0069XX0019               10.  200. 2.5E5  .008 1 0                         0         XX0064               13.  .005                                         0 -1X0073AX0074A               2http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db30.  400. 2.4E5  .008 1 0                         0 -2X0073BX0074B                2.  260. 2.9E5  .008 1 0                         0 -3X0073CX0074C                                                                 0 -1XX0075XX0036               10.  200. 2.5E5  .008 1 0                         0 -1X0078AX0211A               20.  400. 2.4E5  .012 1 0                         0 -2X0078BX0211B                2.  260. 2.9E5  .012 1 0                         0 -3X0078CX0211C                                                                 0 -1X0257AX0081A               50.  650. 2.4E5  .015 1 0                         0 -2X0257BX0081B               10.  360. 2.9E5  .015 1 0                         0 -3X0257CX0081C                                                                 0 -1X0082AX0083A               20.  400. 2.4E5  .068 1 0                         0 -2X0082BX0083B                2.  260. 2.9E5  .068 1 0                         0 -3Xhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db30082CX0083C                                                                 0 -1X0271ALINE2A               20.  650. 2.4E5  .024 1 0                         0 -2X0271BLINE2B                2.  360. 2.9E5  .024 1 0                         0 -3X0271CLINE2C                                                                 0 -1X0086AX0269A               20.  400. 2.4E5  .012 1 0                         0 -2X0086BX0269B                2.  260. 2.9E5  .012 1 0                         0 -3X0086CX0269C                                                                 0 -1X0088AX0293A               20.  650. 2.4E5  .015 1 0                         0 -2X0088BX0293B                2.  360. 2.9E5  .015 1 0                         0 -3X0088CX0293C                                                                 0 -1X0074AX0090A               20.  400. 2.4E5  .015 1 0                         0 -2X0074BX0090B                2.  260. 2.9E5  .015 1 0   http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3                      0 -3X0074CX0090C                                                                 0 -1X0074AX0271A               20.  400. 2.4E5  .085 1 0                         0 -2X0074BX0271B                2.  260. 2.9E5  .085 1 0                         0 -3X0074CX0271C                                                                 0   X0271A                               .0005                                   0   X0271B                               .0005                                   0   X0271C                               .0005                                   0 -1X0269AX0211A               20.  650. 2.4E5  .022 1 0                         0 -2X0269BX0211B                2.  360. 2.9E5  .022 1 0                         0 -3X0269CX0211C                                                                 0

version 5.6

X0211AX0257A               20.  650. 2.4E5  .022 1 0 http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3                        0 -2X0211BX0257B                2.  360. 2.9E5  .022 1 0                         0 -3X0211CX0257C                                                                 0 99SICC                     1.1E6    1.                                         1             100.           6.5E5

.E3           7.6E5

.E3            8.E5

.E3          8.34E5

.E3           8.5E5

.E4          9.35E5

.E4         1.082E6

.E4           1.2E6

X0104AX0105A               20.  400. 2.4E5  .068 1 0                         0 -2X0104BX0105B                2.  260. 2.9E5  .068 1 0                         0     Application Manual   -3X0104CX0105C                                                                 0 -1X0106AX0257A               20.  400. 2.4E5  .012 1 0                         0 -2X0106BX0257B                2.  260. 2.9E5  .012 1 0                         http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db30 -3X0106CX0257C                                                                 0 -1X0108ATR400A               20.  650. 2.4E5  .017 1 0                         0 -2X0108BTR400B                2.  360. 2.9E5  .017 1 0                         0 -3X0108CTR400C                                                                 0 -1X0105AX0110A               20.  400. 2.4E5  .025 1 0                         0 -2X0105BX0110B                2.  260. 2.9E5  .025 1 0                         0 -3X0105CX0110C                                                                 0 99SICB                     1.1E6    1.                                         1             100.           6.5E5

.E3           7.6E5

.E3            8.E5

.E3          8.34E5

.E3           8.5E5

.E4          9.35E5

.E4         1.082E6

.E4           1.2E6

PT1A  LINE1A               20.  650. 2.4E5  .http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3024 1 0                         0 -2PT1B  LINE1B                2.  360. 2.9E5  .024 1 0                         0 -3PT1C  LINE1C                                                                 0 -1X0118AX0293A               20.  400. 2.4E5  .012 1 0                         0 -2X0118BX0293B                2.  260. 2.9E5  .012 1 0                         0 -3X0118CX0293C                                                                 0 -1X0083AX0120A               20.  400. 2.4E5  .015 1 0                         0 -2X0083BX0120B                2.  260. 2.9E5  .015 1 0                         0 -3X0083CX0120C                                                                 0         TR400A                          .003                                   0         TR400B                          .003                                   0         TR400C                          .003                                   0 -1X0105AX0108A      http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3         20.  650. 2.4E5  .051 1 0                         0 -2X0105BX0108B                2.  360. 2.9E5  .051 1 0                         0 -3X0105CX0108C                                                                 0 -1SICA  X0108A               20.  400. 2.4E5  .007 1 0                         0 -2SICB  X0108B                2.  260. 2.9E5  .007 1 0                         0 -3SICC  X0108C                                                                 0 99SICA                     1.1E6    1.                                         1             100.           6.5E5

.E3           7.6E5

.E3            8.E5

.E3          8.34E5

.E3           8.5E5

.E4          9.35E5

.E4         1.082E6

.E4           1.2E6

AX0133A                1.   50.                                         0   X0132BX0133B                1.   50.                                 http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3        0   X0132CX0133C                1.   50.                                         0 -1XX0135XX0075               10.  200. 2.5E5  .007 1 0                         0 -1X0083APT1A                 20.  400. 2.4E5  .085 1 0                         0 -2X0083BPT1B                  2.  260. 2.9E5  .085 1 0                         0 -3X0083CPT1C                                                                   0   PT1A                                 .0005                                   0   PT1B                                 .0005                                   0   PT1C                                 .0005                                   0

version 5.6

X0293AX0269A               20.  650. 2.4E5  .022 1 0                         0 -2X0293BX0269B                2.  360. 2.9E5  .022 1 0                         0 -3X0293CX0269C                                                       http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3          0 -1XX0143XX0135               10.  200. 2.5E5  .018 1 0                         0         XX0062               40.                                               0         XX0062               13.  .005                                         0 -1XX0149XX0069               10.  200. 2.5E5  .007 1 0                         0 -1XX0151XX0149               10.  200. 2.5E5  .018 1 0                         0         XX0151               40.                                               0         XX0151               13.  .005                                         0         XX0143               40.                                               0         XX0143               13.  .005                                         0 -1LINE2AX0132A               20.  650. 2.4E5    3. 1 0                         0 -2LINE2BX0132B                2.  360. 2.9E5    3. 1 0                         0 -3LINE2CX0132C                            http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3                                     0 $INCLUDE, D:_9.LIB, X0033A, X0033B, X0033C, XX0019, X0166A $$

, X0166B, X0166C, XX0167

$INCLUDE, D:_9.LIB, X0166A, X0166B, X0166C, XX0167, X0170A $$

, X0170B, X0170C, XX0171

$INCLUDE, D:_9.LIB, X0170A, X0170B, X0170C, XX0171, TWR4A# $$

, TWR4B#, TWR4C#, TOP###

$INCLUDE, D:_9.LIB, TWR4A#, TWR4B#, TWR4C#, TOP###, X0178A $$

, X0178B, X0178C, XX0179

$INCLUDE, D:_9.LIB, X0178A, X0178B, X0178C, XX0179, X0182A $$

, X0182B, X0182C, XX0183

$INCLUDE, D:_9.LIB, X0182A, X0182B, X0182C, XX0183, LINE1A $$

, LINE1B, LINE1C, XX0036

/SWITCH

&lt; n 1&gt;&lt; n 2&gt;&lt; Tclose &gt;&lt;Top/Tde &gt;&lt;   Ie   &gt;&lt;Vf/CLOP &gt;&lt;  type  &gt;

TOP                                           MEASURING              http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3  1   X0090AX0086A       -1.     1.001                                             0   X0090BX0086B       -1.     1.001                                             0   X0090CX0086C       -1.     1.001                                             0   X0110AX0106A       -1.     1.001                                             0   X0110BX0106B       -1.     1.001                                             0   X0110CX0106C       -1.     1.001                                             0   X0120AX0118A       -1.     1.001                                             0   X0120BX0118B       -1.     1.001                                             0   X0120CX0118C       -1.     1.001                                             0 13XX0016TWR4A                                                         XX0048   0 /SOURCE

&lt; n 1&gt;&lt;&gt;&lt; Ampl.  &gt;&lt; Freq.  &gt;&lt;Phase/T0&gt;&lt;   A1   &gt;&lt;   T1   &gt;&lt; TSTART &ghttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3t;&lt; TSTOP  &gt; 15LIGHT -1     1.2E5     4.E-6     5.E-5        5.                            1. 14X0133A 0    -3.3E5       50.                                     -1.        1. 14X0133B 0    -3.3E5       50.     -120.                           -1.        1. 14X0133C 0    -3.3E5       50.      120.                           -1.        1. /INITIAL

/OUTPUT

ALINE1BLINE1CTWR4A TWR4B TWR4C TR400ATR400BTR400CPT1A  PT1B  PT1C

MODELS

BRANCH

SWITCH

SOURCE

INITIAL

OUTPUT

PLOT

NEW DATA CASE

Application Manual

results of the simulation are drawn in Fig. 6 .9. The blue line is the voltage stress appearing at the transformer terminal, the red line shows the incoming surge measured at the voltage transformer of Line1 (node PT1 of the circuit). The discharge current of the gapped arresthttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3er is drawn at the bottom if the figure. As it can be seen, the instantaneous value of the power frequency voltage was set opposite to the polarity of the lightning surge in the simulation.

version 5.6 213

Application Manual

: voltage stress at the transformer terminal. Green: arrester discharge current.

.3 Modeling Rectifiers, zigzag transformers and analysis of Harmonics (Exa_14.adp) In section  5.8.1 of the Advanced Manual, it is shown how to create a 6-pulse controlled thyristor-rectifier bridge and make it available in ATPDraw as a user specified single object. In this part of the manual a diode rectifier will be used instead and the focus shifted to harmonics in the supplying line currents. The case is an industrial plant consiting of AC/DC converters and consuming 55 MW for aluminium production. The plant is supplied by a 132 kV high voltage AC system and there arehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 concerns about the harmonics in the current on the high voltage side. This example shows how to model an equivalent 24 pulse diode rectifier and calculate the harmonics in currents in Models. The harmonics could alternatively have been calculated as a part of a post-processing.  Fig.  6.10 shows the example circuit.

[此处图片未下载成功]

.  6.10 – Example circuit (Exa_14.acp).

[此处图片未下载成功]

ATPDraw version 5.6

[此处图片未下载成功]

Application Manual

diode bridge is modeled and compressed into a group as shown in Fig.  6.11. Note the need for small resistors (1 μΩ) to decouple the diodes and added snubber circuits. The R and C data for all six snubbers are added to the External parameter group, but will appear as only two parameters in the compressed object. A bitmap icon is created for diode bridge.

.  6.11 – Comprhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ess a 3-phase diode bridge.

.  6.12 – Component dialog of the compressed group ACDC.

key unit to produce the 24-pulse system are the two supplying transformers phase shifted 15 degrees and with a Y and Δ coupling on the secondary side. This is accomplished by using the Saturable Transformer component with a zigzag coupling on the primary winding. The input

.12. The Saturable Transformer requires direct dialog of the upper transformer is shown in Fig.

of electrical quantities so recalculation of Test Report data is required. The transformers had the following test report data:

version 5.6 215

[此处图片未下载成功]

Application Manual

:    ZN0d11y

power:    24.8 MVA

primary voltage: 10.735 kV

secondary voltage: 693 V

tertiary voltage:  693 V

frequency:   50http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 Hz

circuit current:  0.0056 pu

circuit impedance 1-2: 0.0084   j0.1015 pu

circuit impedance 1-3: 0.0084   j0.1015 pu

circuit impedance 2-3: 0.0210   j0.1887 pu

shift Z (ref. 3):  &#177;7.5 deg.

[此处图片未下载成功]

This will result in the standard per unit equivalent circuit for the short circuit impedances

[此处图片未下载成功]

[此处图片未下载成功]

Fig.  6.13 – Per unit equivalent circuit of the 3-winding transformer.

the negative resistance in the primary winding. This could result in a stability problem in the simulations, but fortunately this didn’t seem to be the case in this example. The input dialog of the Saturable transformer with the electrical parameters is shown in Fig.  6.14.

.14 – Component dialog of the Saturable Transformer component. Fig.

version 5.http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db36

[此处图片未下载成功]

Application Manual

total winding voltage is UA=10.735/= 6.2 kV

short circuit impedance is

=( 0.0021 j0.00715) (10.735kV)/ 24.8 MVA = 0.00976 j0.0332[Ω] 2

(7.5  )The zigzag winding 1 is further split in Z and Y parts with n==0.165.  sin(60 7.5  )

voltages across each winding part and the individual leakage impedances are automatically calculated by ATPDraw as:

z=U1y10.735/kV=5.68kV       cos(7.5) 0.165 cos(60 7.5)=5.68kV 0.165=0.934kV     1[Ω] = -8.4 [mΩ]1 0.165 0.165R1y= 0.00976 [Ω] = -1.4 [mΩ]1 0.1650.03321L1z= [H] = 0.103 [mH]2π 501 0.165 0.03320.1652

y=

[此处图片未下载成功]

[H] = 2.79 [μH]2π 501 0.165R1z= 0.00976

the HV winding 1 is chosen as the primary winding, the magnetizing branch will be added to the first winding part (Z) of the zigzag winding. This is probably not a http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3good choice, and alternatively the magnetizing branch should be added to the low-voltage Y-coupled winding. This could be done externally or by choosing winding 3 as the primary.

measured inductance is

/2 Lm=pu=0.328 pu = 0.328 (10.735kV)/ 24.8 MVA=1.52 [H] 2π 50 0.0056

the inductance that should be added to winding 1Z in ATP:

Lmz==1.28 [H] 1 n n

is of no importance in this example and a single point is set on the characteristic page (i, λ)=(1, 1.28).

a measurement of the zero sequence impedance is missing a reasonable assumption for this particular transformer is to set it to 2/3 of the positive sequence magnetizing current. Further, the zero sequence inductance added in ATP is one half of the real value. This gives

U5.685.68R0=≈2 =

[此处图片未下载成功]

=25.2[Ω]  ATPATP1.283 L0z2 Lmz

Delta- winding:

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3The total winding voltage is UA2=0.693 kV

short circuit impedance is

=(0.0105 j0.0944) 0.693kV)2/ 24.8 MVA =0.61 j5.48[mΩ] R2=0.61 [mΩ] and L2=17.5 [μH] ATPDraw version 5.6 217

[此处图片未下载成功]

Application Manual

Wye- winding:

total winding voltage is UA3=0.693/=0.4 kV

short circuit impedance is

=(0.0105 j0.0944) 0.4kV)2/ 24.8 MVA =0.203 j1.83[mΩ]

=0.203 [mΩ] and L3=5.85 [μH]

ATP file format and connectivity of the transformer specified in  is:

THREE PHASE TX0001  25.2

[此处图片未下载成功]

[此处图片未下载成功]

1.            1.28             9999

Z1A   T0002C            -.0084.103215.6797

T0002A            -.0014.00279.93446

D2A   D2C               .00061 .0174  .693  4Y3A                      .0002.00585    .4

T1A       http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3              T1B

Z1B   T0002A  2      T0002B

D2B   D2A

Y3B

T1A                     T1C     1Z1C   T0002B

T0002C

D2C   D2B     4Y3C

example shown in Fig.  6.10 also includes a stepdown transformer and regulating transformer (regulation not modeled) that also are modeled as Saturable Transformer components. Alternatively the BCTRAN or Hybrid Transformer models could have been used as they have an internal conversion of test report data. These models do not support Zigzag transformers, however.

harmonics are calculated by an algorithm in MODELS. This is shown in chapter  5.5.1 in this manual. The automatic approach is assumed. A default model is used and the Models text is typed in under Edit. The output of absolute value and angle are declared s 26-phase (ABSF and ANGF) while the input X is single phase. The user can selec the type of inphttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ut (switch current in this case) by cliakin on the left input node of the model and select Input Current in the Node dialog box. The Model will output all harmonics 0..N (where N is a data parameter) as a function of time. The calcualtion is performed by integration of a sliding window of size 1/FREQ [sec]. The selection of variables to plot is made from a models probe connected to the ABSF node.

probe is set to 26-phases and the the

of special interest 1, 5, 7, 11, 13, 23, 25

checked under Monitor.

.  6.15 – Model probe dialog.

version 5.6

[此处图片未下载成功]

Application Manual

line current in phase A at the 132 kV side is selected as input. A connection is drawn from the left 3-phase side of the switch an to the single phase Model input node. In the Connection dialog that then pops up phase A is selectehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3d. The simulated phase A current is shown in Fig.  6.16 and the ththrdth5 7, 23 and 25 harmonics calculated in Models shown in Fig.  6.17.

[此处图片未下载成功]

[此处图片未下载成功]

Fig.  6.16 – Simulated line current phase A at the 132 kV side.

.  6.17 – The harmonics of the current in Fig.  6.16.

harmonics can also be calculated in for instance PlotXY as shjown in Fig.  6.18, but not as a

version 5.6 219

Application Manual

of time.

[此处图片未下载成功]

[此处图片未下载成功]

Fig.  6.18 – Harmonics calculated by FFT in PlotXY.

.  6.19 – DC voltages on the LV side.

.4 Modelling of electrical machines and controls

section illustrate a few examples of machine and control modeling with emphasis on how to interphase the various component involved.

.4.1 TACS controlled inducthttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ion machine (Exa_4.adp)

example shows the usage of the Universal Machine type 3, manual initialization along with usage of TACS. The use of info arrows, whose purpose is to visualize information flow between the TACS FORTRAN objects are also shown here. The info arrows can be selected under TACS | Draw relation in the component selection menu and they are handled graphically as normal connections. They do not affect the ATP-file, however. The example is taken from exercise 46 in

[2]. The ATPDraw constructed circuit is shown in Fig.  6.20/b:

ATPDraw version 5.6

[此处图片未下载成功]

Application Manual

.  6.20/a - Induction machine   TACS

[此处图片未下载成功]

.  6.20/b - ATPDraw scheme of the induction machine example (Exa_4.adp)

TACS part of the circuit controls three sources producing a pulse width modulated armature voltage. Thhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3e TACS objects FORTRAN1 is referenced in the Reference part of this Manual.

input window of the TACS object at the end of the TACS chain is shown in Fig.  6.21. This TACS object creates the armature voltage in phase A of the 3-phase node V.

version 5.6 221

[此处图片未下载成功]

Application Manual

.  6.21 - TACS Fortran input window

the TACS statement the user must type in the expression(s). Only single phase TACS Fortran objects are supported. The two (blue) info arrows into this TACS object serve as visualization of the SIGA (from node SIGA) and VD signals. The induction machine was given the data shown in

.22: Fig.

.  6.22 - Induction machine input window

.22 must be specified by the user as in the case for all object input The numerical values in Fig.

. The identity text in front of each attribute strhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ictly follows the input variable in the ATP

[此处图片未下载成功]

ATPDraw version 5.6

Application Manual

Book [3]. The ATP-file created by ATPDraw is shown below:

NEW DATA CASE

--------------------------------------------------------

Generated by ATPDRAW  July, Tuesday 30, 2002

A Bonneville Power Administration program

Programmed by H. K. H&#248;idalen at SEfAS - NORWAY 1994-2002

--------------------------------------------------------

Induction motor supplied by a

pulse width modulated source.

Test example 1.

dT  &gt;&lt; Tmax &gt;&lt; Xopt &gt;&lt; Copt &gt;

.E-5      .1

3       0       0       1       0       0       1       0

HYBRID

/TACS

FS      =1000

PULS            2.      .001     .0005                       .00025http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db32           98AMPL    =4.0*FS

SQPUL   =AMPL*(UNITY-PULS)

VDELTA  =SQPUL*DELTAT

VTRI  65         VDELTA                                                        14VCONTC         .95       60.      -90.                                         14VCONTB         .95       60.     -210.                                         14VCONTA         .95       60.       30.                                         98VB      =(2.0*SIGB-1.0)*VD/2.0

VC      =(2.0*SIGC-1.0)*VD/2.0

SIGC    =VCONTC .GT. VTRI

VA      =(2.0*SIGA-1.0)*VD/2.0

SIGB    =VCONTB .GT. VTRI

SIGA    =VCONTA .GT. VTRI

VD      =791.2

1         2         3         4         5         6         7         8

345678901234567890123456789012345678901234567890123456789012345678901234567890 /BRANCH

&lt; n 1&gt;&lt; n 2&gt;&lt;ref1&gt;&lt;ref2&gt;&lt; R  &gt;&lt; L  &gt;&lt; C  &ghttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3t;

&lt; n 1&gt;&lt; n 2&gt;&lt;ref1&gt;&lt;ref2&gt;&lt; R  &gt;&lt; A  &gt;&lt; B  &gt;&lt;Leng&gt;&lt;&gt;&lt;&gt;0

1.E6                                               2         BUSMG              13.33                                               1   BUSMG                                 5.E6                                   3   BUSMG BUSMS              1.E-6                                               1   BUSA  VA                  .001                                               1   BUSB  VB                  .001                                               1   BUSC  VC                  .001                                               1   BUSA  NEUT                1.E4                                               0   BUSB  NEUT                1.E4                                               0   BUSC  NEUT                1.E4                                               0 /SWITCH://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3r&lt; n 1&gt;&lt; n 2&gt;&lt; Tclose &gt;&lt;Top/Tde &gt;&lt;   Ie   &gt;&lt;Vf/CLOP &gt;&lt;  type  &gt;

/SOURCE

&lt; n 1&gt;&lt;&gt;&lt; Ampl.  &gt;&lt; Freq.  &gt;&lt;Phase/T0&gt;&lt;   A1   &gt;&lt;   T1   &gt;&lt; TSTART &gt;&lt; TSTOP  &gt; 14BUSMS -1-374.03889     1.E-5                                                   60VC     0                                                                       60VB     0                                                                       60VA     0

Next comes Universal Machines

UM

0

general UM specification

1 1331BUSMG        2                                     .1885           60.

Magnetization inductances

.840692          .0160

.785398163          .0160

Stator coils

NEUT        1       73.5587

.095         .0005BUSB  NEUT        1        80.545://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3par

.095         .0005BUSC  NEUT        1     -154.1034

Rotor coils

.075         .0004                  1      169.6725

.075         .0004                  1        19.285

UM

/INITIAL

version 5.6 223

BUSMG      182.840692

BUSMG                           182.840692

/OUTPUT

VB    VC

TACS

BRANCH

SWITCH

SOURCE

INITIAL

OUTPUT

PLOT

NEW DATA CASE

Application Manual

new Grouping feature of ATPDraw can be used in a creative

in this example, too. The pulse width modulated source and the mechanical load might be compressed into a single icon. The

version of this example circuit is also part of the

distribution with the name of Exa_4g.adp.

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3[此处图片未下载成功]

As shown left an artistic icon may improve the readability of the

and help in understanding the circuit for non-author users.

.23 - PWM source and mechanical load compressed into a single icon. Fig.

.4.2 Windsyn machine model

challenge with the above example is to obtain the electrical data for the induction machine. The program WindsynATPDraw is integrated with ATPDraw and enable manufacturers data to be used instead of the electrical data. The input dialog of the Windsyn component is shown in Fig.

.24. You can specify the data in this dialog, but you have to click on Run Windsyn to create the

. 6.24 – Windsyn input data. Induction machine, wound rotor.

[此处图片未下载成功]

Fig.

version 5.6

Application Manual

initialization of the machine was chosen as set under ATP|Settings/http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3Switch&amp;UM. The required manufacturers data for producing the same electrical model as in Exa_4.acp were not available. The efficiency and starting current parameters were adjusted to reach relatively close to the data given in Exa_4.acp. Note that the mechanical network is included inside the Windsyn component and that the stator neutral is assumed directly grounded. This resulted in comparable

.25. Installation of WindsynATPDraw.exe is stator current in steady state as shown in Fig.

to use this component. The link to the installed program is set under Tools|Options/Preferences-Windsyn. Note that Windsyn in the version used here resets the units of inertia to kWs/kVA each time. Besides this it was possible to simply click on Continue-Continue-Create files|Save run data-Exit in Windsyn. When you click on Exit in Windsyn the control goes back to ATPDraw (press ESC if Windsyn does not terminate properly) anhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3d the data files atpdraw.pch and atpdraw.wis are read into memory. The pch file is then run through ATP to produce the ‘Name’.lib used for $Include. This file (w1.lib in this case) is written to the same loacation as the final ATP file (Result Directory). You can inspect this ‘file’ by clicking the Edit lib-file button.

[此处图片未下载成功]

6.4.3 Machine control (Exa_17.acp)

control is typically of minor importance in an electromagnetic transients program as the time constants involved are much larger than the electrical time constants. Newertheless is some situation it might be of interest. The Fig.  6.26 shows a simple example where the Windsyn synchronous machine model is being controlled by a governor and an exciter. The loads of the machine doubles at 2 seconds and goes back to the initial 500 kW at 10 seconds. The Windsyn generator is auto-initialized and this involves two sources hidden inside http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3its lib-file. Initialization of the control units can thus be a challenge. To control the machine additional external sources must be adjusted. MODELS is here used for convenience, but TACS components will result in much master performance. The Windsyn component requires the special request card ‘UM TO TACS’ so be able to do calculation performance parameters in TACS. This is added as a User Specified|Additional component. The parameters used and the type of controls may certainly be discussed, but the point here is to illustrate the interface between machine and control.

version 5.6 225

Application Manual

speed control takes as input the actual speed of the machine (voltage at the TORQUE node of the machine) and gives out the torque to an additional current source connected to the same node.

voltage control takes as input the phase A voltage to ground and gives out thhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3e field voltage to an additional voltage source. The example shows how to get the field current and initial field voltage into the ST1A exciter model  A separate model is used to calculate the rms value.

[此处图片未下载成功]

[此处图片未下载成功]

.26 – Machine control of Winsyn, autoinitialize synchronous machine (Exa_17.acp). Fig.

.4.3.1 Hydro turbine governor

gate opening limits must be adjusted to take the steady-state condition into account and Gmin=-1 is set in this case to allow 1 pu increase and reduction in torque. Also the initial head h0 is set to zero here.

valve and

[此处图片未下载成功]

droop control

version 5.6

Application Manual

TUR_GOV

Tw,D, gFL, gNL, fp, Rp,Tr,Rt,Tg,Tp,Ks

,Rmaxopen,Gmax,Gmin,MW,Wrated, Wref

W

Torque

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 x1,x2,x3,x4,Pmech,At,x5,h,q,qNL,h0,s

,y2,g,h1,Wrefpu,Wpu,torque

dflt:0,x2 dflt:0,x3 dflt:0,x4 dflt:0, x5 dflt:0,

dflt:0,h dflt:0, y1 dflt:0,y2 dflt:0,g dflt:0

:=0  --Initial head. Set to zero in case of auto-initiation of generator.

:=recip(gFL-gNL)

:=(gNL)*sqrt(h0)

:=(Wref/Wrated)

:=(W/Wrated)*(30/pi)

--Governor hydraulic turbin

:= Wrefpu-Wpu-x5

(x2/x1):=(1|s0)/(1|s0 Tp|s1)

:=(Ks*x2) min:Rmaxclose max:Rmaxopen              --Gate opening/closing rate    cLaplace(x4/x3) dmin:Gmin dmax:Gmax:=(1|s0)/(1|s1)  --Gate position

(g/x4):=(1|s0)/(1|s0 Tg|s1)                   --Gate servo motor

(x5/x4):=(Rp|s0 ((Rp Rt)*Tr)|s1)/(1|s0 Tr|s1) --Permanent and transient droop    --Hydraulic turbin

(q/y1):=(1http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3|s0)/(Tw|s1)                        --q=Flow

:=(q*recip(g))**2                                    --h=Head

:=(q*q)*fp                                          --Penstock head loss

:=(h0-h-h1)                                         --Change in head

:=(q-qNL)*h                                         --Change in mechanical power   Pmech:=At*y2 (g*D*(Wrefpu-Wpu))

--Pmech:=g                                            --Uncomment to turn off turbine   Torque:=(Pmech*recip(W))*MW*1e6

.  6.27 – Hydro turbine governor

.4.3.2 Exciter model

Exciter is of type IEEE ST1A with inputs; terminal voltage VT, field current IFD, reference voltage Vref and stabilizer signal VS (all signals in pu). The Exciter IEEE DC1A is also implemented for comparison.

V KC IFDV

EFD

.  6.28 – IEEE ST1A exciter. Parameters used; TR =0.04http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3, TB =10, TC =1, KA=190, TA =0, TF =1,

=0, KLR =0, ILR=5, VRmax=7.8, VRmin=-6.7, KC=0.08.

exciter model ST1A requires the field current as input. This variable can be obtained directly from the Windsyn component as it is used there in the TACS section. The name of the TACS variable is ‘IE1Cn’, where n is the machine number (1 in this case). To get the machine number,

[此处图片未下载成功]

version 5.6 227

Application Manual

[此处图片未下载成功]

the Windsyn component and read the machine number field (cannot be set). Then click on the IFD node of the exciter model and specify the node name IE1C1 and input type TACS as shown in Fig.  6.29.

[此处图片未下载成功]

[此处图片未下载成功]

6.29 – How to get the field current into Models, and how to specify the Vs and VT nodes. Fig.

does not allow field voltage regulation bhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3efore 1 sec. The field connections are modeled as shown in Fig.  6.30 with 0.01 Ω separating resistors. The initial field voltage can be found by setting the the external field voltage to zero and then measure the current through it. This special trick is illustrated in the ST1A model, but not actually used in this example.

[此处图片未下载成功]

Fig.  6.30 – Internal field winding connections in Windsyn (n=Machine number)

EX_ST1A

Vref,VTpu,Tr,Tc,Tb,Ka,Ta,Vuel,Voel, Klr, Ilr, Kf, Tf, VRmax,VRmin, Kc, EFDref,IFDref

VT, Ifd, Vs, If0

Efd

x1,x2,x3,x4,x5,x6, Efd,Vc,IFDpu,Efd0

dflt:0,x2 dflt:0,x3 dflt:0,x4 dflt:0,x5 dflt:0, x6 dflt:0,

dflt:0, VT dflt:0

:=0

T&lt;2*timestep then  --Special trick to obtain the initial field voltage

:=-If0*0.01://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3r

:=-IFD/IFDref

--Vc:=VT/(1 Tr)

(Vc/VT):=(1/VTpu|s0)/(1|s0 Tr|s1)

(x6/x5):=(Kf|s1)/(1|s0 Tf|s1)

:=Vref-Vc-Vs-x6

(x2/x1):=(1|s0 Tc|s1)/(1|s0 Tb|s1)

(x3/x2):=(Ka|s0)/(1|s0 Ta|s1)

:=x3-(IFDpu-Ilr)*Klr

:=max(x4,Vuel)

:=min(x5,Voel)

:=x5 min:VT/VTpu*VRmin max:VT/VTpu*VRmax-Kc*IFDpu

:=Efd*EFDref 0*Efd0                    --Efd0 not used here

version 5.6

Application Manual

[此处图片未下载成功]

Fig.  6.31 – IEEE DC1A exciter. Parameters used; TB =0.06, TC =0.173, KA=400, TA =0.89, TE

=1.15, KE =1, A =0.014, B = 1.55, KF =0.058, TF =0.62.

EX_DC1A

Vref,Tc,Tb,Ka,Ta,VRMAX,VRMIN,Kf,Tf,Te,Ke,Vuel,A,B, Efdbase

Vc

Efd

x1,x2,x3,x4,x5,xhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db36, Vfe,Vf,Efd,Vcpu

dflt:0,x2 dflt:0,x3 dflt:0,x4 dflt:0,x5 dflt:0, x6 dflt:0, Vfe dflt:0 Vf dflt:0

:=0

:=(Vc*sqrt(3)/(Vref*1000))  --Phase voltage measured so scale to line voltage   x1:=(1-Vcpu-Vf)

(x2/x1):=(Tc|s1 1|s0)/(Tb|s1 1|s0)

:=max(x2,Vuel)

(x4/x3) dmin:VRMIN dmax:VRMAX:=(Ka|s0)/(Ta|s1 1|s0)

:=(x4-Vfe)

(x6/x5):=(1|s0)/(Te|s1)

:=x6*Ke A*exp(B*x6)

(Vf/Vfe):=(Kf|s1)/(Tf|s1 1|s0)

:=x6*Efdbase

.4.3.3 RMS value calculation

RMS value is calculated by a standard models provided by Laurant Dube. Since the speed of the generator changes the frequency is calculated by another model. The MODELS|Default model option was used and the text simply pasted into the Model component. Edithttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3|Flip was used to switch the input and outputs. As this model gives its output to another model it must be written first to the ATP file. This is managed by giving it a lower Order number than the receiving model and then choose ATP|Settings/Format – Sort by Order. In the receiving model the input node must be set to Input MODEL.

rms_meter

freq     -- base frequency

_ini dflt:-1 -- initial rms value

x        -- monitored signal

xrms     -- rms value of monitored signal

-- internal, x*x

-- internal, integral of x2

-- 1/freq

xrms

version 5.6 229

CELLS(ix2): 1/freq/timestep  1

:= recip(freq)

(ix2) := 0

(x2) := 0

xrms_ini &lt;0 THEN xrms:=0 ELSE xrms:=xrms_ini ENDIF

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3C

:= x*x

:= integral(x2)

t&gt;period THEN

:= sqrt((ix2 - delay(ix2, period))/period)

Application Manual

frequency is calculated by another model based on zero-crossing detection.

[此处图片未下载成功]

[此处图片未下载成功]

6Fig.

version 5.6

Application Manual

.5 Simulating transformer inrush current transients

magnetic coupling between the windings and the nonlinear characteristic of the magnetizing reactance are the most important factors in transformer energizing transient studies. The BCTRAN supporting routine of ATP can be used to derive the R L or (L-1 R) matrix representation of a single or 3-phase multi-winding transformer. ATPDraw now provides a similar interface to the BCTRAN supporting routine like the one provided for the LCC ohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3bjects. The BCTRAN input data are the excitation and short circuit factory test data, which can easily be obtained from the transformer manufacturers. Additionally, the user can select between several options for modeling the nonlinear magnetizing branch.

first example circuit of this section demonstrates the use of BCTRAN objects for transformer energization studies. In the second example, readers are familiarized with the application of user specified objects and the Grouping feature for transformer modeling.

.5.1 Energization of a 400/132/18 kV auto-transformer (Exa_10.adp)

study case is the energization of a 3-phase, three-winding Yyd coupled transformer. The wye connected 132 kV windings and the delta coupled 18 kV windings are unloaded in this study. The schematic diagram of the simulated case is shown in Fig.  6.34, the corresponding ATPDraw circuit is depicted in Fig.  6.35.://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ar

/132/18 kV

[此处图片未下载成功]

6.34 - One-line scheme of the transformer and the 400 kV source.

[此处图片未下载成功]

Fig.

.35 - ATPDraw circuit (Exa_10.acp). Fig. 6

nameplate data of the transformer are as follows:

rating Vhigh/Vlow/Vtertiary:   Power rating:      Positive seq. excitation loss/current:  Positive seq. reactance: High to Low:     High to Tertiary:     Low to Tertiary: Short circuit loss:   High to Low:     High to Tertiary:     Low to Tertiary:  400/132/18 kV, Yyn0d11  250 MVA (75 MVA tertiary) 140 kW / 0.2 % 15 % (Sbase=250MVA) 15 % (Sbase=250MVA) 12.5 % (Sbase=75MVA) 41.6667 % (Sbase=250MVA)   7.2 % (Sbase=75MVA) 24 % (Sbase=250MVA) 710 kW 188 kW 159 kW

the BCTRAN dialog box, you specify first the number of phases and the number of windings per phase under Structure (see Fig.  6.36). Under Ratings, the nominal line-to-line voltage,http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 power

version 5.6 231

Application Manual

, the type of coupling of windings and the phase shift must be entered. For auto-transformers, the nominal voltage of the windings (which is the required input for BCTRAN

[此处图片未下载成功]

) is calculated automatically by ATPDraw and the short-circuit impedances are also re-defined according to the Eq. 6.45, 6.46, 6.50 of the EMTP Theory Book [5]. The zero sequence excitation and short circuit parameters are approximately equal to the positive sequence values for an auto-transformer having tertiary delta winding, so the Zero sequence data available check boxes are unselected in this example. The External Lm option is chosen under Positive core magnetization because external Type-96 hysteretic inductors are used to represent the magnetizing inductance. Accordingly, only the resistive component of the magnetizing current will be enteredhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 as IEXPOS in the BCTRAN input file.

.36 - BCTRAN dialog box of the 400/132/18 kV transformer. Fig.

data specification the program offers to generate a BCTRAN input file and run ATP. It can either be performed by a Run ATP requests, (without leaving the dialog box), or selecting OK. If the BCTRAN-file is correct, a punch-file will be created. This file is directly included in the final ATP-file and there is no conversion to a library file as for lines/cables. The BCTRAN input file generated by ATPDraw is shown next. This file is given extension .atp and stored in the /BCT folder.

NEW DATA CASE

MODULE BCTRAN

$ERASE

Excitation test data card

&lt;  FREQ  &gt;&lt; IEXPOS &gt;&lt;  SPOS  &gt;&lt; LEXPOS &gt;&lt;IEXZERO &gt;&lt; SZERO  &gt;&lt;LEXZERO &gt;&lt;&gt;&lt;&gt;&lt;&gt;&lt;&gt;  3       50. .05600056      250.      140.                        http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3       0 2 3 0

Winding data cards

&gt;&lt;  VRAT  &gt;&lt;   R    &gt;&gt;&lt;  PHASE1  &gt;&lt;  PHASE2  &gt;&lt;  PHASE3  &gt;

version 5.6

154.729872           H_BUSAL_BUSAH_BUSBL_BUSBH_BUSCL_BUSC

76.2102355           L_BUSA      L_BUSB      L_BUSC

18.           T_BUSAT_BUSCT_BUSBT_BUSAT_BUSCT_BUSB

Short-circuit test data cards

&lt;&gt;&lt;  PIJ   &gt;&lt; ZPOSIJ &gt;&lt;  SPOS  &gt;&lt;ZZEROIJ &gt;&lt; SZERO  &gt;&lt;&gt;&lt;&gt;

2      710.33.4150145      250.33.4150145      250. 0 1

3      188.61.3951637      250.61.3951637      250. 0 1

3      159.       24.      250.       24.      250. 0 1

card ending short-circuit test data

$PUNCH

card ending BCTRAN data

NEW DATA CASE

CARD     Application Manual

nonlinearhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 magnetizing branch of the 400/132/18 kV auto-transformer is represented by delta coupled Type-96 hysteretic inductors in this study. The flux-current characteristic of these inductors can be obtained by means of the HYSDAT supporting routine of ATP. Fig.  6.37 shows the hysteresis loop of the Itype-1 material of ATP and of the magnetic core of the transformer.  1.51

.5

[%]

.5

Hyst-

.37 - The shape of the hysteresis loop of the transformer magnetic core  Fig.

with the material type 1 of ATP's HYSDAT supporting routine.

output file generated by the HYSDAT supporting routine is listed below. In this example the file is given a name HYSTR400.LIB and stored in the /USP folder.

&lt;      &gt;  Cards punched by support routine on  21-Jul-02  14.08.23  &lt;      &gt;

HYSTERESIS

$ERASE

C  IThttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3YPE   LEVEL    Request Armco M4 oriented silicon steel -- only 1 availab

1       4    That was ITYPE=1.  As for LEVEL=2, moderate accuracy outp

98.2    97.2    Current and flux coordinates of positive saturat

.68250000E 01 -9.49129412E 01

.45500000E 01 -9.43411765E 01

.10475000E 01 -9.23400000E 01

.91000000E 00 -9.03388235E 01

.84125000E 00 -8.86235294E 01

.13750000E-01 -8.51929412E 01

.14812500E 00 -8.11905882E 01

.55975000E 00 -7.43294118E 01

.29625000E 00 -6.28941176E 01

.91000000E 00 -4.57411765E 01

.13750000E 00  3.05894118E 01

.75125000E 00  4.23105882E 01

.59250000E 00  5.71764706E 01

.10475000E 01  6.86117647E 01

.33797500E 01  7.43294118E 01 -1.5

version 5.6 233

.74918750E 01  8.00470588E 01

.39362500E 01  8.51929412E http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db301

.28356250E 01  8.91952941E 01

.29625000E 01  9.20541176E 01

.13750000E 01  9.49129412E 01

.82000000E 01  9.72000000E 01

.35025000E 02  9.77717647E 01

.

[此处图片未下载成功]

Application Manual

a nonlinear characteristic can be connected to the Type-96 inductor in two ways: include as an external file, or enter flux-current data pairs directly in the Characteristic page as shown in Fig.  6.38. The Copy and Paste buttons of the dialog box provide a powerful way to import the whole characteristic from an external text file via the Windows clipboard or export it to another Type96 objects. It is thus possible to bring a HYSDAT punch-file up in a text editor, mark the characteristic, copy it to the clipboard and paste it into the Characteristic page. The number of data however must be less or equal to 64. No such limit exists for the included nonlinear charahttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3cteristics.

.38 - Importing the nonlinear characteristic from a HYSDAT punch-file. Fig.

complete ATP input file generated by ATPDraw for this study case is listed next:

NEW DATA CASE

Generated by ATPDRAW  July, Sunday 21, 2002

A Bonneville Power Administration program

Programmed by H. K. H&#248;idalen at SEfAS - NORWAY 1994-2002

--------------------------------------------------------

$DUMMY, XYZ000

dT  &gt;&lt; Tmax &gt;&lt; Xopt &gt;&lt; Copt &gt;

.E-6     .15

5       0       0       1       0       0       1       0

1         2         3         4         5         6         7         8

345678901234567890123456789012345678901234567890123456789012345678901234567890 /BRANCH

version 5.6

&lt; n 1&gt;&lt; n 2&gt;&lt;ref1&gt;&lt;ref2&gt;&lhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3t; R  &gt;&lt; L  &gt;&lt; C  &gt;

_BUSA                          .004                                   0         L_BUSB                          .004                                   0         L_BUSC                          .004                                   0   SOURCASUPLA                 2.  63.7                                         0   SOURCBSUPLB                 2.  63.7                                         0   SOURCCSUPLC                 2.  63.7                                         0   SOURCASUPLA               200.                                               0   SOURCBSUPLB               200.                                               0   SOURCCSUPLC               200.                                               0   T_BUSA                                 .01                                   0   T_BUSB                                 .01                                   0   T_BUSC            http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3                     .01                                   0 96T_BUSBT_BUSC             8888.   0.0                                         1          -36.825     -94.9129412     Application Manual

.4125     -93.7694118

.1375     -90.9105882

.2275     -88.0517647

.148125     -81.1905882

.05075     -68.6117647

.365      49.1717647

.66125      70.3270588

.57125      78.9035294

.55      85.7647059

.21125      90.3388235

.465      93.7694118

.2            97.2

.025      97.7717647

T_BUSAT_BUSB             8888.   0.0                                         1          -36.825     -94.9129412

.4125     -93.7694118

.1375     -90.9105882

.2275     -88.0517647

.148125     -81.1905882

.05075     -68.6117647

.365      49.1717647

.66125      70.3270http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3588

.57125      78.9035294

.55      85.7647059

.21125      90.3388235

.465      93.7694118

.2            97.2

.025      97.7717647

T_BUSCT_BUSA             8888.   0.0                                         1          -36.825     -94.9129412

.4125     -93.7694118

.1375     -90.9105882

.2275     -88.0517647

.148125     -81.1905882

.05075     -68.6117647

.365      49.1717647

.66125      70.3270588

.57125      78.9035294

.55      85.7647059

.21125      90.3388235

.465      93.7694118

.2            97.2

.025      97.7717647

_BUSA                          .006                                   0         H_BUSB                          .006                                   0         H_BUSC                          .006         http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3                          0 $VINTAGE, 1,

T_BUSAT_BUSC             6942.8436268432

T_BUSBT_BUSA             0.0

.8436268432

T_BUSCT_BUSB             0.0

.0

.8436268432

AR

H_BUSAL_BUSA             3.2888630659697 .42462348721612

version 5.6

L_BUSA                   -7.231251366149             0.0

.681001957452 .09492595191772

T_BUSAT_BUSC             2.3450004639366             0.0

.67537379274             0.0

.34949508527             0.0

H_BUSBL_BUSB             .1936225317E-15             0.0

-.677127449E-15             0.0

.1202491824E-14             0.0

.2888630659697 .42462348721612

L_BUSB                   -.677127449E-15             0.0

.2041578689E-14             0.0

-.282318606E-14             0.0

.23125http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db31366149             0.0

.681001957452 .09492595191772

T_BUSBT_BUSA             .1202491824E-14             0.0

-.282318606E-14             0.0

-.6542678427E-4             0.0

.3450004639366             0.0

.67537379274             0.0

.34949508527             0.0

H_BUSCL_BUSC             .1936225317E-15             0.0

-.677127449E-15             0.0

.1202491824E-14             0.0

.1936225317E-15             0.0

-.677127449E-15             0.0

.1202491824E-14             0.0

.2888630659697 .42462348721612

L_BUSC                   -.677127449E-15             0.0

.2041578689E-14             0.0

-.282318606E-14             0.0

-.677127449E-15             0.0

.2041578689E-14             0.0

-.282318606E-14             0.0

.231251366149             0.0

.681001957452 .http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db309492595191772

T_BUSCT_BUSB             .1202491824E-14             0.0

-.282318606E-14             0.0

-.6542678427E-4             0.0

.1202491824E-14             0.0

-.282318606E-14             0.0

-.6542678427E-4             0.0

.3450004639366             0.0

.67537379274             0.0

.34949508527             0.0

$VINTAGE, 0,

$UNITS, -1.,-1.

RL

/SWITCH

&lt; n 1&gt;&lt; n 2&gt;&lt; Tclose &gt;&lt;Top/Tde &gt;&lt;   Ie   &gt;&lt;Vf/CLOP &gt;&lt;  type  &gt;

H_BUSA       -1.      .045        1.                                   1   SUPLB H_BUSB       -1.      .045        1.                                   1   SUPLC H_BUSC       -1.      .045        1.                                   1   SUPLA H_BUSA     .0735        1.                                             1   SUPLB H_BUSB     .0785        1.    http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3                                         1   SUPLC H_BUSC     .0785        1.                                             1 /SOURCE

&lt; n 1&gt;&lt;&gt;&lt; Ampl.  &gt;&lt; Freq.  &gt;&lt;Phase/T0&gt;&lt;   A1   &gt;&lt;   T1   &gt;&lt; TSTART &gt;&lt; TSTOP  &gt; 14SOURCA 0   326600.       50.                                     -1.        1. 14SOURCB 0   326600.       50.     -120.                           -1.        1. 14SOURCC 0   326600.       50.      120.                           -1.        1. /INITIAL

/OUTPUT

SUPLB SUPLC H_BUSAH_BUSBH_BUSC

BRANCH

SWITCH

SOURCE

INITIAL

OUTPUT

PLOT

NEW DATA CASE

Application Manual

version 5.6

Application Manual

results of the simulation are shown in Fig.  6.39. In the reported case, the steadhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3y state magnetizing current of the unloaded transformer is interrupted at 45 ms producing high residual flux in two phases. As a result, a high amplitude inrush current may occur at a subsequent

[此处图片未下载成功]

.39 - Steady-state magnetizing current (upper curves) and the Fig.

current (lower curves) at a subsequent energization.

.5.2 Energization of a 132/15 kV generator step-up transformer (Exa_11.adp)

use of the icon customization and the advantages of the grouping feature of ATPDraw are demonstrated in this example. The simulated case is again a transformer switching study, in which a 155 MVA 132/15 kV Y/d coupled step-up and a 4 MVA 15/6.9 kV D/d coupled auxiliary transformer are energized together. The fast start gas turbine plant is located near to a 400/220/120 kV substation and the transformers are connected with the substation by a 120 kV single core XLPE cable. Duringhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 the step-up transformer energization the generator is still disconnected, so need not be considered in this study. The ATPDraw circuit of the simulation is shown in Fig.  6.40.

[此处图片未下载成功]

.40 - ATPDraw circuit (Exa_11g.adp) Fig. 6

version 5.6 237

Application Manual

.  6.40 shows several customized ATPDraw objects created by the Edit | Compress command. If you are not familiar with this grouping feature please read in section  5.1 of this Advanced Manual. This feature provides a powerful tool in advanced modeling. On Fig.  6.40 the nonlinear, hysteretic transformer objects, the parallel connected 3-phase breakers and the TACS objects for flux measurement were compressed into single objects, and the icon of each group has been customized, as well. The icon of some non-group objects were also customized, e.g. the LCC object of the XLPE cable. The uncompresshttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ed version of this case is also part of the ATPDraw's example collection and is shown in Fig.  6.41. Therefore, you can see how the grouping feature makes the circuit more readable.

[此处图片未下载成功]

.41 - ATPDraw circuit without using compress (Exa_11.adp). Fig. 6

model of the Ynd11 and the Dd0 transformers consists of a linear part (user specified library object or BCTRAN object) and a nonlinear hysteretic inductor. The capacitances between the transformer windings and ground have been considered, as well. These capacitances do not influence the inrush current significantly, but they need to be taken into account especially at delta coupled transformer terminals to avoid &quot;floating subnetwork found&quot; simulation errors. For more details about the model parameters please read in section  5.8.2 of the Advanced Manual.

compress option of ATPDraw can be used effectively to create new prhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3obe-type objects, as well. The 3-phase Flux probe of this example has been constructed by integrators (TACS | Transfer functions | General) objects, time controlled switches (to set zero initial conditions) and coupling to TACS objects. The output of the Flux probe (the instantaneous flux linkage of the transformer windings) can be used to analyze the operation of the model during steady state no-load conditions, and during the transformer de-energization/re-energization, as shown in Fig.

.42.

circuit breaker of the transformer has a common drive with mechanical phase shift of 60 electrical degrees. The making sequence is A-C-B with 3.33 ms delay between the poles and the breaking sequence is B-C-A. Some results of the simulation obtained by the elaborated model are shown next. Fig.  6.43 shows the flux linkage and the phase-to-ground voltages of the step-up transformer during the no-load breaking proceshttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3s. The residual flux is quite low in all phases, thus a subsequent energization will not produce high amplitude inrush current even if the making is done at the voltage zero crossing. When synchronizing the first pole to close with the bus voltage and energize the transformer close to the voltage peak, the inrush current amplitude will not exceed the peak value of the nominal load current of the transformer (see in Fig.  6.44).

ATPDraw version 5.6

Application Manual

Fig.

[此处图片未下载成功]

6.43 - Non-sinusoidal voltage oscillations appear after de-energizing the step-up transformer Fig.

(upper curves). The residual flux is less then 30% in each phases (lower curves).

version 5.6 239

[此处图片未下载成功]

Application Manual

[此处图片未下载成功]

6.44 - Interrupting the steady state no-load current of the step-up transformer (upper curhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ves) Fig.

the inrush current amplitude (below) when energizing the first pole of the breaker:

) at the voltage zero crossing, b) close to the voltage peak.

version 5.6

Application Manual

.5.3 Using the Hybrid Transformer component  (Exa_16.acp)

Hybrid Transformer component (XFMR) provides a topologically correct core model with individual saturation characteristics in legs and yokes calculated based on relative core dimensions. Further the saturation characteristic is based on the Frolich equation with an additional, optional air-core inductance thus improving the response above the last test report value. This is of great importance when it comes to over-excitation situations like inrush current simulations. The XFMR component in version 5.6 offers type 96 inductances even if these are not recommended for transient studies. This givhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3es on the other hand residual flux in the core after de-energization. In general advance Models controlled hysteretic inductors are needed to give good inrush current predictions.

.  6.45 shows the XFMR input dialog for the example Exa_16.acp

[此处图片未下载成功]

. A 3-legged stacked core is selected and this requires relative yoke dimensions to be given under Core data. A Triplx core (single phase units) does not require relative dimensions. Under Inductance and Core the short and open circuit test report data are given, respectively (Resistance automatically follow Inductance for Test Report data). The Winding sequence is set with the low-voltage winding as the inner. The XFMR dialog can work test report data directly. Creation of the saturation characteristics is automized (for type 96 half of the core losses is assigned to hysteresis losses with a Steimetz coefficient n=2, and a uniform width of the hyhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3steresis).

.45 – XFMR model example Exa_16.acp Fig. 6

version 5.6 241

Application Manual

the user clicks on OK ATPDraw performs an internal calculation of the leakage inductance in the same way as BCTRAN. The winding resistances are connected outside the A-matrix, however. The core model is fitted to the Test Report rms values by a Gradient Method optimization routine.

user should also click on the Settings… button

the Core page to select the type of nonlinear

(98, 93, or 96) and the number of points

linearized Frolich equation (maximum 9). A high

is required to get good inrush current

. The final slope inductance (part of the

-core inductance) is set to zero in this case.

data really required to estimate it. Using the

check box will estimate La=http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3μ0 6/a' where

factor a=6 is typical for core material M4 and a'

found from the optimization (with '=0)

.  6.46 – Core settings.

.  6.47 shows a simulated inrush currents switching in a 290 MVA transformer from the 16 kV side with zero residual flux. The same transformer is modeled both in BCTRAN and XFMR and the comparison shows that the XFMR gives about four times higher inrush currents. This is because the BCTRAN model incorrectly assumes linear extrapolation of the magnetization characteristic above the Test Report data. In addition the currents into the XFMR model have more reasonable waveshapes and attenuation.

[此处图片未下载成功]

[此处图片未下载成功]

modeled in BCTRAN and XFMR.

version 5.6

Application Manual

.6 Switching overvoltage studies with statistical approach (Exa_12.adp)

shttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3witching impulse withstand level of EHV line insulators are generally lower than the lightning impulse withstand level. Therefore, some measures are needed to protect the line against switching overvoltages, especially when the insulation level is rather low, like in case of line uprating. One or more of the following measures could be applied to reduce these overvoltages:   - mounting surge arresters at the line terminals and along the line

- application of circuit breaker with closing resistors

- synchronizing the breaker operations at line energization and reclosing

- limiting or eliminating the trapped charge at dead time of the 3-phase reclosing

influence of the latter two measures to the switching overvoltage distribution is analyzed in this example. The use of the master/slave feature of ATP's statistical switches is also introduced.

EMTP model shown in Fig.  6.48 has been elaboratehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3d for a line upgrading feasibility study to analyze the switching performance of a 400 kV compact line. The clearances, the location of the phase- and ground wires, and the length of the composite insulator strings are assumed known in this example.

[此处图片未下载成功]

.48 - ATPDraw circuit for the statistical switching study (Exa_12.adp). Fig. 6

investigated line has been divided into four sections, each of them represented by an LCC JMarti object. To set up the initial conditions of the line easily, a 3-phase voltage source is connected to the line at right having voltage amplitude equal to the desired trapped charge. This source is disconnected before the operation of the statistical switches to make the line unloaded. It is worth to mention that some care is needed when constructing the EMTP model for such a statistical simulations, because the unnecessary over-complication of the model may increase http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3the overall simulation time of that many statistical runs significantly.

.6.1 Setting program options for the statistical simulation

simulated switching incidence is a 3-phase reclosing in this study. Statistical switches of Gaussian-type represent the reclosing breaker. The master/slave dependency is now supported by ATPDraw, thus phase A is specified as master and the remaining two as slave. ATP requires the master switch be specified earlier in the ATP-file then a slave. ATPDraw ensured automatically this ordering. This is why the closing of the dialog box of a master switch is somewhat delayed.

version 5.6 243

[此处图片未下载成功]

[此处图片未下载成功]

Application Manual

.49 - Input parameters of master and slave statistical switches. Fig.

rest of program options and circuit parameter settings for a statistical study is very similarhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 to that of any other time domain simulations. There is one addition however. You need to specify the Switch study and Switch controls under ATP | Settings / Switch before generating the ATP-file.   Unless you need special settings, the Switch controls parameters need not be modified.

.  6.50 - Setting the parameters of the statistical study.

Output Manager found under ATP|Output Manager (F9) enables the user to select those output requests to be added to the statistical tabulation. The user can also group and scale the output requests. Example 12 requests as default only output of the MID voltage, but the terminal voltages and for instance surge arrester energy can be added. The selection of alternative statistical tabulation is shown in Fig.

[此处图片未下载成功]

6.52.

.6.2 Results of the statistical study

worst-case assumption the fault, which precedes the 3-phase rehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3closing in one or more phases has not been considered here. Taking that the inductive voltage transformers play a significant role in eliminating the trapped charge in the healthy phases during the dead time of reclosing, but CVTs or CCVT has no such effect, two different cases have been considered:

) the trapped charge is equal to the phase to ground voltage peak

) the trapped charge is 30% of the phase to ground voltage peak.

reclosing operations are synchronized to the bus voltage in this simulation. It means that the master switch is closed when the instantaneous value of the phase-to-ground bus voltage is equal to zero. The average delay for the slave switches in phase B and C is set 120 and 60 electrical degrees, respectively. The standard deviation of the operating time of the synchronous controller and the breaker has been considered as an additional parameter in the study:

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3

version 5.6

Application Manual

) accumulated deviation of the breaker and the controller operating time is 1 ms

) accumulated deviation of the breaker and the controller operating time is 2 ms.

statistical tabulation of the overvoltage distribution will be part of the LIS-file, as shown next:

) -------------------------------------------------------------------------------------------------- Statistical output of  node  voltage   0.3430E 06 |0             MIDA  MIDB  MIDC

distribution of peak voltage at node  &quot;MIDA  &quot;.

base voltage for per unit printout is  V-base = 3.43000000E 05

voltage         voltage  in     Frequency    Cumulative               Per cent     number         in per unit      physical units     (density)     frequency     .GE. current value         51 http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3          1.2750000      4.37325000E 05             0             0          100.000000

1.3000000      4.45900000E 05             2             2           98.000000

..........

2.1750000      7.46025000E 05             1            99            1.000000

2.2000000      7.54600000E 05             1           100             .000000

of preceding table follows:       Grouped data     Ungrouped data

= 1.66850000E 00     1.66882696E 00

= 3.85116162E-02     3.81739314E-02

deviation = 1.96243767E-01     1.95381502E-01

..........

) --------------------------------------------------------------------------------------------------   SUMMARY   SUMMARY   SUMMARY   SUMMARY   SUMMARY   SUMMARY   SUMMARY   SUMMARY   SUMMARY   SUMMARY    4 ) -------------------------------------------------------------------http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3------------------------------- The following is a distribution of peak overvoltages among all output nodes of the last data card that have the same base voltage.

distribution is for the maximum of the peaks at all output nodes with  V-base = 3.43000000E 05

voltage         voltage  in     Frequency    Cumulative               Per cent     number         in per unit      physical units     (density)     frequency     .GE. current value         51           1.2750000      4.37325000E 05             0             0          100.000000

1.3000000      4.45900000E 05             1             1           99.000000

............

2.2750000      7.80325000E 05             1            99            1.000000

2.3000000      7.88900000E 05             1           100             .000000

of preceding table follows:       Grouhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ped data     Ungrouped data

= 1.77125000E 00     1.77305706E 00

= 5.25173611E-02     5.27332819E-02

deviation = 2.29166667E-01     2.29637283E-01

, a brief summary of the simulation results is given next. Considering the metal-oxide arresters with 2 p.u. protection level at both ends of the line, the highest overvoltages appear in the inner points of the line. As an example, Fig.  6.51 shows the probability distribution functions of the switching overvoltages arising in the middle of the line. The four curves correspond to the following cases:

) Three phase reclosing with 30% trapped charge. Standard deviation of the accumulated operating time of the synchronous controller and the breaker is 1 ms.

) Three phase reclosing with 100% trapped charge. Standard deviation of the accumulated operating time of the synchronous controller and the breaker is 1 mhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3s.

) Three phase reclosing with 30% trapped charge. Standard deviation of the accumulated operating time of the synchronous controller and the breaker is 2 ms.

) Three phase reclosing with 100% trapped charge. Standard deviation of the accumulated operating time of the synchronous controller and the breaker is 2 ms.

it can be seen, the reclosing overvoltages are quite low even if the trapped charge is close to the voltage peak, if the reclosing operations are synchronized to the bus-side voltage zero by a point on wave controller.

version 5.6 245

Application Manual

%

[此处图片未下载成功]

50

.21.41.61.8

[此处图片未下载成功]

P.U.22.22.4 .51- Probability distribution function of the 3-phase reclosing overvoltages.  Fig. 6

http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3.52 – Output Manager and alternative request of Statistical Tabulation.Fig.

version 5.6

[此处图片未下载成功]

ATPDraw version 5.6 247

.1 PFC simulations in ATPDraw

Verify feature of ATPDraw enables the user to compare the line/cable model with an exact PI-equivalent as a function of frequency, or verify the power frequency benchmark data for zero/positive short circuit impedances, reactive open circuit line charging, and mutual zero sequence coupling. The Verify module supports the POWER FREQUENCY CALCULATION (PFC) of zero and positive short circuit impedances and open circuit reactive line charging, along with mutual zero sequence impedance for multi circuit lines.

supporting programs LINE CONSTANTS and CABLE CONSTANTS calculate the series impedance and the shunt admittance from geometrical data and material prophttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3erties. These electrical parameters are part of the printout file (.lis). The power frequency calculations give in principle the short circuit impedances and the open circuit reactive power. The line/cable may be a single circuit component with an arbitrary number of phases or a multi-circuit component where all circuits normally are three-phase. The following parameters are calculated for a single circuit in a line/cable with n conductors:

) All terminals at one end of the line/cable are connected to ground. A positive sequence symmetrical voltage is applied to the terminals at the other end and the positive sequence impedance is calculated: Z =E /I

voltage applied to the terminal i is:

=E  exp( j 2π (i 1)/n),  where n is the number of phases in the circuit.

positive sequence current is obtained from the terminal currents by the formula:

=1 [I1 I2 exp(j2π/n)    Ii exp(j2π(i 1)/n)   http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 In exp( j2π/n)] n

zero sequence impedance is calculated in a similar way:   Z0=E0/I0

voltage E0 here is applied to all terminals and I0 is the average current supplied by the source.

) All terminals at one end of the component are open (except the conductors which are specified to be grounded). A positive sequence symmetrical voltage is applied to the terminals at the other end and the positive sequence current component is calculated by the same formula as for the positive sequence impedance. The positive sequence open-circuit reactive power is then calculated by the formula:

*Q =Imn E  I  , where E  is the line to line voltage. ()

the voltage between two adjacent phases for an n-phase circuit gives E =V/[2 sin(π/n)]. The calculation I  is based on an ATP calculation with E   =1.0. Using this value for I  implies that

= V2 n

sin(π/n)2Im(I )

also automahttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3tically calculates the reactive power supplied by the source (Q1..Qn). The open-circuit reactive power can thus also be calculated by taking the average of these quantities for all phases and multiply by a factor 2 (since a peak value 1.0 is used in the calculation and the line-to-line voltage is specified as rms):

version 5.6 249

V2 2(Q1 Q2    Qn) Q =n

zero sequence open-circuit reactive power is calculated as well. The same voltage is then applied to all terminals at one end of the line. The zero sequence current is the average value of the current injected into the terminals. This current I0 is calculated by ATP with E0 = 1.0. Using this value for I0 implies that

= V2 n

sin(π/n)2Im(I0)

this case ATP automatically calculates the reactive power Q , injected into the circuit from the source. Similarly to the positive sequence values, the zerohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 sequence open-circuit reactive power is also equal to

V2 2Q0=(Q) n

a line/cable with several circuits, each circuit is tested separately. For short-circuit calculation the other circuit(s) is/are is also grounded at one end, while for open-circuit calculations all terminals are open. The mutual coupling between the circuits is calculated as well and called zero sequence transfer impedance. This is done by connecting all phases of each individual circuit to a common node. A current 3&#183;I0 is then applied to one of these common nodes circuit and the voltage on the other node is measured. All terminals at the other end of the component is grounded. The procedure is repeated for all circuits except the last one. Below is listed the xVerifyF.dat file for a 6-phase line.

NEW DATA CASE

.667E-9    -1.0

1               1

$PREFIX, D:\par

$INCLUDE, LCChttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3_6.lib, INZO1_, INZO1_, INZO1_, INZO1D, INZO1E, INZO1F $$

, OUTO1A, OUTO1B, OUTO1C, OUTO1D, OUTO1E, OUTO1F

$INCLUDE, LCC_6.lib, INZO2A, INZO2B, INZO2C, INZO2_, INZO2_, INZO2_ $$

, OUTO2A, OUTO2B, OUTO2C, OUTO2D, OUTO2E, OUTO2F

$INCLUDE, LCC_6.lib, INZS1_, INZS1_, INZS1_, INZS1D, INZS1E, INZS1F $$

, ######, ######, ######, ######, ######, ######

$INCLUDE, LCC_6.lib, INZS2A, INZS2B, INZS2C, INZS2_, INZS2_, INZS2_ $$

, ######, ######, ######, ######, ######, ######

$INCLUDE, LCC_6.lib, INPO1A, INPO1B, INPO1C, INPO1D, INPO1E, INPO1F $$

, OUPO1A, OUPO1B, OUPO1C, OUPO1D, OUPO1E, OUPO1F

$INCLUDE, LCC_6.lib, INPO2A, INPO2B, INPO2C, INPO2D, INPO2E, INPO2F $$

, OUPO2A, OUPO2B, OUPO2C, OUPO2D, OUPO2E, OUPO2F

$INCLUDE, LCC_6.lib, INPS1A, INPS1B, INPS1C, INPS1D, INPS1E, INPS1F $$

, ######, ######, ######, ######, ######, ######

$INCLUDE, LCC_6.lib,http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 INPS2A, INPS2B, INPS2C, INPS2D, INPS2E, INPS2F $$

, ######, ######, ######, ######, ######, ######

$INCLUDE, LCC_6.lib, INMS11, INMS11, INMS11, INMS12, INMS12, INMS12 $$

, ######, ######, ######, ######, ######, ######

BRANCH

SWITCH

INZO1_ 1       1.0       50.       0.0                          -1.0

INZO2_ 1       1.0       50.       0.0                          -1.0

INPO1A 1       1.0       50.       0.0                          -1.0

INPO1B 1       1.0       50.     -120.                          -1.0

INPO1C 1       1.0       50.     -240.                          -1.0

INPO2D 1       1.0       50.       0.0                          -1.0

INPO2E 1       1.0       50.     -120.                          -1.0

INPO2F 1       1.0       50.     -240.                          -1.0

INZS1_ 1       1.0       50.   http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3    0.0                          -1.0

INZS2_ 1       1.0       50.       0.0                          -1.0

INPS1A 1       1.0       50.       0.0                          -1.0

INPS1B 1       1.0       50.     -120.                          -1.0

INPS1C 1       1.0       50.     -240.                          -1.0

INPS2D 1       1.0       50.       0.0                          -1.0

INPS2E 1       1.0       50.     -120.                          -1.0

INPS2F 1       1.0       50.     -240.                          -1.0

INMS11-1        3.       50.       0.0                          -1.0

version 5.6

BLANK SOURCE

OUTPUT

CARD PLOT

NEW DATA CASE

xVerifyF.dat file describes the following 9 cases:

V&#183;://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3rω

V&#183;  cosω

[此处图片未下载成功]

E =1.0 V

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

[此处图片未下载成功]

3&#183; I0 Cir. 1- Cir. 2:  Z00=V12/I0

: (real and imaginary part). Z0 = R0   jX0.

.1 – LCC-Verify; Power Frequency Calculations.

[此处图片未下载成功]

Fig. 7

version 5.6 251

Appendix

phase of a circuit is connected to a 1 V amplitude voltage source with zero phase angle. The other end of the line is grounded. Z0 is calculated as the inverse of the injected current divided by the number of phases in the circuit. All phase conductors of other phases are open.

sequence short circuit impedance: (real and imaginary part). Z  = R    jX .

phases of a circuit are connected to a 1 V amplitude voltage source with phase angle -360*(i-1)/n where i is the phashttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3e number (1,2,3..) and n is the number of phases of the tested circuit. The other end of the line is grounded. Z  is calculated as the inverse of the positive sequence current. All phase conductors of other phases are open.

sequence line charging: Q0

phase of a circuit is connected to a 1 V amplitude voltage source with zero phase angle. The other end of the line is open. Q0 is the injected reactive power multiplied by the square of the user specified base voltage (multiplied with 2/n). All phase conductors of other phases are open.

sequence line charging: Q

phases of a circuit are connected to a 1 V amplitude voltage source with phase angle -360*(i-1)/n where i is the phase number and n is the number of phases of the tested circuit. The other end of the line is open. Q  is calculated as the average injected reactive power multiplied by the square of the user specified bahttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3se voltage (multiplied with 2/n). All phase conductors of other phases are open.

zero sequence impedance: (real and imaginary part). Z00 = R00   jX00.

phase of the ith circuit is connected to a 1 A amplitude current source with zero phase angle. The receiving end of the circuits i and j is grounded. The jth circuit is short-circuited and open in the sending end. Z00 is calculated as the voltage at the sending end of the jth circuit. The process is repeated for all circuits. All phase conductors of phases not belonging to the ith and jth circuit are open.

.2 Line Check

performing transient analysis of power systems, high frequency models of overhead transmission lines and underground cables must be developed. In this process, parameters like ground and conductor conductivity, cross-section geometry, and average overhead line height could be uncertain and questionable. Vhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ery often the only reliable benchmark data are sequential parameters at power frequency. It is thus of great interest to be able to verify the developed line/cable model at power frequency before simulating and analyzing transients. The present version of ATPDraw has in the LCC-module a built in option to verify a line segment [1]. This is done by calculating the short circuit input impedances and the open circuit reactive power consumption. In addition a frequency scan is supported. However, data for each line segment is rarely available, and in addition one would prefer to verify an entire line/cable length including the effect of transpositions. Instead of calculating the short circuit input impedance and the open circuit reactive power consumption it would be better to obtain the serial impedance and the shunt admittance along with the average mutual impedance and admittance between circuits in 6-phase and 9-phase cases. The nehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3w module integrated in ATPDraw involves an improved handling of the equivalent mutual coupling between circuits.

version 5.6

Appendix

.2.1 Single phase systems

, consider a single-phase circuit of length l with frequency domain distributed series

.2. The line is spited in segments of length impedances and shunt admittances, as shown in Fig.

.

[此处图片未下载成功]

.  7.2 – Single phase representation of transmission line. Z=R jωL [Ω/m], Y=G jωC [S/m].

currents and voltages at the sending and receiving ends will not be equal. The idea is further to use the measured quantities at both terminals to obtain the series impedance and shunt capacitance. Current balance at point x results in   i=Y u. The voltage drop between x and  x

u 2ux dx gives  =Z i. These two equations result in the wave equation =Z Y uwithttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3h the  x x

u(x)=A eγ x B e γ x, where the constants A and B are determined from the boundary conditions and γ=Z Y. The current is i(x)= Z 1  u= Z 1 γ A eγ x B e γ x  x()

. Short circuit case:

is the typical configuration for obtaining the series impedance. A sinusoidal voltage or current is applied at the sending end while the receiving end is grounded.

(0)=U0andu(l)=0 gives

B=U0and A eγl B e γl=0which result in

(x)=U0 sinhγ (l x)coshγ (l x) and i(x)=U0 Z 1 γ  sinhγ lsinhγ l    (1)

currents at the terminals are

(0)=U0 Z 1 γ

(l)=U0 Z 1 γ coshγ l1 1 ≈U0 (Z l) 1  1  (γl)2  (γl)4...  and     (2)  sinhγ l45 3 17 1 ≈U0 (Z l) 1  1  (γl)2  (γl)4...     (3) sinhγ l360 6

the approximation comes from a series expansion of the hyperbolic functions.

second quadratic term is elimihttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3nated in the following combination:

(0) 2 i(l)1  ~=U0 (Z l) 1  1  (γl)4... i=3 180        (4)

version 5.6 253

Appendix

total series impedance can thus be approximated by the following combination of the measured inputs and outputs:

=3 u(0)

(0) 2 i(l)sc1  =Z l  1  (γl)4... ≈Z l   [Ω]  180      (5)

same result is obtained if a current is applied at the sending end instead of a voltage.

. Open circuit case:

is the typical configuration for obtaining the shunt admittance. A sinusoidal voltage or current is applied at the sending end while the receiving end is left open.

(0)=U0andi(l)=0 gives

B=U0and A eγl B e γl=0which result in

(x)=U0 coshγ (l x)sinhγ (l x) and i(x)=U0 Z 1 γ  coshγ lcoshγ l    (6)

unknown terminal quantities are:

(0)=U0 Z 1 γ

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3aru(l)=U0 sinhγ l2 1 ≈U0 Y l  1  (γl)2  (γl)4...  and     (7) coshγ l15 3 15 1 ≈U0  1  (γl)2  (γl)4...  coshγ l24 2      (8)

the approximation again comes from a series expansion of the hyperbolic functions.

to the short circuit case an equivalent voltage is defined as:

2~=u(0) 2 u(l)=U  u (γl)4... 0 1  (γl) 336 3        (9)

total shunt impedance can be approximated by the following combination of the measured inputs and outputs:

=3 i(0)

(0) 2 u(l)2 1 Y l  1  (γl)2  (γl)4... 15 3 =Y l  1 1 (γl)4... ≈Y l    [S]=  5180 1  24    (γl)...  1  (γl) 336  oc(10)

same result is obtained if a current is applied at the sending end instead of a voltage.

. Comparison with input impedance/admittance

short circuit input impedance and the open circuit input admittance (scaled to get reactive power in ATPDraw) is for chttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3omparison

=u(0)

(0)sc2 1 =Z l  1 (γl)2 (γl)4...  and 15 3       (11)

version 5.6

=                Appendix i(0)

(0)oc2 1 =Y l  1 (γl)2 (γl)4...  15 3       (12)

these expressions there is a quadratic term present, but for short transmission lines the two approaches will give similar results.

. PI-circuits implications

far only a distributed parameter model has been investigated. However, concentrated parameter models are often used. Besides, the distributed parameter models in ATP are replaced by PI-equivalents during steady state calculation. This sub-section briefly outlines the implications of this.

.3 shows a PI-equivalent under short- and open circuit testing.  Fig.    i(l)            u(l)=0

[此处图片未下载成功]

uu

[此处图片未下载成功]

-

.  7.3 – Testing a PI-chttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ircuit. Left: short circuit; serial impedance. Right: open circuit shunt admittance.

procedure for calculation of the series impedance and shunt admittance in (5) and (10) will in this case result in

u(0)=i(0) 2 i(l)

i(0)=u(0) 2 u(l)sc (γl)2    and   =≈Z l 1 2 6 1 (γl)/6  Z l (γl)2    =Y l ≈Y l 1 2 12 1 (γl)/6  1 (γl)2/4YsPI    (13)

to the present quadratic term, the result in (13) will be less accurate than for distributed parameters models. Care must be taken to prevent wrong results for long transmission lines. For example by splitting the line up in smaller segments. In constant parameter distributed parameter line models the series resistance (R) is concentrated at each end (R/4) and at the middle of the line (R/2). This will result in some different formulations than in (13), with accuracy dependent on R.

solution to this problem is to request 'Ehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3XACT PHASOR EQUIVALENT' [2, 3] which prevents ATP from using lumped resistance. In such case the &quot;exact pi&quot; equivalent is used (as is also the case for frequency dependent transmission line models in ATP). The exact PI-equivalent is on the

.4. form shown in Fig.

[此处图片未下载成功]

u(0)

.  7.4 – Exact PI-equivalent

reference to (13) the calculated series impedance and shunt admittance become

[此处图片未下载成功]

version 5.6  255

and

Appendix ZsExact PIYsExact PI3 u(0)=i(0) 2 i(l)sc (γl)4Z3 sinh(γl) ≈Z l 1 =  180Y2 cosh(γl) 3 i(0)=u(0) 2 u(l)oc4 l(γ)Y3 sinh(γl)≈Y l  1 =  180Z2 cosh(γl)    (14)

see that the exact-pi equivalent gives the same result as the distributed parameter model.

.2.2 3-phase systems

. Positive and zero-sequence

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3A 3-phase circuit is tested with positive and zero sequence sources applied. In the positive sequence, phase number i is energized with a sinusoidal source with a phase angle -120&#186;&#183;(i-1). In the zero sequence system all phases are energized with a sinusoidal source with zero phase angle. In cases with several 3-phase circuits in parallel the other circuits are not energized and open. The series impedance and shunt admittance are calculated for each individual phase as deduced above. For example in phase a: Zsa=3 ua(0)/(ia(0) 2 ia(l)).

. Self-impedance/admittance

self-impedance and admittance of the 3-phase circuit j is defined as the average of the values for each individual phase: Zjj=1/3 (Zsa Zsb Zsc) and Yjj=1/3 (Ysa Ysb Ysc) in either the zero- and positive-sequence system.

. Mutual couplings

couplings are the equivalent impedance and admittahttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3nce between circuits. The deduction of

.5. Each 3-phase these quantities is base on an equivalent two-phase representation shown in Fig.

is equated by a single conductor with its self-impedance/admittance and with the average voltage and current distribution.

.5 – Two-phase representation Fig.

to the single-phase case, matrix expressions are now developed and approximated by series expansions. The end-result is equal to the single-phase case:

(0)=Zs ~i           (15)

~

[此处图片未下载成功]

i(0)=Ys u

version 5.6

with

Y12  ZZ  Y Y

,   Zs= 1112 , Ys= 1112

Z12Z22   Y12Y22 Y12   u(0)  i(0)

(0)= av1 ,i(0)= av1 ,

uav2(0)  iav2(0)

~ 1 u(0) 2u(l) ~ ~i1 1 iav1(0) 2iav1(l)  uav1~== , u= ~1 =  av1i~  u2 3 uav2(0) 2uav2(l)  i2  3  iav2(0) 2iav2(l)   ://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3

(16) (17) (18)

unknown mutual impedance and admittance becomes

uav1(0) ~i1

Z12= Z11  ii 1 2

~ iav1(0) u1   Y11  Y12=

u1 u1 u2

[此处图片未下载成功]

[此处图片未下载成功]

(19) (20)

[此处图片未下载成功]

In the positive sequence system the average currents and voltages tend to be very small, and for a perfectly symmetric and transposed systems exactly zero. In such situations the positive sequence coupling has no meaning. The typical test condition is to apply 1 pu current at both circuits with

[此处图片未下载成功]

the other ends grounded to obtain the mutual impedance. For mutual admittance the test condition is to apply 1 pu at one and 0 (or -1) pu at the other circuit and leaving the other ends open.

[此处图片未下载成功]

7.3 Hybrid Transformer, XFMR

modeling of the transformer is based on the magnetic circuit thttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ransformed to its electric dual [7, 8]. The leakage and main fluxes are then separated into a core model for the main flux and an inverse inductance matrix for the leakage flux. The copper losses and coil capacitances are added at the terminals of the transformer. The resulting electrical circuit is shown in Fig.  7.6. Only standard EMTP elements are used.

.  7.6 – Electric model of the Hybrid Transformer [9],

-windings (H and X), 3-phases, 3-legged core.

version 5.6

parameters can be based on three different data sources; typical values, test report, and design information. The three sources can be selected independently for resistance, inductance, capacitance, and core. Test report input is based on standard open- and short-circuits tests, with capacitance measurements as an additional option. This is the http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3normal choice of data source for existing transformers. Design data requires the geometry and material parameters of the windings and the core. Such data are rarely available so this option is more for research purposes. The Typical value option uses available text book tabulated values of leakage impedance, copper and core losses, and magnetizing current to estimate model parameters. This is suitable when the transformer is not purchased yet, or data is unavailable in an initial study. However, such model must be used with caution.

.3.1 Leakage inductance

leakage inductance is modeled with an inverse inductance matrix (A-matrix). The matrix has dimension (nw 1) np where nw is the number of physical windings, the core is connected to the nw  1 winding, and np is the number of phases [7-9]. The coupling (auto, Y, D), turns ratio, and phase shift are produced directly in the A-matrix. All possible phase shifts are http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3supported. The A-matrix has the following structure for a three-winding, three-phase transformer:

a11a12a13a14

a aaa (1)      21222324   Aw0 whereAw=

a31a32a33a34

Aw

a41a42a43a44

ABC are the three phases and PSTC stands for primary, secondary, tertiary, and the core (

[此处图片未下载成功]

nw 1) winding.  AwA=  0

0

A

A-matrix is assumed to have no mutual coupling between the phases. The entire zero-sequence effect is modeled in the attached core. The Aw-matrix is established according to the EMTP Theory Book [5] Section 6.4, and Section 5.2.4 p. 31 in [7].

.3.1.1 Typical values

leakage reactance is established from [11] using the lowest value in the typical range. In the case of a three-winding transformer the leakage reactance (in pu) between the inner and outer winding is approximated ahttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3s the sum of the other two. In this case it is assumed that the medium voltage winding is the middle one.

.3.1.2 Test report

leakage reactance is calculated from the standard test report short circuit data (positive sequence).

[pu]=          (2)

the case of an autotransformer the reactances are scaled according to the Theory Book [5] Section 6.7.

.3.1.3 Design data

leakage reactances are calculated according to classical MMF distribution theory as shown in [7, 8]. Both cylindrical and pancake windings are supported.    258

version 5.5

.3.1.4 Handling of the core winding

artificial core winding is related to the leakage channel between the inner physical winding and the core. A parameter K=a1/a2 is defined in [7, 10] where a1 is the width of the inner leakage channel and a2 is the width of the leakage channelhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3 between the inner and the outer/middle winding. A fixed value K=0.5 is used in ATPDraw. If the pu leakage reactances XML, XMH, and XHL (L=inner, M=middle, H=outer) for a three winding transformer are given then the leakage reactances to the core winding are assumed to be [7, 10] XLC≈K XML,XMC≈XLC XML=(K 1) XML, and XHC≈XMC XHM=(K 1) XML XHM           (3)

.3.2  Winding resistance

winding resistances are added externally at the terminal of the transformer (A-matrix). Optionally, the resistances can be frequency dependent.

.3.2.1 Typical values

typical winding resistances (at power frequency) are in principle based on [12]. A function (4) is established that takes in the parameter u [kV] and s [MVA] and returns the resistance in %. Data for a 290 MVA/ 420 kV transformer (Table I) were used to extend the data given in [12]:

u

=0.7537

15

.0859http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3

s 0.2759  [%]

(4)

.3.2.2 Test report

test report data are given at power frequency. The per unit short circuit resistances are calculated from short circuit power losses in the test report (positive sequence). The winding resistance (in pu) is assumed to be equally shared between the windings in the case of a two-winding transformer. In the case of a 3-winding transformer the traditional star-equivalent approach is used.

the case of an auto-transformer the short circuit resistances are recalculated according to the

[此处图片未下载成功]

power balance used in [10]. The approach used for reactances (from the Theory Book [5]) did not work out for the resistances.

.3.2.3 Design data

user can specify the winding conductivity σ, the equivalent cross section A of each turn, the average length l of each turn, number of turns of the inner winding N. The DC resistance is nhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ormalized to the power frequency. If the resistance is assumed to be frequency dependent the conductor area must be specified in height and width (which determines the stray losses).

.3.2.4 Frequency dependency

report resistances are assumed to followRS(ω)=R0R0 is the resistance at the

version 5.6

power frequency ω0. This expression results in considerably lower values than suggested in Fig. 26 in [7]. This needs to be further investigated. The design data resistances are assumed to follow eq. (37) in [7].

calculated R(ω) and ω value pairs are fitted to the function (two-cell Foster equivalent)

(ω)=R0 L(ω)=

ω2 L1

ω

L1

ω2 L22

R2

ω

L22

(5)

R12

ω2 L1

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3arR22R2 ω2 L22

the resistances R1 and R2, and inductances L1 and L2 as unknowns. The fitting routine is

on a Genetic Algorithm implemented in ATPDraw. The object function is defined as OF= min (|R(ω)-RS(ω)| |ω L(ω)|) contrained to positive unknowns. A negative inductance L0=-L1-L2 is added in series with the winding resistance to compensate for the inductance of the Foster cells. A constraint is put on the total inductance |L0| &lt;Lw where Lw is the inverse of the diagonal Aw-matrix element, [7] section 5.4.2. The constraint is handled simply by setting L1=L2=0.5 Lw when the constraint is violated and then continue to obtain new optimized values for R1 and R2.

.3.3  Capacitance

C-matrix is split in two halves and connected to each end of the physical windings. The capacitance matrix C is based on the following two matrices:

C11C12

=  C21C22

://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ar  C31C32

CAA

C23   and Cp= CBA C33   CCA

CCC

(6)

Cw matrix contains the capacitances between windings 1-3 equal in all phases. The capacitance matrix Cw is built up like a nodal admittance matrix. The Cp matrix contains capacitances that are specific to phase A, B, or C. These are typically connected to the outer windings. The total C-matrix is then built on these two symmetrical matrices dependent on the type of winding (pancake/cylindrical). The concept “outer winding” will be different for pancake and cylindrical windings.

.3.3.1 Typical values

capacitive coupling factor Kc can be specified by the user with a default value of 0.3. The concept of transient recovery voltage (TRV) is used to calculate the effective capacitance when the inductance is known [13]. IEEE standard C37, Fig. B2 [14] is used to obtain the typical fhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3requency of the TRV for a known voltage level and fault current.

(U,S,Xpu,f)=

I

πU fTRV(U,I) [μF]        (7)

U in [kV], S in [MVA] and  I=

[kA]

U Xpu

the case of typical values, the Cp matrix (between phases) is always set to zero for lack of any better choice. For a two-winding transformer the Cw matrix is calculated as

[1,2]=CPS=Kc Ceff(US,S,XPS,pu,f)Cw[1,1]=CPP=Ceff(UP,S,XPS,pu,f) Cw[1,2] Cw[2,2]=CSS=(1/Kc 1) Cw[1,2]

(8)

version 5.5

a three winding transformer the typical capacitance is more complicated with several coupling factors involved. Here a simple approach is used:

[1,3]=CPT=0

[2,3]=CST=Ceff(US,S,XST,pu,f) Cw[2,2]  Cw[3,3]=CTT=Ceff(UT,S,XST,pu,f) Cw[2,3]

(9)

approach could be further discussed and improved.

.3.3.http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db32 Test report

the test report the capacitances between each winding and ground and between all windings is assumed to be directly specified while the Cp matrix is set to zero. All values must be specified per phase.

[此处图片未下载成功]

7.3.3.3

[此处图片未下载成功]

Design data

calculation of design data capacitances are based on [7] chapt. 5.3, p. 33-42. The user has to specify the winding geometry as well as the various equivalent permittivities of insulation system. Standard formulas for calculating the capacitance between cylinders and for cylinders over planes are used with end effect and tank effect adjustments.

.3.4 Core

core model is connected to the “core winding” terminals of the A-matrix. Triplex (single phase cores), stacked cores with three and five legs, and shell form cores are supported. Basically the inductive and resistive core parts are treated independently, bhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ut this is a point that requires more research particularily for 3- and 5-legged cores where harmonics in the flux creates additional losses. The core losses are represented by a linear resistor and the nonlinear inductances are modeled by the Frolich equation (10). Each part of the core is modeled with its own core loss resistance and nonlinear inductance using information about their relative cross section and length to scale the values. Fig.  7.7 shows the core model for a 5-legged transformer.

.  7.7 – 5-legged stacked core model. The αβγ terminals are the nw 1 winding.  Left: Practical ATPDraw implementation. Right: Topologically correct model.

version 5.6

is assumed that the magnetic material is characterized by five parameters a, b, c , d and e. A list of typical steel materials is developed based on fitting http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3the manufacturer’s data from state of the art catalogues. Older steel materials will have a different characteristic and the losses are typically higher. The material list is only used for design data and typical values.  =

B/H relationship is assumed to follow the Frolich equation where the optional parameter c (introduced in [15]) improves the fitting to test report data around rated voltage

=μ0 H            (10)

specific loss is assumed to follow

f

[W/kg]=   d B2 e B10        (11)

f is the power frequency.

specific loss is traditionally (for instance Westinghouse T&amp;D reference book, 1964) assumed

x said to be 3 for modern materials in the year of to be P=Ke (f t Bmax)2 Ke f Bmax

. In the above expression t is the thickness of the laminates. The traditional expression was tested on modern material data with littlhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3e success.

.  7.8 shows the fit of the specific losses and DC-magnetization curve of ARMCO M4 steel. The Frolich fitting is not very good, and in Fig.  7.8b fitting around the knee point (nominal flux) was preferred at the sacrifice of high field fitting (B=1.9 T). Similar fitting is performed for the other core materials.

.5

()

[A/m

[此处图片未下载成功]

]

[W/kg

[此处图片未下载成功]

]

[此处图片未下载成功]

210

.4

.8

[T]

.21.62

.40.81.21.62

.  7.8a) – Core loss curves (c0)    Fig.  7.8b) DC-magnetization curve 7.3.4.1 Inductance modeling:

basic Frolich equation in (10) is reformulated as a current flux-linkage characteristic by introducing the flux linkage λ=B A N and the current i=H l/N where N is the number of turns of the innehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3r winding, A is the cross section, and l is the length of the involved core section. This gives

version 5.5

[此处图片未下载成功]

λ=

[此处图片未下载成功]

[此处图片未下载成功]

Appendix

= La i/lr   (12)

the constants a'

[此处图片未下载成功]

=a lL/(N2 AL), b'=b/(N AL)and c'=clength (lL) and cross section area (AL) of the core leg, are determined in an optimization process;

(a',b',c')=∑(Imeas,rms(Ui,rms) Icalc,rms(Ui,rms,a',b',c')) for n excitation levels.

=1

.  7.9 Core dimensions, 5-legged stacked core. The user must provide AY/AL, AO/AL, lY/lL, lO/lL

final characteristics are determined by using the relative (to the main leg) dimensions for the corresponding section, Ar and lr. The nonlinear inductances are implemented as optional type 98, 93, or 96 inductances in ATP.://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3r

.3.4.2 Core loss modeling

core loss is split in parts associated with individual core sections. It is assumed that the core loss is proportional to the core volume and to the square of the rms voltage across each section of

.7 (node IX0001) is the time the electric dual. The voltage, Uo, in the neutral point in Fig.

of the neutral flux found during the Frolich optimization described above. Is is assumed that the inductive current components determine the voltage distribution. For a 5-legged core Ploss=3Pleg 2Pyoke 2Pout=p (3 2 Vry (Uy/U)2 2 Vro (Uo/U)2)    (13)  where Vry and Vro are the relative volumes of the yoke and outer legs respectively.  and where Uy and Uo are the rms value of the voltage across the sections.

a 3-legged core the outer leg volume is zero and for triplex and shell form core the loss distribution is straight forward and determined only by the main leg volthttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3age.

the type 96 modelling, half of the loss is included as hysteresiss loss scaled by a Steinmetz coefficient of 2. The hysteresis has a uniform width.

.3.4.3 Typical values

estimation of the magnetizing current (Im) is based on [12]. Some fitting of the data is performed which results in

BIL

=0.73

350

.2933

s     20

0.2154

[%]

0.2134

(14)

the basic insulation level (BIL) is known and

u

=0.855

150

.2283

s     20

[%]

[此处图片未下载成功]

(15)

version 5.6

BIL must be estimated.

[此处图片未下载成功]

BIL is in [kV], u

[此处图片未下载成功]

is the rated voltage in [kV], and s is the rated power in [MVA].

a typical core model the user has to specihttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3fy the maximum B-field (normally 1.5-1.7 Tesla) and the maximum core loss density. First a core material has to be guessed and this gives the a and b values in the Frolich equation (and possibly also the c and d values that would replace p).  The following relationships are then assumed:

λmax=H

[此处图片未下载成功]

UrmsUrms

=Bmax A N A N=ωω Bmax       (16)

(17)

simplistically assumes a sinusoidal magnetizing current.

gives the parameter of the fluxlinkage-current characteristic:

N

ω Bmax1

'=b ≈b

N urmsa'=a

≈ω (1 b Bmax)

,

(18)

'=0

see that the expressions for a’ and b’ are independent of the magnetic material property a. The typical value of b seems to be fairly constant for standard core materials and a value of 0.5 is assumed in ATPhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3Draw.

core loss is estimated as

=p ρ A l=p ρ

(1 b Bmax) 2 urms irms

ω a Bmax

[此处图片未下载成功]

(19)

p [W/kg] and ρ [kg/m3] are given and the volume A l is estimated from (16) and (17).

.3.4.4 Test report

user specifies the excitation voltage in [%], the current in [%] and the core loss in [kW]. The core loss is used directly as explained above to obtain the core resistances. For now the core resistances are assumed to be linear and the core loss value at 100 % excitation is used.

inductive magnetizing current for each point is calculated as

=       (20)

.7 This results in a sequence of excitation points (Urms and Irms). The magnetic circuit in Fig.

sinusoidal fluxes is solved and the rms values of the line currents are calculated and compared to measured ones. Optimized valhttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ues of a’, b’ and c’ (optional) in (12) are found by a Gradient Method implemented in ATPDraw. If a single point is specified the core model is linear.

version 5.5

.3.4.5 Design data

design data the user directly specifies the core material with its B-H relationship (a and b values in (10)). The absolute core dimensions and the number of inner-winding turns N are known, so the inductances can be found directly from (12). Based on manufacturer data the core losses can be established from (11) with B=

Uω A N

known values of the core weight

(volume and density) the core loss can be estimated.

.4 References

[1] ATPDRAW version 3, User Manual, TR A4389, EFI, Norway, 1996

[2] Ned Mohan, Computer Exercises for Power Electronic Education, 1990, Department of

Engineering, University of Minnesota.http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3

[3] ATP-EMTP Rule Book, Canadian-American EMTP Users Group, 1997 [4] Lauren Dube, MODELS in ATP, Language manual, February 1996

[5] H.W. Dommel, Electromagnetic Transients Program. Reference Manual (EMTP Theory

), Bonneville Power Administration, Portland, 1986.

[6] L. Prikler, Main Characteristics of Plotting Programs for ATP, EEUG News Vol. 6,

. 3-4, August-November 2000, pp. 28-33

[7] B. A. Mork, F. Gonzalez, and D. Ishchenko: “Parameter estimation and advancements in

models for EMTP simulations. Task MTU-7: Model performance and sensitivity analysis”, Bonneville Power Administration, Portland, OR, 2004.

[8] B.A. Mork, F. Gonzalez, D. Ishchenko, D. L. Stuehm, J. Mitra.” Hybrid Transformer Model

Transient Simulation-Part I: Development and Parameters”, IEEE Trans. Power Delivery, Vol. 22, pp. 248-255, 2007.

[9] B.A. Mork, F. Gonzalez, D. http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3Ishchenko, D. L. Stuehm, J. Mitra, “Hybrid Transformer Model

Transient Simulation-Part II: Laboratory Measurements and Benchmarking”, IEEE Trans. Power Delivery, Vol. 22, pp. 256-262, Jan. 2007

[10] B. A. Mork, F. Gonzalez, D. Ichshenko, “Leakage inductance model for Autotransformer

simulation”, in Proc. Int. Conf. on Power System Transients, paper 248, 2005. [11] J. J. Graininger and W. D. Stevenson: Power System Analysis, McGraw-Hill 1994. [12] A. Greenwood: Electrical Transients in Power Systems, Wiley, 1991.

[13] IEEE Working Group 15.08.09, Editors: A. M. Gole, J. Martinez-Velasco, A. J. F Keri,

and analysis of power system transients using digital programs, IEEE 99TP133-0, pp. 4.12-4.13, 1998.

[14] IEEE Guide for Transient Recovery Voltage for AC High-Voltage Circuit Breakers Rated

a Symmetrical Current Basis, ANSI/IEEE Standard C37.011-1994.

[1http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db35] N. Chiesa, “Power Transformer Modelling: Advanced Core Model”, M. SC. Thesis,

di Milano, Italy, 2005.

[16] C. Zhu, R.H. Byrd and J. Nocedal : L-BFGS-B: Algorithm 778: L-BFGS-B, FORTRAN

for  large  scale  bound  constrained  optimization, ACM Transactions on Mathematical Software,  Vol 23,  Num. 4, 1997 Page(s): 550 – 560.

[17] W. H. Press, S. A. Teukolsky, W. T. Vetterling, B. P, Flannery: Numerical recipes, 2nd Ed.

, Cambridge University Press.

version 5.6

.5 Index $

$Include...................................................103 $PARAMETER.........................................73 $Vintage...................................................102 A

mode................................................43 ADF files....................................................14 Alternative Transients Phttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3rogram.................10 licencing................................................19 on-line licensing.....................................19 Armafit command....................................157 ATP

file..................................................21 DBM-file..............................................183 GNU version..........................................25 input file.................................................48 lib-file...................................................154 punch-file.............................................154 Rule Book..............................................41 run ATP............................................25; 50 simulation...............................................48 Watcom version.....................................25 ATP menu............................................24; 69 ATP settings...............................................69 ATPDraw...................http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3..................................9 ATPDraw.ini.....................................23 configuration........................................23 download...............................................20 examples..............................................205 hardware requirements.......................20 include files............................................22 installation............................................20 interface..........................................23; 31 on-line help............................................26 options...................................................91 project file..............................................21 support file.............................................21 ATP-EMTP-L mailing list.......................26 attributes.....................................................36 Auto-detect errors......................................70 auto-transformer...............................http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3........234 B

......................................23; 122; 189 BCTRAN dialog..............................175; 234  266

file...........................................177 Bonneville Power Administration................9 C

CONSTANTS.............................23; 117 cable data page.........................................161 CABLE PARAMETERS.................................117 Canadian/American EMTP User Group

-huei Liu...........................................10 W. Scott Meyer......................................10 Characteristic tab.....................................102 circuit comments........................................32 circuit files.................................................58 circuit font..................................................67 Circuit Text..............................................105 circuit window...................http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3.........................33 Circuit window.....................................31; 32 C-like..........................................................13 command line options..............................25 comment dialog..........................................65 comment line..............................................66 Component dialog16; 36; 41; 42; 51; 64; 76; 82; 83; 86; 88; 89; 90; 100; 101; 102; 112; 113; 117; 120; 122; 124; 125; 132; 138; 141; 170; 171; 172; 188; 217; 218

selection menu....31; 32; 35; 100 compress.....................................63; 138; 192 Connection dialog......................51; 105; 221 connections.................................................37 copy............................................................61 copy graphics.............................................61 creating ATP-file......................................48 customizing objects............................http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3......183 cut...............................................................61 D

Data Design.........................................9 DATA BASE MODULE..................................23 DBM-file..................................................184 DC machine..............................................146 default table size........................................12 Default view options..................................95 delta T........................................................49 Directories page.........................................94 distributed line.........................................116 download...................................................20 draw relation......................................33; 131

version 5.5

...............................................43; 61 E

ATP-file.........................................49; 78 Edit circuit.......http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3...........................65; 100; 141 Edit commands.........................................81 edit component...........................................87 Edit group...........................................64; 141 Edit LIS-file..............................................79 Edit menu...................................................36 edit operations..........................................35 edit options.................................................95 edit settings.................................................95 Electromagnetic Transients Program...........9 EMTP.........................................................10 applications...........................................15 Rule Book.............................................269 TPBIG.EXE............................................23 user group...............................................19 enclosing pipe...........................................157 environmehttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3ntal variables

, WATDIR, GNUDIR..............25 export circuit..............................................59 external programs.......................................24 extract.........................................................64 F

probe.................................................240 Format page................................................49 Fortran......................................................129 G

......................................................35 ground symbol............................................47 group customization.................................143 Group dialog...........................................107 group folder..............................................139 Group no. field.........................................102 group selection...........................................43 grouping..................................137; 192; 226 GTPPLOT.http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3................................................13 H

FREQUENCY SCAN....................28 Harmonic source....................................152 Help editor............................................85; 90 Help menu..................................................96 Help topics..................................................97 Hide button...............................................102 hierarchical modeling...................................9

version 5.6

&#248;idalen.................................................9; 26 I

editor.............................................84; 88 Import button............................................177 import circuit..............................................59 Include characteristic................................122 induction machine....................................146 initial conditions...........http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3......................10; 129 J

line.................................................159 L

object......................................154; 205 library object.............................................131 LINE CONSTANTS................................23; 117 line data settings.......................................160 LINE MODEL FREQUENCY SCAN................164 line/cable dialog................................117; 155 linear branch.............................................112 lines/cables.......................................109; 115 Linux...........................................................13 LIS-file.......................................................49 load flow.............................................73; 132 M

...................................................109 Main menu............................................32; 58 Main window...................................http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3.....32; 57 Make File As..............................................48 Map window.........................................33; 96 master/slave..............................................246 metafile...............................................59; 165 miscellaneous parameters...........................48 model file....................................................22 MODELS.....................10; 11; 110; 122; 168 input file structure.................................124 model file..............................................171 mod-file..................................................86 new object............................................171 record....................................................174 sup-file...................................................87 MODELS language..................................168 Modified flag..............................................48 mouse operations..............................http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3..........34 move label..................................................33 multi-layer circuit.....................................137 multilevel modeling..................................137

circuit..........................................38; 58 Noda line..................................................159 Node attribute..........................................172 Node data window.....................................34 Node dialog..............................................105 nonlinear branch......................................113 nonlinear characteristic............................103 O

menu.............................................37 Open group dialog.....................................34 Open probe dialog......................................36 open project................................................58 Optimization......79; 198; 199; 200; 201; 202 Output http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3combo box.....................................46 Output Manager.............76; 77; 78; 247; 249 Output request..........................................102 Output settings...........................................70 P

Engineering Corporation...............10 paste...........................................................61 PCPLOT.....................................................14 phase sequence...........................................53 plotting programs....................................13 PlotXY.......................................................14 polygon selection.......................................61 postprocessor.............................................13 POWER FREQUENCY CALCULATION..164; 253 Power Quality Indexes...............................13 Preferences page........................................93 Probe Curr..................................................40 Probe dialog.............http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3...............................107 Probe Volt..................................................40 probes &amp; 3-phase.....................................111 project file............................................48; 58 public domain............................................10 R

......................................................43; 60 reference object..........................53; 112; 132 refresh........................................................67 reload icon..................................................88 rubber band..........................................62; 63 run ATP................................................48; 75 running simulation.....................................50 S

circuit.................................................48  268

project................................................58 selec group........................................http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3.........35 select group................................................43 select object................................................61 Semlyen line.............................................159 Shortcut menu............................................99 simulation settings...............................49; 69 Simulation sub-menu.................................48 single core cable.......................................157 sorting cards.........................................49; 71 sources......................................................109 splitter......................................................111 splitter object..............................................51 standard components............................27; 82 standard library........................................133 statistical switch...............................150; 245 Status bar..............................................33; 65 support file..........http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3.......................................82 supporting routine..............................11; 175 switches....................................................109 synchronous machine...............................146 SYSTRAN Engineering...............................9 T

...........................................10; 11; 110 coup......................................................127 devices..................................................128 transfer functions..................................128 TACS menu..............................................126 Text editor............................................79; 90 toolbar........................................................43 Tools menu.................................................88 transformer inrush....................................233 Transformers....................................109; 121 Saturable transformer......144;182;217-220 Selection menu.........http://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3............................121 transposition.....................................112; 116 transposition object....................................53 trapezoidal rule...........................................10 U

......................................................43; 60 universal machine....................120; 146; 222 untransposed.............................................116 User specified

new objects..............................183 nonlinear transformer.......................189 Selection menu.............................110; 131 sup-file...................................................82

version 5.5

V

.....................................................74 Verify button............................................157 View options..............................................68 W

://www.wendangwang.cohttp://www.wendangwang.com/doc/ed72a89ca3610bacfbaa5db3m.........................................20 http://www.wendangwang.com........................................19 X

..............................122; 179; 243; 261 Z

PL4.................................................13 Windsyn.............95; 121; 152; 226; 227; 230 zoom...........................................................67

version 5.6

version 5.5

文档下载网是专业的免费文档搜索与下载网站，提供行业资料，考试资料，教学课件，学术论文，技术资料，研究报告，工作范文，资格考试，word文档，专业文献，应用文书，行业论文等文档搜索与文档下载，是您文档写作和查找参考资料的必备网站。

文档下载 https://www.wendangwang.com/

亿万文档资料，等你来发现