____________________________________________________________________________________

Specifier – Use this Section for all projects with fire alarm work on the UW Seattle Campus.  The A/E is expected to modify portions of this Section as necessary to accurately reflect conditions of the project.

This Section is maintained by the University of Washington Environmental Health and Safety Department (EH&S).  Consultants should confer with EH&S for support while editing this specification.  Contact Mark Murray at 206-616-6261 or mmurray@uw.edu.

___________________________________________________________________________________

PART 1 - GENERAL

  - SUMMARY

- This Section specifies requirements for the design and installation of a complete fire detection and alarm system.  The scope of work includes, but is not limited to, the following:

_______________________________________________________________________________

Specifier – Edit the following list as appropriate for the project.

____________________________________________________________________________________

- Permanent signs, labels, and operational instructions.

- All conduit and wiring associated with the fire detection and alarm system (including electromagnetic door closures/holders, specified elsewhere in these Specifications).

- Smoke detectors, heat detectors, and manual alarm stations.

- Speakers (or horns), strobes, remote test switches and remote lamps.

- Connection to the TrueSite System.

- Remote annunciator panel(s).

- Provision of a one-way communication system as part of the audio evacuation system.

- Provision of a two-way fireman’s telephone system.

- Provision of auxiliary controls, wiring and switches including interposing control, monitor relays, and interconnection coordination for the operation of the following systems:

- Campus Automated Access Management System (CAAMS) door control

- Fan control, smoke/fire damper interface

- Elevator recall

- Sprinkler systems

- Stair pressurization

- Emergency responder radio coverage system

- Refrigerant leak detection system

- Fire suppression systems

- The Contractor shall provide all services, miscellaneous parts and labor required to design and install a complete functioning system, in accordance with the manufacturer’s instructions and recommendations.

  - ACRONYMS AND DEFINITIONS

- AHJ		Authority Having Jurisdiction:  The approving authority for this section shall be the Seattle fire department.

- EH&S	UW Department of Environmental Health and Safety, the Owner’s

- subject-matter expert and reviewer.

- Emergency  	A failure of the installed system which, in the sole opinion of the

Owner, creates an unsafe or intolerable condition requiring immediate correction.

- FACP	Fire Alarm Control Panel

- Local  	Means that the main office and service center are located within 	50 miles of the job-site.

- SFD	City of Seattle Fire Department

- TrueSite System	Seattle campus building fire alarm panels, monitoring and control network.

- Vendor	The manufacturer, or local authorized representative of the manufacture, who sells, designs, oversees installation and provides technical support to the installer to commission the fire detection and alarm system.  The vendor also provides warranty services.

- WAC	Washington Administrative Code

  - CODES AND STANDARDS

- The Contractor shall perform all work in accordance with the requirements of the following codes and standards in effect as of the bid date of the Contract Documents, unless otherwise specified in this section to provide designs and installations in excess of the requirements.

- International Fire Code, including any AHJ administrative rules and amendments

- International Building Code, including any AHJ administrative rules and amendments

- NFPA 72 – National Fire Alarm and Signaling Code

- NFPA 70 – National Electrical Code

- WAC 296-46

- Department of Justice - ADA Standards for Accessible Design.

  - QUALITY ASSURANCE

- The vendor design shall be consistent with the basis-of-design as outlined in the Contract Documents.

- Fire alarm equipment shall consist of a system assembled as an approved unit of regularly manufactured components, by a single manufacturer for the purposes described in this Section.  The fire alarm equipment shall have a proven record of service and reliability in projects of similar scope to this project.  Interconnecting equipment that has not been listed for interconnection, or the creation of components or system into a nonstandard unit that is not normally available from the manufacturer, is not acceptable.

- All equipment shall be listed, cross-listed, and labeled by Underwriters’ Laboratories (UL) for fire detection and control.

- Installer and Vendor Qualifications:

- The fire detection and alarm system shall be installed by qualified electricians and mechanics, all of whom are properly trained and qualified in the installation, inspection and testing of fire alarm systems.

- All installation personnel shall have certification (FA-1) from the Seattle Fire Department in accordance with SFD Administrative Rule.

- The vendor shall have a proven record of being responsive, including providing accurate and complete submittals, meeting construction schedules, and being prepared for system testing and acceptance.

- The vendor must be able to provide the Owner any replacement part within 48 hours during the warranty period.

- The vendor shall be able to provide a fully equipped and qualified factory-trained repair technician at the job site within 4 hours of request for emergency services.

- This service shall be available 24 hours a day during the term of warranty.

- Evidence of qualifications or certification shall be provided when requested by the Owner.

  - FIRE ALARM SYSTEM DESCRIPTION

- Equipment and materials shall include the following:

- Intelligent (addressable/analog) fire alarm control panel(s)

- Equipment and circuits for the following:

- Alarm initiating devices

- Notification devices

- Fire alarm system monitored, controlled, and powered equipment

- Communication systems

- Interconnection of the above fire alarm system to the TrueSite System via the fiber junction box.

  - FIRE ALARM SYSTEM OPERATION DESCRIPTION

- Fire Alarm Signals:  Activation of a manual pull station, sprinkler water flow or an automatic sensing device for fire, temperature, flame, carbon monoxide or smoke (except for duct smoke detectors, local smoke sensors and local carbon monoxide sensors) shall result in the following:

- The audible alarm notification devices will continuously transmit a “slow whoop” tone until the fire alarm system is reset or the building microphone override is utilized.

- The visual alarm notification devices will flash until the fire alarm system is reset.

a.	Visual notification circuits shall be synchronized per circuit at each floor’s terminal cabinet.

3.	An alarm signal is transmitted to the TrueSite master stations.

4.	The appropriate campus network display unit (NDU) transmitter will operate and transmit to the central station monitoring company.

5.	A local buzzer in the FACP will sound.

6.	An externally visible amber LED indicator lamp in the FACP will illuminate.

____________________________________________________________________________________

Specifier – For R occupancies, add the following item 1.6A.7.

____________________________________________________________________________________

- Local smoke detector-sounder bases will activate.

- Auxiliary Control Functions:  During certain alarm conditions, as indicated herein, in the Contract Drawings or as indicated in approved Shop Drawings. , the fire alarm system shall  control doors, fans, dampers, elevators and similar types of equipment.  Direct control from detector output contacts is not permissible unless the contacts are fully programmable from the FACP.  Upon a fire alarm condition, the following auxiliary functions shall occur:

- Elevator recall is initiated.

- Shutdown or activate the following fans:

____________________________________________________________________________________

Specifier – For 1.6B.2a and 1.6B.2b, list the fans which require control by the project.

____________________________________________________________________________________

- Environmental fans:  The following general building fans shall shut down upon activation of any fire alarm device via direct control from the FACP.

(1)

(2)

- Dedicated fire safety fans:  The following shaft pressurization fans(s) and other dedicated fire safety fans shall start and be controlled directly from the FACP:

(1)

(2)

- Drop all magnetically-held fire doors following a 10-second time delay.

- All fire/smoke dampers close.

- Supervisory Signals:  Any equipment trouble/malfunction or activation of a sprinkler system supervisory switch (i.e., valve tamper, high/low air pressure) shall result in the following:

- A supervisory signal is transmitted to the TrueSite master stations.

- A local buzzer in the FACP will sound.

- An externally visible amber LED indicator lamp in the FACP will illuminate.

D.	System Trouble Signals:  Any malfunction or trouble condition of the fire alarm system shall result in the following:

- A trouble signal is transmitted to the TrueSite master stations.

- A local buzzer in the FACP will sound.

- An externally visible amber LED indicator lamp in the FACP will illuminate.

E.	Fire Alarm System Reset:

1.	Activation of the fire alarm system reset button shall result of the following:

a.	The fire alarm system shall return to a state of normal.

b.	The system shall automatically restore the signal to the controlled systems to normal operation.

(1)	If there are two or more fans of 20 horsepower (HP) or greater controlled directly from the FACP, the fans shall “stagger start” with an appropriate delay between each start.  The time delay and sequencing shall be incorporated into the ventilation controls or fan motors controllers via time-delay relays.  A 10-second delay between fan restart is recommended. (Not necessary for variable-frequency drive (VFD) controllers).

c.	The trouble signal shall not clear to ‘normal’ until all troubles have been cleared.

2.	Upon application or reapplication of 120 volt AC power, the fire alarm system shall automatically, without any operator intervention, initialize all circuitry and shall be in a normal operating condition.

a.	Systems which require operator intervention to reset manual controls following a 120 volt AC restoration are not acceptable.

____________________________________________________________________________________

Specifier – For projects with a refrigeration system, add the following item 1.6F.

_________________________________________________________________________________

F.	Refrigerant Leak Detection System:

- Fire alarm signal:  Activation of any refrigerant leak detector shall result in the following:

- Activation of the refrigerant audible and visual notification devices until the system is reset. (This shall not result in a building evacuation, but only notification within the refrigeration machinery room or area).

- The FACP will transmit an alarm signal to the TrueSite System with a text message “Refrigerant Leak”.

- The appropriate campus network display unit (NDU) transmitter will operate and transmit to the central station monitoring company.

- A local buzzer in the FACP will sound.

- An externally visible amber LED indicator lamp in the FACP will illuminate.

- Supervisory Trouble signal:  Activation of fan failure shall result in the following:

- Activation of the refrigeration audible and visual notification devices.

- The FACP shall transmit a supervisory signal to the TrueSite System with a text message “Refrigerant fan failure supervisory”.

- A local buzzer will sound in the FACP.

- An externally visible amber LED indictor lamp in the FACP will illuminate.

- System Trouble condition:  Activation of a system panel trouble shall result in the following:

- The FACP will transmit a trouble signal to the TrueSite System with a text message “Refrigerant leak panel trouble”.

- A local buzzer in the FACP will sound.

- An externally visible amber LED indictor lamp in the FACP will illuminate.

  - FIRE ALARM SYSTEM DESIGN CRITERIA

A.	Elevator Recall Functions:

1.	Provide elevator control relays for elevator primary recall, alternate recall, vent damper and flashing hat.

a.	Interposing relays shall be cross-listed with the FACP.

2.	Provide a relay and individual addressable module (IAM) to monitor the elevator shunt-trip power.

B.	Fan Shutdown:

1.	FACP control shall have priority over all other interlocks and controls.

2.	FACP shall shutdown individual fans via an interface relay on the direct digital controls (DDC) for heating, ventilation and air-conditioning (HVAC) systems.

3.	Provide on-off-auto manual override switches with priority over local hands-off-auto (HOA) switches, and other automatic control for all dedicated fire safety fans as identified above.

C.	 Fire Safety Fan Status:

1.	Provide contact point for positive feedback fan status at the FACP using a current sensor relay (specified in Division 23) located at the load side of the disconnect switch for all dedicated fire safety fans.

2.	Provide a relay on fan control power to indicate ready status.  It should be programmed as a supervisory condition.

3.	Provide a red light-emitting diode (LED) indicator lamp for run and a green LED for stop indication at FACP.

D.	Fire/smoke dampers shall close upon AC power failure.

E.	Supervision of fire alarm system components.  If any of the following conditions occur, the fire alarm system shall transmit a supervisory signal:

1.	Grounds, opens and shorts for the following:

a.	The 120 volt AC circuit(s) supplying the FACP.

b.	The TrueSite System circuit

c.	Alarm initiating circuits

d.	FACP auxiliary DC power

e.	Building signaling circuits

f.	Auxiliary control circuits (except the door circuits)

2.	Any equipment trouble/malfunction to the following fire alarm components shall result in the fire alarm system transmitting a supervisory signal:

a.	The FACP battery for high/low voltage and shorted cell.

b.	The FACP charging system.

F.	Annunciation and Manual Switches:

1.	In an addressable system, each initiating device shall annunciate at the FACP and remote annunciator (if provided), as a discrete point on an alphanumeric display.  In addition, the appropriate software zone LED shall illuminate at the FACP.

2.	Provide descriptive alphanumeric program labels for each system-initiating device in accordance with the following format:

a.	Floor-zone-device type-specific Information and or location (and special access notes) Include device type if not included in the standard manufacturer preprogrammed label.

b.	Examples:

(1)	4th FLR, C-Wing, in corridor by room 432

(2)	7th FLR, duct detector, SF-2, in Mechanical room 711

(3)	3rd FLR, Tower, in Stair number 2

3.	Upon a fire alarm condition, a red LED indictor lamp on the fire alarm panel shall illuminate. These LED indicator lamps shall operate continuously until the alarm is reset from the FACP. A red LED indicator lamp shall be provided for each of the following:

a.	General system alarm

b.	Water flow switch

c.	Water pressure switch

d.	Refrigeration leak detection panel

4.	The trouble buzzer shall be silenced by a silencing switch. However, the amber LED indictor lamp shall remain illuminated.

a.	Individual, fully supervised, “test and maintenance” switches with amber LED indictor lamps shall be provided for the following functions and be located inside the door of the FACP:

(1)	Prevent signal transmission to central station.

(2)	Bypass the alarm signaling devices (e.g., speakers, horns, strobes).

(3)	Intercept (i.e., block) fan controls, door controls, elevator controls, dampers and other circuits as specified.

(4)	Bypass activation of the electric water flow bell.

5.	Provide manual switches and status LED indicator lamps at the FACP for fans as described herein and shown on the Contract Drawings.

G.	Fire Alarm Circuits:

1.	Initiating circuits:  The FACP shall support interdependent addressable circuits, originating from FACP-mounted hardware, for each floor and zone.

2.	Notification circuits:

a.	The FACP shall support independent audio and visual alarm circuits for each floor and zone of the building.

(1)	Provide a circuit schedule that includes circuit load calculations and takes into consideration wire length, gauge, number of devices, and other requirements of this Section.

(2)	Do not use a single circuit for multiple floors or zones.

b.	Visual notification circuits shall be synchronized per circuit at each floor’s terminal cabinet.

c.	No speaker circuit shall exceed a -3 dB signal drop.

d.	Strobe circuit voltage drop at the end of the line shall not exceed four (4) volts.  Calculations shall use the UL maximum strobe current.

e.	The FACP shall support independent door and corridor damper control circuits originating from FACP mounted hardware for each floor zone of the building.

f.	Speakers near the FACP shall be installed on a separate circuit and programmed to deactivate if the building fire alarm microphone is used (to prevent feedback).

H.	Power Supplies:

1.	Provide a single 120 volt AC circuit to each FACP cabinet/can.

2.	Emergency power is not required for the door holders.  Doors shall close upon loss of building power.

3.	No power supply or electrical circuit shall be loaded greater than 80% of its rated capacity.

I.	Voice Communication System:

1.	Audio amplifiers shall be sized to provide 1/2 Watt minimum for each installed speaker..  Each audio amplifier shall have 35% minimum spare capacity when attached to the speakers necessary to meet audio requirements.

2.	FACP shall incorporate a spare automatic backup audio amplifier equal in size to the largest individual amplifier.

J.	Addressable Interface Module:  Provide addressable interface modules to interface with non-addressable initiating devices (i.e., water flow switches, tamper switches, beam detectors and kitchen suppression systems).

K.	Smoke/Fire Damper Interface Relays:  Interface relays shall be provided to operate 120 volt AC smoke dampers (provided by Division 23 00 00 “Heating, Ventilating, and Air Conditioning”) from the 24 volt DC fire alarm system.

- Fire alarm contacts shall be rated a minimum of 10 amperes.

- The interposing relay is to be normally closed and the damper(s) powered open.

- Interposing relays shall be UL cross-listed with the FACP.

- Multiple fire/smoke dampers in common areas/floor shall be controlled with a single interposing relay.

L.	Door Holders:  Power for door holders shall be 24 volt DC and originate from the FACP, but shall not transfer to battery power upon loss of 120 volt AC.

M.	Spares:

1.	Provide FACP spare equipment for 5% (at least two each) fully operational speaker, strobe, and auxiliary control circuits.

2.	Provide 20% spare capacity for FACP input/output (I/O) points and IDnet.

____________________________________________________________________________________

Specifier – Insert values in items 3 and 4.

____________________________________________________________________________________

3.	FACP auxiliary relays, minimum 3 amperes form “C” contacts –

4.	FACP control/bypass switches –

  - FIRE CONTROL COMMUNICATION SYSTEMS DESCRIPTION

- The fire alarm speaker system shall incorporate a “one way” fire commander’s voice communication or paging system.  A microphone shall be placed at the main control panel.

- A “two-way” fire fighter’s telephone system with phone jacks shall be installed where indicated on the Drawings.  A sounder shall activate at the FACP when a handset is plugged in at any field jack for the system.

  - SUBMITTALS

- Prepare and submit computer-aided design (CAD) Shop Drawings, battery calculations, product data, and other information required in this Section.

- Shop Drawings:

- The Contractor shall submit CAD Shop Drawings including, as a minimum, the following:

- Floor plans drawn to the same scale as the Contract Drawings, showing device layout, raceway routing, riser diagrams, conduit and wire size, wire identification numbers, and Owner’s room and floor identifier numbers.

- The drawings shall show all equipment locations and all wiring requirements utilizing the Owner’s wiring and cable requirements and the symbols as used on the fire alarm drawings.

- The Owner will provide a standard template of symbols, colors and layers and, when requested, one day of support and instruction in the Owner’s protocols.

- Raceway, conduit and riser diagrams showing FACP, terminal cabinets, raceway layout, circuit identification labels (wire labeling), riser conduit size, and all devices.

- Raceway size calculations showing the percent fill in accordance with the requirements of this Section.

- Typical point-to-point wiring diagrams of control panels including, but not limited to, all: control and annunciator panel components, field devices, relays, fans showing manual override and fire safety fan status wiring diagrams, elevators, and other auxiliary control(s), and terminal cabinets showing all installed wiring (not factory wiring harnesses) and wiring connections.

- Label all components and identify circuits using the Owner’s wire labeling format described in this Section.

- All variances from typical shall be illustrated in separate diagrams.

- Wire/circuit legend with information such as circuit identification, color, gauge, wire type, and number of conductors.

- Circuit schedules for speakers, strobes and auxiliary controls.

- Schedule of addressable circuits and corresponding circuit lengths.

- Detailed mounting installation diagrams of the control panel(s), remote annunciator(s) and batteries.

- Front elevation of the control panel(s) and all annunciator panels.

- Detailed labels and labeling schematics for FACP circuits and field devices.

- Nameplates and messages on the control panel(s) and annunciators shall be shown in actual size.

- Functional response matrix identifying all system responses.

- Battery calculations, speaker and strobe circuit voltage drop and power consumption.

- List the number of 120 volt AC power circuits required for the fire alarm equipment.

- The Contractor shall provide product data sheets identifying all FACP equipment with model number and power consumption calculations.

B.	Submit Shop Drawings, battery calculations, product data, and other information required in this Section to the Owner for Owner approval.

C.	Upon receipt of the Owner’s approval, the Contractor shall submit the Shop Drawings to AHJ for their approval.

D.	After receipt of AHJ’s approval, the Contractor shall re-submit a copy of the Owner-approved shop drawings with the AHJ approval stamp on them and/or accompanying letter.  Partial submittals are unacceptable.

E.	Within forty five (45) days after Owner’s approval of the shop drawings, submit the following for review and approval:

- A written functional performance test (FPT) procedure, in accordance with this Section.

- A complete fire alarm device points list, prepared in Microsoft Excel using 81/2” x 11” or larger sheets, for all circuits identifying the following:

- Device address (initiating only)

- Manufacturer fixed labels (device type)

- Custom labels (conforming to Owner’s wire label format)

- Zone label (if used)

- The list shall also include signaling and all other auxiliary circuits.

F.	Project Record:

- The Contractor shall submit the following for Substantial Completion:

a.	CAD as-built Shop Drawings

b.	A letter certifying that the fire detection and alarm system is completely functional and conforms to all applicable codes, ordinances, and requirements of the Contract.

c.	Final installation permit from the AHJ. (i.e., Seattle Fire Department Field Inspector’s File Notes).

d.	Copy of the completed FPT document.

- The Contractor shall submit the following documents for Final Completion:

  - Fire Detection and Alarm O&M information, included in the O&M Manual specified in Section 01 77 00 “Closeout Procedures.”  Include:

      - Final product data

      - Manufacturer wiring diagrams of all FACP components

PART 2 – PRODUCTS

  - MANUFACTURER

- The fire detector and alarm equipment shall consist of a system assembled as an approved unit of regularly manufactured components, by a single manufacturer for the purposes described in this Section.  Interconnecting equipment that has not been listed for interconnection, or the creation of components or system into a nonstandard unit that is not normally available from the manufacturer, is not acceptable.

- All equipment shall be listed, cross-listed, and labeled by Underwriters’ Laboratories (UL.

____________________________________________________________________________________

Specifier – Projects at the UW Tower employ alternate manufacturers.  For item C, consult with UW EH&S Fire Protection Engineer.

____________________________________________________________________________________

- Subject to the requirements of this Section, fire detection and alarm system shall be manufactured by Simplex®.  No substitutions.

  - LOCKS

- Locks for cabinets, enclosures, and manual pull stations shall be keyed for Corbin CAT #30. No substitutions.

  - FIRE ALARM CONROL PANELS

- The FACP shall be microprocessor-operated, power limited, modular in design and equipped with a nonvolatile memory that requires no battery backup; Simplex 4100ES, no substitutions.

- A single FACP shall be able to utilize, in combination, addressable, analog, and 2/4 wire NO/NC detectors.  (Plug-in “mix and match” modules or similar architecture are acceptable.)

- FACP Software:

- Owner’s personnel shall be able to create and modify control software with an IBM-compatible PC using MS-DOS based or MS-Windows based, menu-driven, user-friendly programming.

- Owner’s personnel shall be able to store the programming on a removable computer disk and pre-program a nonvolatile, transportable memory storage device which can be used for replacement in a FACP as the programming backup.

- All software, including proprietary software, shall be provided to the Owner as necessary to meet the requirements of this section.

- The FACP shall incorporate power supplies and all controls for systems except as described elsewhere within this Section.

- Mount all components within a steel enclosure with locked door(s).

- Door(s) shall incorporate a transparent window for viewing indicator lamps, and other pertinent components.

- Provide additional cabinets, if required for a complete installation.

- Transponders and other ancillary control panels may only be used where shown on Drawings, unless otherwise approved by the Owner.

- Power Supplies:

- The FACP 24-volt DC power supply shall be powered by 120-volt AC power, with a battery backup system regardless of the building’s primary or alternate source of power.  The system shall also include the following requirements:

- Sealed gelled cell-type batteries.

- 24-hour system backup capability plus 15 minutes (for emergency voice/alarm communications service) of full alarm operation at the end of the 24-hour period.

- Charger shall be able to restore batteries to full charge within 48 hours after a complete discharge.

- Provide a separate means of disconnecting all 120 volt AC circuits for the FACP, NAC panel(s) or other fire alarm panels.

- The means of disconnecting power shall be lockable.

- For light-switch type disconnect switches, a Brady 65392 wall switch lockout plate or approved equal shall be used.

- Power supplies must be capable of powering all circuits simultaneously (e.g., door holder power at the same time notification circuits are active.)

- Other FACP Features

- Walk test:  A test mode that causes the system’s signal to sound, and a report to be printed, when a device is activated, or a trouble or supervisory condition identified, followed by a prompt automatic reset of the FACP.

- The signal sounding shall be capable of being turned off independent of the printing function.

- This feature shall be available for system acceptance testing/commissioning.

- Alarm verification:  An activated smoke detector shall automatically reset and then recheck the atmosphere following a 60-second wait period.

- The fire alarm system shall not activate until detection is confirmed following the wait period.

- Activation of a second detector during the waiting period shall activate the alarm system immediately.

- History log:  Log a history of alarm and trouble events for the system.

- Other FACP components shall include the following:

- Fiber modems for connecting to the TrueSite System.

- Alarm and trouble LED indicator lamps located on the FACP to be visible with the door closed.

- Trouble buzzer with silencing switch inside locked cabinet.

- Control and time delay relays as required.

- Supervised switches (one for each listed function) installed to allow a  complete test of the system without evacuating the building, recalling elevators, releasing doors and/or posturing for smoke control (i.e., bypass switches).

- Supervised control switches or relays for use in interfacing with other devices as required.

- Permanent printed labels for all interactive equipment, zones, switches, controls, and instruction.

  - MANUAL PULL STATIONS

- Manual pull stations shall be addressable Simplex 4099-9001 single action, or approved equal.

- Reset shall be accomplished with a lock and Corbin CAT #30 key. No substitutions.

- The station housing shall be fire red factory finish.

- Exposed back boxes shall be provided by the manual pull station manufacturer and be designed specifically for the application.

____________________________________________________________________________________

Specifier – For projects with R occupancy, add 2.6 A.4.

____________________________________________________________________________________

- Provide STI stopper pull station cover with horn; model STI-1100 or approved equal.

  - SMOKE DETECTORS/SENSORS

- Smoke Detectors (ceiling and/or area-type):

- Detectors shall be photoelectric addressable analog with separate base.

- The detectors, complete with terminating equipment, shall be fully supervised and shall not activate alarm due to rapid changes in humidity or a fan maintenance shutdown.

- The detector shall be equipped with LED alarm condition indicator lamp.

- When exposed back boxes are needed, use round surface mounted raceway (wire molding) boxes of the appropriate size.

- The detector shall have an alarm verification function.

- Manufacturer of smoke detectors shall be Simplex; no substitutions.

- Duct Detectors:

- Detectors shall be addressable analog photoelectric with remote indicator lamp and remote test switch.

- The devices shall include necessary sampling tube extensions.

- Heat sensor feature is not required.

- The device shall function uniformly in air velocities of 500 fpm through 3000 fpm.

- The detector shall have an alarm verification function.

- Manufacturer of duct type smoke detectors shall be Simplex; no substitutions.

- Beam Detectors:

- Detectors shall be four (4) wire conventional, single-ended reflected beam type.  The system shall include a test station and remote reset switch.

- A transmitter and receiver within the detector unit shall have an integral sensitivity test feature which satisfies the maintenance and test requirements of NFPA 72 without the use of external test filter screens.  It shall allow for beam alignment between the detector and the reflector to be done at the detector, be capable of automatically adjusting its sensitivity and be capable of being reset from the fire alarm control panel.

- The detector shall be equipped with LED alarm condition indicator lamp.

_____________________________________________________________________________

Specifier – For projects with R occupancy, add 2.7 D, E and/or F.

____________________________________________________________________________________

D.	Local-only Smoke/Carbon Monoxide (CO) Detectors (ceiling type located in apartment units):

1.	Detectors shall be photoelectric addressable analog with separate base.

2.	The detectors, complete with terminating equipment, shall be fully supervised and shall not activate alarm due to rapid changes in humidity or a fan maintenance shutdown.

3.	The detector shall be equipped with LED alarm condition indicator lamp.

4.	The base shall contain a sensor to monitor CO levels and initiate if CO levels are exceeded.

5.	The base shall contain an audible alert (sounder).

6.	If multiple bases serve an area or apartment, all devices within the area or apartment shall synchronize and activate upon initiation of any one detector.

7.  	 The detector shall have an alarm verification function.

8.	Device shall be Simplex 4098-9798 CO monitor base and sounder with 4098-9714 photoelectric smoke sensor; no substitutions.

E.	Local-only Smoke Detectors (ceiling type located in or near sleeping units in residence halls):

1.	Detectors shall be photoelectric addressable analog with separate base.

2. 	The detectors, complete with terminating equipment, shall be fully supervised and shall 	not activate alarm due to rapid changes in humidity, or a fan maintenance shutdown, 	etc.

3.	The detector shall be equipped with LED alarm condition indicator lamp.

4.	The base shall contain an audible alert (sounder).

5.	If multiple bases serve an area or apartment, all devices within the area or apartment 	shall synchronize and activate upon initiation of any one detector.

6.	The detector shall have an alarm verification function.

- Device shall be Simplex 4098-9794 base and sounder with 4098-9714 photoelectric 	smoke sensor; no substitutions.

F. 	Common Area Combination Smoke / CO Sensors:

- Detectors shall be provided as shown on Contract Drawings.

- Devices shall be Simplex 4098-9797 CO base with 4098-9714 smoke sensor, no substitutions.

  - HEAT DETECTORS

- Heat detectors shall be combination of fixed temperature and rate-of-rise low profile addressable analog type and shall be “ordinary” temperature range in all areas except where located in a high ambient temperature area.

- In areas subject to temperature in excess of 140 degrees F, detectors shall be listed for such use.

- An indicator on the exposed surface of the detector shall display the actuated condition of the detector.

  - COMBINATION AUDIBLE/VISUAL DEVICES

A.	Combination speaker/strobe devices shall be white, metal grill, with multiple wattage taps including 1/4, 1/2, 1 watt, and 2 watts at 25 volts, and selectable candela taps including 15/30/75/110cd. All strobe covers shall be blank and not contain the word “FIRE”.

1.	Indoor wall mounted speaker/strobes shall be Wheelock E70-24 MCW-NW, or approved equal.

2.	Indoor ceiling mounted speaker/strobes shall be Wheelock E90-24MCC-NW, or approved equal.

B.	Outdoor and environmental rooms with high humidity and controlled temperature, including coolers and freezers, use Wheelock ET70WP-2475W-NW speaker with Wheelock 10B-W back box, or approved equal.

  - AUDIBLE ALARM DEVICES   (SPEAKERS, HORNS)

____________________________________________________________________________________

Specifier – The audible/visual devices are indicated “white” in color.  If another color is desired, please correct Wheelock model numbers.

____________________________________________________________________________________

- Speakers shall be white, have a sealed back and metal grill. All covers shall be blank and not contain the word “FIRE”.

- Speakers shall be flush mounted.

- Where necessary, surface mounting white Wheelock SBB-W, or approved equal box shall be used.

- For flush mounting use a 4S deep j-box with an extension ring or the 5S j-box by Randl Industries, or approved equal.  (Note:  5S box allows installations in walls not deep enough to accommodate the 4S box and extension ring).

C.	For horn-only fire alarm systems provide separate circuits for horns and strobe devices use:

- Indoor Horn/Strobe:  Wheelock MT-24MCW-NW, or approved equal.

- Outdoor and environmental rooms use:

- Horn:  Wheelock MT-12/24-W, or approved equal.

- Horn/Strobe:  Wheelock MTWP-2475W-NW with Wheelock IOB-W back box, or approved equal.

D.	Refrigerant audible devices shall be a Wheelock MTWP-24MCCH-NW with Wheelock IOB-W back box, or approved equal.

  - VISUAL ALARM DEVICES (STROBES)

- Visual alarm devices shall operate at 24 volts DC and be equipped with a Xenon strobe light which meets requirements outlined in this Section.

- For wall-mounted devices use Wheelock series RSS-24MCW-NW, or approved equal.

- For ceiling-mounted devices use Wheelock series RSS-24MCC-NW, or approved equal.

- For outdoor installations and controlled temperature environmental rooms use Wheelock RSSWP-2475W-NW weatherproof strobe with Wheelock WPSBB-W weatherproof back box, or approved equal.

- Flashers shall be combined into one unit with speakers (or horns) where appropriate.

____________________________________________________________________________________

Specifier – For projects with R occupancy, add 2.10 A.5.

____________________________________________________________________________________

- For residential rooms requiring a ceiling mounted visual alarm device (177cd rating), use Wheelock RSS-24MCCH-NW, or approved equal.

- A Wheelock DSM-12/24 synchronization module, or approved equal, shall be used to synchronize strobe circuits.

- Refrigerant visual alarm devices shall meet the above requirements.  In addition, the device shall be equipped with a “blue” Xenon lens.

  - DOOR HOLDERS

A.	Provide Simplex series 2088 wall mount and floor mount door holders, or approved equal.  Where it is physically impractical to use the Simplex series 2088 style door holders, LCN series 4040SE or 4040SEL door closures may be used with approval by Owner.  Coordinate with Section 08 70 00 “Hardware.”

  - FIRE SPRINKLER SYSTEM – ELECTRIC BELL

A.	The electric bell shall be a Potter Electric MBA 2410, Wheelock MB-G10-24-R, or approved equal.

  - FIRE ALARM TERMINAL CABINETS AND AUXILIARY CABINETS

- Enclosures shall be NEMA Type 1 or Type 12.  Minimum size is 12x12x6 inches.  Size to provide 40% spare capacity.  Locks shall be keyed Corbin CAT 30.  Box and front shall be steel and painted to match wall in finished areas.  Manufacturers:  Hoffman, or approved equal.

- Fire alarm terminal cabinet shall be labeled with a riveted or screwed laminated plastic nameplate indicating “FIRE ALARM TERMINAL CABINET” in 1/4 inch white letters on a red background.

- These blocks shall be sized to accommodate wire from 19 gauge to 10 gauge.  Terminal blocks are to be Allen Bradley 1492-W6 or W10 or Entrelec M4/6, or approved equal, with associated partitions, barriers, stops, and rail.

  - REMOTE ANNUNCIATOR

- Provide an alphanumeric type remote annunciator with 80 character LCD display, and system acknowledgement switch(s).  Manufacturer: Simplex 4603-9101 LCD, no substitution.

- Do not provide zone LED indicator lamps.

PART 3 – EXECUTION

3.1	GENERAL

- No materials shall be provided at the job-site until the Shop Drawings have been approved by the Owner and AHJ.

- While the system installation is in progress, one set of approved Shop Drawings will be kept at the job site and will be updated regularly to reflect current as-built information. The Owner shall be given access to this set to review as necessary.

  - INTERFACE WITH EXISTING FIRE ALARM SYSTEM

A.	The existing fire alarm system shall not be disabled at any time.

  - FIRE WATCH AND FIRE PROTECTION SYSTEM SHUTDOWNS

- When it is necessary to shut down existing fire alarm systems for switch-over purposes or any other reason that leaves the building unprotected, the Contractor shall provide a continuous approved fire watch in accordance with Section 01 35 23 “Owners Safety Requirements” and all AHJ requirements.

- Submit a Utility Shutdown Request form in accordance with Section 01 50 00 “Temporary Facilities and Controls” when requesting approval for fire protection shutdown or functional impairment.

  - MOUNTING POSITIONS

- Locate all fire detection and alarm devices as required by AHJ.

- Mount FACP(s) as indicated on the Contract Drawings.

- Provide one 120 volt AC duplex electrical receptacle on the same wall and within 5 feet horizontally of the fire alarm CPU cabinet, no more than 6 ft above finish floor (AFF). The receptacle shall not be powered by either emergency power or the same circuits supplying the fire alarm system.

- Remote Annunciator Panel:  Location shall be as shown on the Drawings or installed 5 ft AFF, if not indicated.

- Battery Cabinet:  The height of the 110 volt ampere hour battery charger/cabinet shall be no more than 29 inches AFF to the top.  Nothing shall be mounted above the battery charger/cabinet and in the space extending up 30 inches above the top.

- Fire Alarm Terminal Cabinets and Auxiliary Cabinets:

- All cabinets shall be surface, or flush mounted (as shown on the Contract Drawings) with hinged door and latch with lock.

- Provide a wiring scheme similar to that specified herein inside of the cabinet door.

- Provide a schedule identifying all end-of-line resistors for the zone and their respective locations.

- Install terminal blocks in all terminal cabinets and auxiliary control cabinets.

- Install backboards in the terminal cabinets that are fire retardant treated 3/4 inch exterior grade plywood, painted white.

- Smoke Detectors/Sensors:

1.	Beam detectors:

(a)	Locate beam detectors at least 10 feet above walking surfaces.

(b)	Locate the test station below the transmitter on a wall 5 feet AFF on the floor nearest the transmitter.

2.	Duct detectors:

(a)	Install remote indicating lamp and test switches as indicated on the Drawings The remote indicating lamps should be readily visible and within 7 ft AFF.

(b)	In finished spaces, mount remote indicator lamps and remote test switch in close proximity to the duct smoke detector.

(1)	Remote indicating lamps maybe located in the ceilings or walls adjacent to detectors.

(2)	Remote test key switch shall be labeled with the address and description of the duct detector.

- All end-of-line devices shall be located in the terminal cabinet or at the end of the corridor for the zone it serves.

- Audible Alarm Devices (Speakers, Horns):

- Install all speakers at the 1/2-watt setting unless indicated otherwise on the Drawings.  Speakers located in rest rooms and similar enclosed areas where an alarm threshold maybe high should be tapped at 1/4-watt.

- The speaker cable shield or drain wire shall remain intact and be spliced through all terminal cabinets, junction boxes and speakers.

- Speakers shall be flush mounted unless specified otherwise on the Drawings.

- For outdoor audible alarm devices, install a weatherproof back box with weep hole oriented down, and seal conduit penetration.

- Set horns for “slow whoop” tone.

- Visual Alarm Devices (Strobes):  All strobe circuit(s) synchronization module(s) shall located in the terminal cabinet.

- Addressable Interface Modules:  Addressable modules such as individual addressable modules (IAMs) and isolator modules shall be installed in the appropriate boxes as shown in the manufacturer’s installation instructions.  The manufacturer’s mounting brackets (if applicable) and covers with light pipe status windows shall be used.

- Power Supplies:

1.	The means of disconnecting each 120 volt AC circuit (to the FACP, NAC or other fire alarm panels system) shall be installed within 10 feet of each panel and shall be lockable.

2.	The Owner will provide locks for the Brady wall switch lockout plate covers for the Contractor to install.

L.	Smoke/Fire Damper Interface Relays:  Mount in the proximity of the terminal cabinet.

  - MOUNTING METHODS

- Conduit, panels, devices and boxes shall be secured by means of expansion shields in concrete, machine screws on metal surfaces, and wood screws on wood construction.  Attachment with devices driven in by power charge or nail type nylon anchors are not acceptable in lieu of machine screws.

- Initiating Circuit:  No initiating circuit shall exceed 4000 feet in length.

- Audible Alarm Devices (Speakers, Horns):

- An open circuit in any speaker or horn coil shall not prevent the rest of the audio devices connected to that circuit from operating.

- If a short circuit occurs, the faulted circuit shall not prevent any other circuit from operating, and trouble shall be indicated.

- If the shorted circuit clears, signaling operation shall be automatically restored.

- The drain wire shall not be grounded or terminated except at the main FACP.

- Wherever the drain wire is exposed, it shall be wrapped with UL approved electrical tape, in order to avoid shorts or grounds.

- Audible alarm devices shall be flush mounted.

a.	Where necessary, surface mounting white Wheelock SBB-W, or approved equal, box shall be used.

b.	For flush mounting use a 4S deep j-box with an extension ring or the 5S j-box by Randl Industries, or approved equal.  (Note:  5S box allows installations in walls not deep enough to accommodate the 4S box and extension ring.)

- Outdoor audible alarm devices:  Provide weatherproof back box with weep hole oriented down, and seal conduit penetration

  - AUXILIARY CONTROLS

- Provide all wire ways, wiring, control modules, interposing relays, terminal boxes, and relay cabinets for FACP controlled equipment such as fans, dampers, doors, and elevators.

- Each type of equipment shall be controlled by dedicated double throw relays.

- Field control modules must be used for addressable systems.

  - ELEVATOR CAR EQUIPMENT AND TRAVELING CABLE

- Traveling cable is furnished and installed by Division 14 20 00 “Elevators.”  Coordinate circuit requirements and connections.

3.8	RACEWAY AND WIRING SYSTEM

A.	The manufacturer’s recommendations shall only be used as a minimum requirement.

B.	Raceway:

1.	Pre-wire installation inspection:  The Contractor shall coordinate with the Owner to inspect the raceway installation prior to pulling wire.

2.	No raceway shall be filled in excess of 40%.  The Contractor shall demonstrate by performing fill calculations showing that the designs comply with the following criteria.

a.	The raceway system shall resemble a branch and tree configuration.  Branches shall be provided with sufficient junction boxes so that not more than three unassociated circuits pass through a device back box.  Follow manufacturer’s instruction for wires in device back boxes (e.g., Wheelock does not allow use through the back box, except for the signaling appliance).

b.	All raceways shall run parallel or perpendicular to walls, floors, and ceilings.

c.	For surface mounted raceway, runs shall be routed on walls out of visual sight, with vertical drops to wall-mounted devices.

d.	Submit routing layout drawings for approval prior to installation.

e.	Do not encase raceway in concrete, unless specifically indicated in the Contract Documents.

f.	Exceptions are only allowed when use of existing raceways is shown on the Contract Drawings or approved by the Owner.

3. 	All wiring shall be contained in EMT (electrical metallic tubing) conduit or raceways dedicated to fire alarm service.

a.	Metal clad (MC) cable is allowed where use of EMT conduit is not feasible in difficult retrofit applications with specific approval of the Owner.  The cable must also be approved by the fire alarm system manufacturer.

4.	Conduit minimum size shall be ¾ inch, unless approved by Owner.

5.	Surface mounded raceway shall be equal to Wiremold 700 series minimum.

6.	All conduit and raceways shall be color-coded by a ¾ inch red tape band at 10 foot intervals.  Use Scotch® Brand 35 vinyl electrical color coding tape, or approved equal.

7.	Paint all junction box covers for the fire alarm system “red.”  Paint J-Box covers in finished areas to match the wall or ceiling and put a ½ inch minimum red dot on the cover.

8.	For exterior devices and devices installed in lower than normal temperature environments (i.e., refrigerators, freezers, etc), the device back-box holes and conduit (on both sides of the wall penetration) shall be sealed per NPFA 70.

C.	Wiring:

1.	Aluminum wire and stranded wire are not allowed.

2.	All wiring shall be UL approved and marked, and brought to the job-site in original packages.

3.	All solid wire terminations shall be made bare to screw terminals specifically designed for bare wire connection.  Make cable shield terminations with Thomas & Bretts “Sta-Kon”, or approved equal, self-insulated spade lugs were connected to screw type terminals.

4.	Interposing relays shall be used for all switched power loads and shall be located such that the switched power conductors do not run in the same raceway as the interposing relay coil power or any other energy-limited low voltage conductors.

5.	Do not run power limited wiring in the same wire-ways with, or closely parallel to, high voltage and/or switched power wiring.

6.	Wire that has scrapes, nicks, gouges, or crushed insulation shall not be used and must be removed.

7.	Wire insulation shall be one of the types required by NEC.  All wires shall be sized per NEC for the load serviced.  Field wiring for initiation, supervision and signal circuits shall be solid conductor.  All wire shall be approved for fire alarm installations.

8.	“Pig tailing” and “Tee tapping” is prohibited for all system circuits, except door circuits and addressable signaling line circuits.

a.	Addressable signaling line circuits may be Tee shaped only in the terminal can for the floor which that circuit serves.

9.	Fire alarm system shall be wired “Class B”, device-to-device, with no splicing unless approved by the Owner.

10.	End of line resistors shall be located in the terminal cabinet, the end of the corridor or other unassigned (public) space for the zone served.

11.	Splicing shall be made with Minnesota Mining & Manufacturing Co., Ideal Industries, or Thomas & Betts wire connectors, or approved equal.

a.	Minnesota Mining & Manufacturing Co. “Scotchloc™” model spring wire connectors are not approved.

12.	Colors shall match when possible and the conductors shall be mechanically secured to each other so that no stress is applied to the splice.

13.	Wire pulls by powered mechanical means are not permitted.

a.	Conduit shall be thoroughly cleaned of all foreign material just prior to pulling the wire or cable.

b.	Lubricants shall be compounds specifically prepared for cable pulling and shall not contain petroleum or other products which will affect cable insulation.

14.	No wire run or circuit shall be longer than 80% of the maximum allowable length and power consumption for the wire size and application.  No output circuit shall exceed 80% of the maximum load capacity specified by the manufacturer.

15.	Terminate all wiring for each zone or floor in a terminal cabinet as indicated in the Contract Documents prior to running the wires to the fire alarm panel.  Provide at least one terminal cabinet for each floor.

16.	Wiring in all cabinets and terminal boxes shall be neatly arranged and bundled with tie wraps, or equivalent.

17.	All inductive loads, such as door holders and interface relays, without integral reverse electromagnetic field (EMF) suppression must have suppression on those circuits.

18.	Wiring for all exterior devices and devices installed in lower than normal temperature environments (i.e., refrigerators, freezers, etc) shall be rated for its environmental conditions.

D.	The following wire shall be used unless an alternate is approved by the Owner.  Color-coding shall be by the wiring insulation.  Single conductor wires shall be solid.

TABLE 3.7 D - Wire and Cable Requirements

Circuit Type		Quantity/Color			Size		Section			ID

Addressable			West Penn D975, or		#18		0.0450 sq.in.			L

circuit	(See Note 1)	Belden 5320FJ			#18		0.035 sq.in.

24 VDC			1 pink (pos.)	THHN			#14		0.0174 sq.in. 		P

1 grey (neg)THHN

Remote			1 pair TFN				#16		0.0158 sq.in.			R

Indicator Light		(2 pink)

Monitor Switch		1 pair TFN				#16		0.0158 sq.in.			T

(tamper, flow		(2 brown)

& pressure)

Audio Alarm	(speakers)	Belden 5220FL 			#16		0.0249 sq. in.		A		(See Notes 1 & 2)		Belden 5120FL			#14		0.037  sq. in.

Visual Alarm	(strobes)	1 pair THHN				#14		0.0174 sq.in.			V

(See Note 3)		1 brown (negative)

1 blue (positive)

Door Holder &		1 black (negative),			#14		0.0174 sq.in.			D

Door Lock			1 red (positive) THNN

Smoke Control		1 pair THHN    			#14		0.0174 sq.in.			Z

Damper			(blue)

Fan Control			2 orange THHN 			#14		0.0174 sq.in.			H

(simple shutdown)

Fan Control			5 orange THHN			#14		0.0435 sq. in.		Q

(shutdown, overide,	(3 orange, control)

and status)			(2 orange, status)

Elevator functions		7 yellow THHN			#14		0.0348 sq.in.			E

Panel Ground		1 green THHN			#10		0.0184 sq.in.			-

Bell				2 violet, THHN			#14		0.0174			B

Note 1: 	Cable must conform to FACP system manufacturer's requirements.

Note 2:	Contractor's option, 14 or 16 gauge (see Part II - FACP).  This is a two conductor shielded cable.  The same size cable shall be used for the entire system.

Note 3:	(see Part 2 – products herein).  All circuits shall be 14 gauge; twelve-gauge wire is not allowed.  Provide multiple circuits for a single zone as required.

E.	Wire labeling:  All circuits and conduits shall be identified in accordance with Table 3.7C, with labels to include circuit type, zone, floor and wing (if applicable).  Labels must be provided at the FACP, terminal cabinets, and all junction boxes with more than 5 circuits.  Labels shall be produced using an electronic labeler utilizing a 10 point font size.

Table 3.7E - Wire Labeling

- Format:         X - XX - XX – XX

ID - Z - F - W

2.	Example:      V   12   6    J

Circuit (ID) = 	Per Wire Table (i.e., V for Visual)

Zone (Z)    = 	1, 2, 3,,,,,,,,,,,,,,,,,,,, 23, 24

Floor (F)    = 	M1, 01, 02,,,,,,,, 10, 11

Wing (W)   = 	A, B, C,,,,,,,,,, NN, EA, SW

- All initiating and signaling circuit devices shall be externally labeled with a printed adhesive label approximately ½” x 1” in size.  Identify the circuit and zone, consistent with wire labeling scheme, using a 12 to 14 point font, black ink on white.

  - SIGNAGE

- Refrigeration System:  Provide all refrigerant audible and visual devices with signs.  Signs shall be three layer etched plastic with white letters on a blue background.  Letters are to be ½ inch high minimum.  Signs should read “REFRIGERANT SYSTEM.”  The signs are to be permanently hung below the device(s).

  - SUBSTANTIAL COMPLETION REQUIREMENTS

- Commissioning and Training:  The fire detection and alarm system shall be commissioned and Owner training shall be provided per the requirements of Section 01 91 00 “General Commissioning Requirements.”

- Functional Performance Testing (FPT):  The completed system shall be subjected to two (2) required tests.

- The first FPT shall be conducted by the Contractor and witnessed by the Owner and A/E.

- This test shall start after the system is complete and clear of troubles.

- Should the results not be satisfactory to the Owner, then corrections will be made and a re-test will be required at the Contractors sole expense.  The installer and a factory trained technician for the FACP shall be present for all testing.

- The first FPT shall be in accordance with the Owner approved FPT procedure to demonstrate and certify proper system operation.

- As a minimum, the FPT shall provide a detailed method of testing and documenting the system to demonstrate that that system functions as intended by the design.

- The FPT procedure data forms shall document the following, as a minimum:

- All detectors shall be removed from their base and checked for trouble.  Remove one device per addressable circuit from its box and lift a wire to test the supervision and ground.  Failure due to improper system wiring will require a comprehensive test of the circuit.

- Remove one device per signaling circuit from its box and lift a wire to test for supervision and ground.  Failure due to improper system wiring will require a comprehensive test of the circuit.

- All bypass and control switches shall be operated to indicate proper supervision of the switch

- All valve and sprinkler supervision switches shall be operated to verify proper response.

- All valve and sprinkler supervision switches shall have one wire removed to verify proper supervision.

- Each alarm output, detection or supervision zone AUG be tested for proper response to ground conditions.

- Test the TrueSite System for proper operation.

- AC power shall be interrupted for 24 hours and followed by a 15 minute alarm test (for voice systems).

- Remove all critical fuses to check for proper supervision.

- Test the firemen’s telephone system for supervision of the wiring and for quality of voice transmission.

- Test all detectors for alarm operation.

- Test all signaling devices fro proper operation.  Devices that fail and are replaced will require a retest.

- Test all alarm sounding devices for proper operation.

- All elevator, fan, door holder, damper and other control functions and circuits shall be tested for proper operation.

- Test for proper operation of the Public Address portion of the FACP.

- Test fan and damper control, including manual override and priorities.  Coordinate with other trades.

- Test magnetic door closures/holders and locking mechanisms.  Verify appropriate priority with security and access control systems.

- Test elevator recall, (primary and alternate), vent damper and flashing hat.

- Test transfer to emergency power, where provided.

- Test alarm verification function.  Confirm no delay occurs if two detectors are activated.

- Confirm analog sensor adjustable sensitivity function is operable and properly set.

- Demonstrate history log and print port functions.

- Confirm FPT with system response matrix.

- Confirm all conduit penetrations to exterior or cold rooms are sealed on both sides per NFPA 70.

- Audibility tests shall be conducted by the Contractor to determine compliance with the requirements.  For replacement systems in occupied buildings, the audibility test shall be conducted after normal working hours.

- Smoke Sensor Sensitivity Report:  Following completion of the preliminary test, the Contractor shall place the FACP on-line with outputs bypassed for a period of 10 days.

- A report of all system smoke sensors with sensor high and low readings and recommendations for alarm threshold settings, and device relocation if necessary, shall then be submitted to the Owner.

- Smoke detectors with a reading of 95 and higher are considered dirty and will be required to be cleaned or replaced for Substantial Completion of the system.

- The Contractor shall then adjust detector sensitivity as required by the Owner.

- After satisfactory completion of the first FPT test, the Owner will provide direction for the Contractor to schedule the second FPT test for the AHJ final acceptance test. The Contractor shall execute the AHJ final acceptance test as a condition of Substantial Completion.

- Approval of the AHJ shall be evidenced in writing and a copy forwarded to the Owner.

- The requirements for final testing shall be as requested by AHJ at the final test.

END OF SECTION