BACnet Protocol Implementation Conformance Statement

Date: 07-11-2011

Vendor Name:  Lennox Industries, Inc.

Product Name:  Prodigy Rooftop Unit Controller

Product Model Number: M2

Firmware Revision: 1.00h

Applications Software Version: 7.08.xx

BACnet Protocol Revision: 7

Product Description:

HVAC controller designed to control Lennox commercial rooftop units.

BACnet Standardized Devices Profile (Annex L):

BACnet Application Specific Controller (B_ASC)

List all BACnet Interoperability Building Blocks supported (see Annex K in BACnet 2008):

Data Sharing: 			DS-RP-B, DS-RPM-B, DS-WP-B

Device Management: 	DM-DDB-B, DM-DOB-B, DM-DCC-B, DM-RD-B

Which of the following device binding methods does the product support?  (check one or more)

( Send Who-Is, receive I-Am (BIBB DM-DDB-A)

( Receive Who-Is, send I-Am (BIBB DM-DDB-B)

( Send Who-Has, receive I-Have (BIBB DM-DOB-A)

( Receive Who-Has, send I-Have (BIBB DM-DOB-B)

( Manual configuration of recipient device's network number and MAC address

( None of the above

Standard Object Types Supported:

Device

Analog Input

Analog Output

Analog Value

Dynamically Creatable Objects: 	None

Dynamically Deletable Objects: 	None

Proprietary Properties: 				None

Device Object:

Optional Properties Supported:	Location

Description

Optional Writable Properties:		Object_Identifier

Object_Name

Max_Master

Max_Info_Frames

Location

Description

Property Range Restrictions:		Object_Identifier: 0 – 4194302

Object_Name: max. 32 characters

Max_Master: 1 – 127

Max_Info_Frames: 1 – 65535

Location: max. 32 characters

Description: max. 32 characters

Analog Input Objects:

Optional Properties Supported:	None

Optional Writable Properties:		Out_Of_Service (AI239 – AI252, AI274 – AI285 only)

Property Range Restrictions:		None

| Object Id | Object Name | Units | Data Range |
| --- | --- | --- | --- |
| 198 | Mac address | None | 0 - 127 |
| 199 | IMC address | None | 1 - 31 |
| 200 | IMC version[4] | None | 0 - 127 |
| 201 | IMC version[5] | None | 0 - 127 |
| 202 | IMC version[6] | None | 0 - 127 |
| 203 | IMC version[7] | None | 0 - 127 |
| 204 | IMC version[8] | None | 0 - 127 |
| 205 | IMC version[9] | None | 0 - 127 |
| 206 | IMC version[10] | None | 0 - 127 |
| 207 | IMC version[11] | None | 0 - 127 |
| 231 | Unit ID | None | 0 - 127 |
| 232 | Unit status | None | 0 - 255 |
| 239 | Space temperature | Deg. F | 63.75 - 100.00 |
| 240 | Discharge air temperature | Deg. F | -8.7 – 164.4 |
| 241 | Effective occupancy | None | 0 - 2 |
| 242 | Local outside air temperature | Deg. F | -30.6 – 131.6 |
| 243 | Local space temp. | Deg. F | 63.75 – 100.00 |
| 244 | Outside air damper | Percent | 0 - 100, 255 |
| 245 | Heat primary | Percent | 0 – 100 |
| 246 | Heat secondary | Percent | 0 – 100 |
| 247 | Cool primary | Percent | 0 – 100 |
| 248 | Economizer enabled | Percent | 0, 1, 255 |
| 250 | Supply fan status | Percent | 0 - 100 |
| 252 | Space temperature setpoint (effective) | Deg. F | 40.0 – 95.0 |
| 253 | Current error | None | 0 - 255 |
| 254 | Error pointer | None | 0 – 83 |
| 255 | Most recent error 1 | None | 1 - 255 |
| 256 | Most recent error 2 | None | 1 - 255 |
| 257 | Most recent error 3 | None | 1 - 255 |
| 258 | Most recent error 4 | None | 1 - 255 |
| 259 | Most recent error 5 | None | 1 - 255 |
| 260 | Most recent error 6 | None | 1 - 255 |
| 261 | Most recent error 7 | None | 1 - 255 |
| 262 | Most recent error 8 | None | 1 - 255 |
| 263 | Most recent error 9 | None | 1 - 255 |
| 264 | Most recent error 10 | None | 1 - 255 |
| 274 | Space co2 sensor (effective) | Parts/million | 0 – 6, 7 – 1992, 1993 - 2000 |
| 275 | Space co2 sensor (local) | Parts/million | 0 – 6, 7 – 1992, 1993 - 2000 |
| 276 | Space humidity (effective) | Percent | 0 - 100 |
| 277 | Space humidity (local) | Percent | 0 - 100 |
| 278 | Dehumidification setpoint (effective) | Percent | 0 - 100 |
| 279 | Dehumidification status | None | 0 - 2 |
| 281 | Return air temperature | Deg. F | -8.7 – 164.4 |
| 282 | Building static pressure | Inches of water | -0.500 - .500 |
| 283 | Duct static pressure | Inches of water | 0 – 5.00 |
| 285 | Exhaust fan status | Percent | 0 - 100 |

Analog Output Objects:

Optional Properties Supported:	Min_Pres_Value

Max_Pres_Value

Optional Writable Properties:		Out_Of_Service

Property Range Restrictions:		None

| Object Id | Object Name | Units | Min. Value | Max. Value | Valid Values Within Range |
| --- | --- | --- | --- | --- | --- |
| 101 | Application mode control | None | 0 | 255 | 0,1,3,6,9,208,209,216,217,218,224 – 230,232,236,254,255 |
| 102 | Outdoor air min. pos. control | Percent | 0 | 255 | all |
| 103 | Occupancy override control | None | 0 | 255 | all |
| 104 | Occupancy scheduler control | None | 0 | 255 | all |
| 107 | Occupancy sensor input | None | 0 | 255 | all |
| 108 | Space dehumidification setpoint | Percent | 0 | 100 | all |
| 109 | Temperature setpoint | Deg. F | 36.25 | 100.00 | all |
| 110 | Temperature setpoint offset | Deg. F | -32.00 | 31.75 | all |
| 113 | Space temperature input | Deg. F | 36.25 | 100.00 | all |
| 114 | Emergency override control | None | 0 | 255 | all |
| 115 | Compressor enable control | None | 0 | 255 | all |
| 117 | Primary heat enable control | None | 0 | 255 | all |
| 119 | Auxiliary heat enable control | None | 0 | 255 | all |
| 123 | Duct static setpoint | Inches of water | 0 | 5 | all |
| 124 | Building static setpoint | Inches of water | -0.5 | 0.5 | all |
| 125 | Discharge air cooling setpoint | Deg. F | 40 | 80 | all |
| 126 | Discharge air heating setpoint | Deg. F | 80 | 140 | all |
| 127 | Supply fan capacity input | Percent | 0 | 255 | all |
| 128 | Exhaust fan capacity input | Percent | 0 | 255 | all |
| 129 | Set Economizer Outdoor Air Suitable | None | 0 | 255 | all |

Analog Value Objects:

Optional Properties Supported:	None

Optional Writable Properties:		Present_Value

Property Range Restrictions:		None

| Object Id | Object Name | Units | Min. Value | Max. Value | Valid Values Within Range |
| --- | --- | --- | --- | --- | --- |
| 1 | Baud Rate Setting | None | 9600 | 76800 | 9600,19200,38400,76800 |
| 130 | Heating Occupied setpoint | Deg. F | 40 | 95 | all |
| 131 | Cooling Occupied setpoint | Deg. F | 40 | 95 | all |
| 132 | Heating Unoccupied setpoint | Deg. F | 40 | 95 | all |
| 133 | Cooling Unoccupied setpoint | Deg. F | 40 | 95 | all |

Standard Object Types Supported:

- Compressor

- Heat Stage

- Blower

- Economizer

- Air

Compressor Objects: (Instances 1,2,3 and 4)

Standard Properties Supported:	Object_Identifier

Object_Name

Object_Type

Out_Of_Service

Proprietary Properties Supported:	 Lennox_Object_Installed

Lennox_Object_Running

Lennox_Object_Run_Time

Lennox_Object_Min_Cycle_Time

Lennox_Object_Cycle_Count

Lennox_Object_Error

Heat Stage Objects: (Instances 1,2,3 and 4)

Standard Properties Supported:	Object_Identifier

Object_Name

Object_Type

Out_Of_Service

Proprietary Properties Supported:	 Lennox_Object_Installed

Lennox_Object_Running

Lennox_Object_Run_Time

Lennox_Object_Min_Cycle_Time

Lennox_Object_Cycle_Count

Lennox_Object_Error

Lennox_Object_HeatType

Blower Objects: (Instance 1)

Standard Properties Supported:	Object_Identifier

Object_Name

Object_Type

Out_Of_Service

Proprietary Properties Supported:	 Lennox_Object_Running

Lennox_Object_Run_Time

Lennox_Object_Cycle_Count

Lennox_Object_Error

Economizer Objects: (Instance 1)

Standard Properties Supported:	Object_Identifier

Object_Name

Object_Type

Out_Of_Service

Proprietary Properties Supported:	 Lennox_Object_Installed

Lennox_Object_Running

Lennox_Object_Run_Time

Lennox_Object_Cycle_Count

Lennox_Object_Error

Air Objects: (Instances 1,2 and 3)

Standard Properties Supported:	Object_Identifier

Object_Name

Object_Type

Proprietary Properties Supported:	 Lennox_Object_Temperature

Lennox_Object_Duct_Static_SP

Lennox_Object_Relative_Humidity

Lennox_Object_CO2_Level

Data Link Layer Options (check all that are supported):

( BACnet IP, (Annex J)

( Able to register as a Foreign Device

( ISO 8802-3, Ethernet (Clause 7)

( ANSI/ATA 878.1, 2.5 Mb. ARCNET (Clause 8)

( ANSI/ATA 878.1, RS-485 ARCNET (Clause 8), baud rate(s) ____________

( MS/TP master (Clause 9), baud rate(s): 9600, 19.2k, 38.4k, 76.8k

( MS/TP slave (Clause 9), baud rate(s):

( Point-To-Point, EIA 232 (Clause 10), baud rate(s): _________________

( Point-To-Point, modem, (Clause 10), baud rate(s): _________________

( LonTalk, (Clause 11), medium: _________________________________

( Other: _____________________________________________________

Networking Options: None

Segmentation Capability: None

Character Sets Supported:

Indicating support for multiple character sets does not imply that they can all be supported simultaneously.

( ANSI X3.4				( IBM(/Microsoft( DBCS		( ISO 8859-1

( ISO 10646 (UCS-2)		( ISO 10646 (ICS-4)			( JIS C 6226

If this product is a communication gateway, describe the non-BACnet equipment/network(s) that the gateway supports: N/A

Include any addition information about the product's BACnet capabilities relevant to interoperability:

1. When writing a new baud rate to AV1, new baud rate only takes affect after a reset