# Technology Implementation Specifications

# for the

# Oakland Unified School District

# Version 1.4

December 4, 2008

# Table of Contents

Introduction	1

1.0	Communication Cable System Infrastructures	2

1.1	Overview	2

1.2	Definition – Communication Cable System	3

1.3	Basic CCS Contractor Responsibilities	4

1.4	CCS Standards and Submittals	7

1.5	Products and Minimum Provisions	11

1.6	CCS Pathway Installation	20

1.7	Bonding and Grounding	24

1.8	CCS Installation	25

1.9	CATV Cable System Provisions	28

1.10	Testing	30

1.11	Warranty	31

1.12	Voice and Data CCS Labeling	32

1.13	As-Built Documentation	32

1.14	Miscellaneous Specifications	33

2.0	Network System Infrastructures	34

2.1	Overview	34

2.2	Cabling and Network Infrastructures	34

2.3	Enterprise Network Architecture	34

2.4	Switched Architecture Characteristics	35

2.5	Power Protection	36

2.6	Network Security	37

2.7	Systems Testing and Acceptance	37

3.0	Voice Communication System Infrastructures	38

3.1	Overview	38

3.2	Clocks, Bells and Paging	38

3.3	Scope of Work	38

3.4	Technology and Guidelines	39

3.5	Required Station and Attendant Equipment	40

A	Appendix A: Data Cabling Systems Design Standards	42

# Introduction

# General

The Technology Implementation Specifications within this document represent the standards of the Oakland Unified School District (OUSD) relative to the provisioning and implementation of Information Technology and related systems.  Collectively, these specifications address a broad range of technologies, specifically:

Communication Cable Systems (CCS) and Related Infrastructures

Data Network (e.g., LAN/WAN) Infrastructures

Cable Access Television (CATV) Content Distribution Infrastructures

Voice-over-IP (VoIP) Telecommunication Infrastructures

Please note that, wherever a specific manufacturer and/or product is listed, the words “or equivalent” shall be understood to be appended.  Such equivalents, however, are subject to OUSD approval.

# 1.0	Communications Cable
System Infrastructures

# 1.1	Overview

The Communication Cable System (CCS) is designed to be a distributed star topology with all data, voice and video (CATV) services originating from a Main Distribution Facility (MDF).  From the MDF, cables shall extend to various Intermediate Distribution Facility (IDF) and Small IDF (e.g., CDF) locations distributed throughout the campus.  To the extent possible, all MDFs, IDFs and Small IDFs shall be located in secured areas and/or enclosures; all such locations shall be subject to approval by OUSD.  An extensive conduit and manhole system extends throughout most of the larger campuses and provides communication pathways to each of the buildings.

Connectivity between these facilities shall be via fiber optic and/or copper cables.  For all new implementations, the following represents OUSD Standard:

50/125 micron Multimode Fiber Optic Cables, with SC-Type Connectors

Singlemode Fiber Optic Cables, with SC-Type Connectors

Category 6 Unshielded Twisted Pair Copper Cables, with Category 6 RJ45 Connectors

RG6 Coaxial Cables, with F-Type Connectors

Alternate standards may be approved by OUSD on a case-by-case basis where existing cable will be supplemented by new cables.

Separate parallel star and daisy chain topologies typically exist for security services, fire alarm, building management, voice and bells.  The CCS Contractor shall take great care should be taken not to disturb these systems in any way.  The Technology Implementation Specifications herein are intended to cover data, voice and video connectivity; they are not intended to cover these other systems.

This section provides a description of technical and/or performance specifications relative to OUSD’s CCS installation unit pricing requirements.  Specifically, this section has been arranged to present information in the following order:

Basic CCS Contractor Responsibilities

CCS Contractor Qualifications

Panduit design and installation certifications

Provisioning by CCS Contractor

Provisioning by Others

CCS and CCS pathways Installations

Submittals/Variances

Acceptance and Subsequent Support

Other CCS Contractor Responsibilities

System Documentation and Standards

Standards, Guidelines and Practices

System Certification and/or Warranties

Products

MDF/IDF Room Buildouts

CCS Pathways

Backbone Cables and Terminations

Horizontal Cables and Terminations

Other

Installation

CCS Overview

MDF/IDF Room Buildouts

CCS Pathways

Backbone Cables and Terminations

Horizontal Cables and Terminations

Miscellaneous Cable Requirements

Labeling Schemes

Testing Procedures

As-Built Documentation

Miscellaneous OUSD Installation Requirements

# 1.2	Definition – Communication Cable System

Communication Cable System (CCS) is defined as all required equipment and cabling including the following:  cabinets, racks, splice enclosures, termination blocks, cross-connect wire or cordage, patch panels, patch cords, telecommunication outlets, mounting hardware, wire management, shielded and unshielded twisted pair, sub-duct (innerduct), coaxial and optical fiber cable installed and configured to provide computer data and voice connectivity from each data or voice device to the network file server or voice network/switch designated as the service point of the local area network.

Cables and terminations shall be provided and located as shown and in the quantities indicated in the Scope of Work and supported by the drawings.  Fiber cables shall terminate in modular patch panels located in all demarcation and termination points shown on the drawings.  All cables and terminations shall be identified at all locations.  All cables shall terminate in an alphanumeric sequence at all termination locations.  All copper cable terminations shall comply with, and be tested to TIA/EIA 568A and TSB-67 standards for Category 6 (or lesser standards, as applicable) for data cabling and telephone installations.  Station cables shall terminate on appropriate station termination hardware, surface mount or flush mount, equipped as shown on the drawings.

1.3	Basic CCS Contractor Responsibilities

Attributes.  The CCS Contractor shall, at a minimum, possess the following attributes:

Current manufacturer certification as a certified designer and as a certified installer of the product to be installed, which shall remain valid during the entire course of the installation agreement, with no known pending action or intent by manufacturer and/or the CCS Contractor to terminate or limit status as a manufacturer certified designer and installer.  NOTE: Pending Respondent status as a certified designer and installer is unacceptable.

At least one prior year of certified status with the manufacturer for the products to be installed, including the right and ability to deliver a completed installation conforming to the manufacturer’s warranty program requirements; additionally, the CCS Contractor must have completed at least five similar projects as a certified designer and installer for the products to be installed.

Five years of CCS and CCS pathway implementation experience under its current organizational structure, either directly or under wholly owned predecessor entities.

Profitable status for at least the two preceding fiscal years (three years if privately held and not submitting financial statements).

No significant pending litigations, which may subject the company to financial risk exceeding twenty percent of its value.

Insurance coverage as required by OUSD (such as, but not limited to, workers compensation), as well as professional liability coverage of not less than $1,000,000 per occurrence.

At least one Registered Communication Distribution Designer (RCDD) certified by Building Industries Consultant Services International, including the willingness and intent to assign such personnel to this project as project engineer or project manager.

Personnel specifically trained and certified under the manufacturer’s installation training program, including the willingness and intent to assign installation project resources in a manner which utilizes certified personnel for each and every project manager and foreman/supervisor position associated with providing services to meet these installation requirements.

Provisioning by CCS Contractor.

It shall be the responsibility of the Contractor to provide any cable path engineering and cable system engineering not already provided on drawings issued by OUSD for the subject CCS installation.  OUSD or OUSD’s representative, prior to cable placement, must approve any engineered pathways not already depicted on the drawings.  The Contractor shall provide a designated project manager to coordinate engineering and construction activity with OUSD or OUSD’s representative throughout the course of this engagement.

The CCS Contractor, except as otherwise indicated herein, shall also:

Provide and install all materials including, but not limited to: communications cable; station jacks, inserts and faceplates; device boxes and brackets; cable support apparatus; cable runways; cable raceways; conduits, sleeves, firestopping, underground pull boxes, junction boxes, grounding, coring and patching, equipment racks, equipment cabinets, MDF/IDF termination components; firestopping; labeling; testing; etc.

Provide and furnish all supplemental labor and related services, including, but not limited to: design/engineering, testing, and test equipment, as-built documentation in AutoCAD printed drawings and software file copy format, contract administration, etc., as applicable to expeditiously completing CCS installations at OUSD facilities in accordance with requirements of this Technical Specification

Provide and furnish all permits

Satisfy all shipping, tax and other expenses reasonably associated with the CCS Implementation

Provide and furnish completely installed and certified systems, inclusive of as-built documentation, cable test documentation, manufacturer’s warranties, as well as any and all regulatory signoffs associated with the CCS Implementation.

Provide and furnish completed lien waivers and lien releases for each supplier or trade subcontractor utilized during the course of the project.

Coordinate as necessary with OUSD facilities personnel, campus faculty, OUSD’s Representative, and other OUSD contractors, as well as execute CCS installations in accordance with demands of OUSD’s CCS requirements.

OUSD reserves the right to define other CCS Contractor responsibilities before executing a final contract.

Provisioning by Others.  Within the fulfillment of each OUSD CCS installation requirement, certain responsibilities are borne by others.  The following bullets generally outline the duties of OUSD and OUSD’s representative.

OUSD’s Representative: For purposes of OUSD’s CCS installation requirements, OUSD Representative’s overall responsibilities include: providing OUSD with advice and design services relative to the communications infrastructure; oversight and/or project management specifically relevant to OUSD’s CCS installation requirements; serve as a liaison between OUSD, the CCS Contractor, campus faculty, various OUSD facilities personnel, and others as applicable but specifically relevant to design, engineering and implementation of OUSD’s CCS infrastructure.

CCS Installation.  It is intended that all unshielded twisted pair (UTP) cabling will be installed, tested and certified to meet the latest available draft of TIA/EIA requirements for Category 6 cabling installations, as well as other industry standards, guidelines and practices.  Fiber optic cabling implemented pursuant to OUSD’s CCS installation requirements shall likewise be installed, tested and certified to meet the latest applicable standards, guidelines and practices.  Furthermore, each installation shall be certified to meet the latest available manufacturer’s requirements for an extended warranty of fifteen (15) years minimum duration.

CCS Contractor Submittals/Variances.  OUSD’s CCS installations require the submittal of various items as part of the project process.  These items include, but are not limited to:

Identification of and specifications regarding any specification variance (see Variances, below)[1][2]

AutoCAD plot(s) of CCS pathways and outlet placement drawings, inclusive of proposed outlet numbering layout[1]

Support details for each CCS pathways system to be installed by CCS Contractor[1]

Proposed location of termination block(s) supporting MPOE/Tie Cable services at each building MPOE[1]

Sample outlet, termination and cable labels of each type[1]

MDF and IDF rack or cabinet elevation drawings[3]

Fiber optic cable test results from each cable spool (if applicable)[2]

Current test equipment calibration certifications for each specific test device[2]

Written notice of scheduled testing (to be delivered at least three business days in advance)[2]

Detailed cable test result documentation[3]

Detailed as-built drawings[3]

NOTES:    [1] – Constitutes an initial submittal to be provided no later than the date/time specified by OUSD.    [2] – To be submitted as necessary prior to commencing affected work.    [3] – To be submitted within ten days after completion of each CCS installation (unless otherwise noted).

This Specification and associated documents may specify various required materials, components and processes.  To the extent the CCS Contractor intends to deviate from any written or intended specification, a written submittal must be provided to OUSD/OUSD’s Representative and written OUSD approval must be granted prior to proceeding with any variance.

Acceptance and Subsequent Support.  Prior to each CCS installation final acceptance, the CCS Contractor will perform complete system tests under the supervision of OUSD and/or OUSD’s Representative.  The CCS Contractor will furnish all necessary test equipment and perform all work required to determine or modify CCS performance to meet specifications as described herein.  This work shall include, but not be limited to, the following at no extra cost:

Complete testing of each and every cable pair or fiber strand in accordance with TIA/EIA standards and guidelines

Submission of detailed, computer generated test results to OUSD/OUSD’s Representatives as required within this Technical Specification

Adjustment of all components for optimum quality operation as well as for maximum manageability and esthetic quality

Development and provision of complete as-built drawings and other documentation as required within this Technical Specification

Provision of complete instruction to OUSD’s personnel in the proper operation of the CCS by a qualified representative of the CCS Contractor at a time suitable to OUSD; complete instructions, diagrams and drawings necessary to ensure the success of the training shall be developed by the CCS Contractor and will become the property of OUSD prior to acceptance

OUSD shall either accept the network in writing or notify CCS Contractor in writing, specifying in reasonable detail, those particulars, which OUSD deems unacceptable.  With respect to any such particulars, which OUSD deems are unacceptable, the CCS Contractor shall immediately proceed to correct them, and after correction thereof, OUSD shall accept  or reject the modifications in writing.

Other CCS Contractor Responsibilities.  In addition to the above, the CCS Contractor shall also abide by the following responsibilities:

Site Cleaning.  Throughout the progress of each OUSD CCS installation, the CCS Contractor shall keep the working areas free from debris of all types and shall remove from the premises all refuse resulting from any work performed by the CCS Contractor.  On a daily basis and at the completion of its work, the CCS Contractor shall, to the extent possible, leave the premises in a clean and finished condition.

Safety Requirements.  The CCS Contractor will utilize appropriate personnel and display warning signs, signals, flags and/or barricades at the work site to ensure adherence to OUSD, State and industry safety regulations and as prudence requires.  Costs for such safety provisions shall be included within each unit pricing cost.

Specification Status.  All specifications and requirements related to this project will not be “frozen”, but are subject to change by OUSD and/or OUSD’s Representative.

# 1.4	CCS Standards and Submittals

Standards, Guidelines and Practices.  As stated earlier, installation and certification of all unshielded twisted pair (UTP) cabling in accordance with the latest available TIA/EIA requirements for Category 6 cabling installations is required.

Structured Communication Cable Systems and CCS Pathways shall be installed in a “neat and workmanlike manner” as specified by ANSI/NECA/BICSI 568-2001 and National Electrical Code, Sections 110-12 and 800-6.

The CCS contractor shall adhere to and comply with the latest versions and/or revisions of each applicable standard.  Among the various standards, guidelines and practices applicable to this project are the following:

BUILDING INDUSTRY CONSULTING SERVICES INTERNATIONAL:

BICSI Telecommunications Distribution Methods Manual

CALIFORNIA BUILDING STANDARDS COMMISSION:

California Electrical Code (1998) Title 24, Part 3

FEDERAL COMMUNICATIONS COMMISSION (FCC):

FCC Part 68.5: Establishment of Telephone Premises Wiring Attestation List

INSULATED CABLE ENGINEERS ASSOCIATION (ICEA):

ANSI/ICEA S-80-576: Communication Wire and Cable for Wiring of Premises (1994)

NATIONAL ELECTRICAL MANUFACTURERS ASSOCIATION (NEMA):

NEMA WC 63: Telecommunications Cables (1994)

NATIONAL FIRE PROTECTION ASSOCIATION (NFPA):

NFPA 70: National Electrical Code (1999)

Public Works Standards, Inc.

Green Book Standard Specifications For Public Works Construction (2000)

RURAL ELECTRIFICATION ADMINISTRATION (REA)

REA 345-165: Digital Stored Program Controlled Central Office Equipment (Form 522) (1989)

REA TECM 823: Electrical Protection by Use of Gas Tube Arrestors (1980)

TELECOMMUNICATIONS INDUSTRY ASSOCIATION/ELECTRONIC INDUSTRIES ALLIANCE (EIA)

TIA/EIA-455-21: FOTP-21 Mating Durability of Fiber Optic Interconnecting Devices (1988)

EIA-492AAAA: 62.5 uM Core Diameter/125 uM Cladding Diameter Class Ia Multimode, Graded-Index Optical Waveguide Fibers (1989)

TIA/EIA-526-14A: Optical Power Loss Measurements of Installed Multimode Fiber Cable Plant – OFSTP-14 (August 1998)

TIA/EIA-568-B.1: Commercial Building Telecommunications Cabling Standard Part 1: General Requirements (May 2001)

TIA/EIA-568-B.2: Commercial Building Telecommunications Cabling Standard Part 2: Balanced Twisted-Pair Cabling Components (May 2001)

TIA/EIA-568-B.3: Optical Fiber Components Standard (April 2000)

TIA/EIA-569: Commercial Building Standard for Telecommunications Pathways and Spaces (June 2001)

TIA/EIA-570: Residential Telecommunications Wiring Standard  (October 1999)

TIA/EIA-598: Optical Fiber Cabling Color Coding (May 1995)

TIA/EIA-606: Administration Standard for the Telecommunications Infrastructure of Commercial Buildings (February 1993)

TIA/EIA-607: Commercial Building Ground and Bonding Requirements for Telecommunications (August 1994)

TIA/EIA TSB-75: Additional Horizontal Cabling Practices for Open Offices (1996)

TIA/EIA TSB-758: Customer-Owned Outside Plant Telecommunications Cabling Standard  (April 1999)

UNDERWRITERS LABORATORIES INC. (UL)

UL 444: Communications Cables (1994; R 1995, Bul. 1995 and 1996)

UL 467: Grounding and Bonding Equipment (1993; Bul. 1994 and 1996, R 1996)

UL 497: Safety Protector for Paired Conductor Communication Circuit (1995)

UL 514C: Nonmetallic Outlet Boxes, Flush-Device Boxes, and Covers (1988; R 1989, Bul. 1993 and 1994)

UL 910: Flame-Propagation and Smoke-Density Values for Electrical and Optical-Fiber Cables Used in Spaces Transporting Environmental Air (1995; R 1995, Bul. 1995 and 1996)

UL 969: Marking and Labeling Systems (1995)

UL 1286: Office Furnishings (1993)

UL 1581: Electrical Wires, Cables, and Flexible Cords (1991; Bul. 1993, 1994, 1995, and 1996, R 1996)

UL 1666: Flame Propagation Height of Electrical and Optical-Fiber Cables Installed in Vertical Shafts (1991; Bul. 1995 and 1996)

UL 1863: Communication Circuit Accessories (1995)

Federal, state, local, and OUSD codes, rules, regulations and ordinances governing the work, as well as various additional standards, guidelines and practices, may apply and shall be incorporated as part of these Technical Specifications.

In reviewing the various Contract Documents, the CCS Contractor shall be responsible for noting conflicts between proposed design/concepts and the applicable standards, guidelines and practices.  A written Request for Information (RFI) shall be developed by the CCS Contractor and submitted to OUSD and/or OUSD’s Representative prior to commencing any work impacted by such conflicts; such RFIs shall describe the conflict/violation and, if appropriate, recommend alternative solutions with associated costs.  OUSD and/or OUSD’s Representative warrants it will diligently strive to address such RFIs in order to minimize negative impact on each CCS installation completion schedule.

Where the requirements of the Contract Documents are more stringent than applicable codes, rules, regulations, ordinances, standards, guidelines and practices, the Contract Documents shall apply.  In all other instances, the most current standards, guidelines and practices shall apply.

System Certification and/or Warranty.  The installation must be certified to meet the manufacturer’s latest available warranty program requirements and delivering to OUSD an extended warranty of at least twenty-five (25) years duration.  At minimum, such warranty shall, at no additional cost to OUSD, provide a system warranty covering the installed CCS against defects in workmanship, components and performance.  General features of the warranty shall, at a minimum, include:

An installation warranty extending to the CCS protecting OUSD against defects in workmanship for a period of at least one year from the date of system acceptance.  Such warranty shall provide all labor and materials necessary to correct a failed portion of the system and to demonstrate performance within original specifications after the repairs are accomplished.

A system performance warranty extended by the CCS component manufacturer for a period of not less than fifteen (15) years from date of system acceptance.  The performance warranty shall warrant the installed horizontal copper and, as applicable, the installed horizontal and backbone fiber optic portions of the system.  All such links and segments shall be warranted in accordance with the latest applicable requirements as defined by TIA/EIA.

As outlined herein, OUSD intends that the resulting CCS will be warranted under the extended warranty provisions extended by the manufacturer.  The Technical Specification is based on the products being manufactured by Panduit and others.  The warranty shall extend to UTP and fiber optic portions of the installation to the fullest extent allowed by the manufacturer.

Submittals.  The CCS Contractor is to submit the following prior to construction for OUSD approval:

Manufacturer's Catalog Data:

Telecommunications cabling (backbone and horizontal)

Fiber optic type SC connectors

Telecommunications outlet/connector assemblies (RJ-11 and RJ-45 jacks)

Equipment enclosures and support racks

Patch Panels (Copper and Fiber optic)

Power Strips

Cable Hangers

Floor outlet boxes or modules

Firestop material

External mounted raceway

Cable tray

Drawings:

Telecommunications Drawings

Distribution Frame Elevations

Telecommunications Drawings:

Provide BICSI RUDD-approved drawings complete with wiring diagrams and details required to prove that the distribution system shall properly support connectivity from the MDF to the IDF to the telecommunications work area outlets.

Show the layout of cabling and pathway runs, MDF, IDF and ground system.

Drawings shall depict final telecommunications cabling configuration, including location, gage, pair assignment and patch panels after telecommunications cable installation.

Provide a plastic laminated schematic of telecommunications cable system showing cabling, MDFs, IDFs, SMALL IDFs, and equipment rooms keyed to floor plans by room number.

Provide two (2) electronic copies of as-built drawings to OUSD; such files shall leverage Autodesk AutoCAD 2003 or later.

Distribution Frame Elevations:

Provide shop drawings showing layouts of applicable equipment including incoming IDF racks, patch panels and LAN equipment.

Statements:

Installer qualifications

Test plan

Professional References

Labeling Scheme

# 1.5	Products and Minimum Provisions

The Contract Documents generally outline industry standard components to be installed as part of OUSD’s CCS installation requirements.  Such identification is intended to be general in nature rather than exhaustive; all quantities, if stated, are subject to validation by Respondent.  Respondent is reminded that differences between estimated quantities and those reasonably derived based from the Contract Documents (as well as through bid conferences, job walks, RFB addendums, and other distribution of information) shall be the responsibility of the CCS Contractor; there shall be no additional cost incurred by OUSD for complying with the specifications and requirements of the Contract Documents.

Any variance from those components identified on the drawings and/or below shall be submitted to OUSD/OUSD’s Representatives for approval prior to ordering and installation; the risk for all costs incurred by the CCS Contractor for materials ordered prior to such written approval shall be borne entirely by the CCS Contractor.  Nonetheless, it is imperative that the CCS Contractor determine the availability of necessary materials and propose equivalent substitutes as necessary to meet all installation milestones; delays in CCS installations due to lack of product availability are unacceptable.  As catalog numbers change frequently, the CCS Contractor must verify all part numbers prior to ordering materials.  Clarifications will be issued in response to written Requests for Information (RFIs)

All UTP, fiber optic cabling, innerduct and cable ties, where required, will be plenum-rated (i.e., CMP, ONFP).  Copper and fiber optic backbone cable intended for installation within conduit, riser shafts and chases, etc., shall be at a minimum, rated CMR (riser rated).  Unrated cable (such as filled ASP) shall not be installed within the structure except when placed within EMT, IMC, PVC or RGS conduit.

CCS Delivery and Storage.  CCS Contractor shall provide protection from weather, moisture, dirt, dust and other contaminants for telecommunications cabling and pathway equipment placed in storage.

Components.  Components shall be UL or third party certified.  Provide a complete system of telecommunications cabling and pathway components using star topology and support structures, pathways, and spaces complete with conduits, pull wires, raceways, junction boxes, underground pull boxes, outlets, and cables, as per OUSD CCS requirements.  Fixed cables and pathway systems for telecommunications systems shall be UL listed or third party independent testing laboratory certified, and shall comply with NFPA 70.  Horizontal cable shall be General or Mohawk, and termination equipment shall be Panduit and installed and certified so as to provide a 25-year warranty.

Pathways (Backbone & Horizontal).  Pathways shall consist of conduits; pull boxes, sleeves, cable runway, raceways, ceiling hangers, J-Hooks and outlet boxes as per the drawings.  Provide grounding and bonding as required by TIA/EIA-569 and TIA/EIA-607.

Distribution Frames.  Provide main distribution facilities (MDFs) and intermediate distribution facilities (IDFs), as required per each CCS installation site walk for terminating and cross connecting permanent cabling links.

Equipment Enclosures.  Equipment cabinets shall consist of frame, sides, top, front door and back door.  Perforated doors shall be provided for enclosures within secured rooms, but solid doors are required within classrooms and other rooms/areas where students may be present.  Lockable front and louvered/perforated lockable back doors are required.  Enclosure frames and doors shall be made of 16-gauge high quality cold rolled steel (CRS) throughout in an all-welded construction.  Enclosure side panels and top panels shall be made of minimum 18-gauge high quality cold rolled steel (CRS).  Cabinet finish color shall be determined by OUSD, modular type steel construction and treated to resist corrosion.

The following additional requirements apply:

Enclosure Top Panel is to be perforated to allow for heat exhaust as well as adaptable for fan assembly options.

Enclosure should have three (3) cable access panels located at base of cabinet on each side and at the back for cable access when cabinet may not be on raised floor or cable entry is not coming from the ceiling.

Enclosure shall have a 1,000 pound loading capacity.

The enclosure shall provide 19” rack mounting.

Dimensions shall be approximately 84”H X 24” W X 36” D. Seismic bracing shall be installed.

A 315 CFM top mount fan assembly enclosed within a fan housing and supplied with 6 foot power cord shall be provided within all enclosures.

The equipment enclosure shall be Cooper B-Line E2-SC-842436-19-BL or OUSD approved equal.

Equipment Racks.  Equipment racks shall be freestanding modular aluminum units designed for telecommunications terminal support and coordinated with dimensions of units to be supported.  Equipment racks shall have approximate module dimensions of 84 inches high by 19 inches wide by 3 inches channel depth.  Additional characteristics of the equipment racks shall be as follows:

All high strength, lightweight 6061-T6 aluminum extrusion construction.

Equipped with two top angles or top bars and heavy-duty assembly hardware.

Have EIA hole pattern on front and rear.

Assemble to provide 19-inch mounting with no additional hardware.

Have:

EIA Channel: 3" x 1.265" x 1/4" thick flange

Base Angles: 3 1/2" x 6" x 3/8" thick (pair)

Top Angles: 1 1/2" x 1 1/2" x 1/4" (pair).

Top Bars: 1 1/2" x 1/4" (pair).

A weight capacity of 1000 lb (weight must be evenly distributed).

Clear coated over a brushed aluminum finish.

Provide floor and ceiling access for cable management and distribution.

Provide a pre-drilled base for floor attachment of rack.

Equipment racks shall be earthquake braced.

Equipment racks shall be Cooper B-Line SB-556-084-XU or OUSD approved equal.

Wire Management.  All 84” tall equipment racks shall be equipped with vertical wire management organizers.  All equipment racks, wall mount racks and wall mount cabinets shall be equipped with horizontal wire management.

All horizontal wire managers shall be heavy duty painted black metal units designed specifically to connect to equipment frames.  All vertical wire managers shall be aluminum with a black finish.  All wire managers shall be secured to the frames and shall provide a clear and unobstructed pathway in which to route the cables.  Each UTP and fiber optic patch panel will have one (1) 2RU horizontal wire manager above and below.

Vertical Wire Managers.  Vertical wire managers shall be six inches wide and seven feet tall.  Vertical wire mangers shall have evenly spaced wire rings designed to maintain jumper, patch, or cross-connect wire in place.

Vertical wire managers shall be designed to extend past the frame to allow placement of equipment in any position within the rack.  When mounted between equipment frames, they shall be designed to direct cables into either frame and shall be securely mounted to both units.  Vertical wire managers shall be equipped with cable restraint latches.

Vertical wire managers shall be Cooper B-Line-SB-63S-084 or OUSD approved equivalent.

Equipment Rack – Wall-Mounted.  Wall-mounted equipment racks shall have approximate module dimensions of 36 or 48 inches high by 19 inches wide by 3 inches channel depth.  Additional characteristics of the equipment racks shall be as follows:

All high strength, lightweight 6061-T6 aluminum extrusion construction.

Rated for 350 lb. load capacity (dependant on wall characteristic)

Have EIA hole pattern on front and rear.

Assemble to provide 19-inch mounting with no additional hardware.

Have an EIA Channel 3" x 1.265" x 1/4" thick flange.

Be clearcoated over a brushed aluminum finish.

Provide access for cable management and distribution.

Provide pre-drilled base for wall attachment of rack.

Wall-mounted equipment racks shall be mounted on plywood backboard in location to be determined.

Wall-mounted equipment racks shall be manufactured by Cooper B-Line or OUSD approved equivalent.

Equipment Cabinet – Wall-Mounted.  Wall-mounted equipment cabinets shall be fully enclosed, lockable, modular type steel construction and treated to resist corrosion.  Such cabinets shall be wall mount/swing out type, providing 19” rack mounting, and designed to allow for left or right-hand swing.  While cabinet size will be determined on a project-by-project basis, default dimensions shall be approximately 36”H X 24” W X 24” D or 48”H X 24” W X 24” D.  An optional 210 CFM side mount fan assembly supplied with power cord shall be available.  Cabinet finish color shall be determined by OUSD.

Cabinet shall be mounted on plywood backboard in location to be determined.

Cabinets shall be manufactured by Cooper B-Line or OUSD approved equal.

Cable Runway.  Cable runways (ladder rack) shall be provided to permit installation of communications, computer, CATV, paging, distribution system cables and other low voltage system cables.  Cable Runway: Runway (ladder rack) shall be constructed of an open bottom with 1½” cable bearing surface 12” on center.  Side rails shall be minimum 1 ½” high and constructed of tubular steel.  Finish shall be black baked enamel.

Accessories and special transitions shall be provided for all changes in direction and offsets.  Use manufacturer’s standard fittings, including bolting assemblies for all end-to-end connections.  Provide transverse and longitudinal seismic restraints as required.  Provide plastic trough dropout bushings at each location where cables will descend into the equipment racks.

Cable runway wall angle supports shall be steel angles, black baked enamel finish.  Ends to be smooth without hooks or projections.  Brackets shall be able to support an end load of 600 lb. with a safety factor of 1.65.

Cable runway elbows, tee’s, 90 degree bends and crosses:  All horizontal and vertical 90 degree elbows, tees, 90 degree bends and crosses shall be made with right angle couplings which clamp to the runway without the need for drilling or cutting.

Cable runway shall be manufactured by Cooper B-Line or OUSD approved equal.

Backboards.  MDF and IDF walls shall be covered with ¾-inch thick, Grade A/C, void-free, fire rated plywood, as required.  3/4 inch thick by 8 feet-0 inches high A/C plywood.  Backboards shall be mounted vertically, starting 6 inches above the finished floor, and secured to the walls.  All backboards are to be constructed of 4 feet by 8 feet plywood.  All plywood panels must be mounted in contact with one another, leaving no gaps between sheets.

At OUSD designated wall-mount IDF rack and cabinet locations, the CCS Contractor shall install ¾-inch thick, Grade A/C, void-free, fire rated plywood of adequate height and width to support the mounting of wall mount racks or cabinets.

MDF and IDF backboards shall be equipped with sufficient quantities of 2” and 4” ‘D’ rings.

Grounding and Bonding Products.  The CCS Contract shall comply with UL 467, TIA/EIA-607, and NFPA 70.  Components shall be identified as required by TIA/EIA-606.

Firestopping Material.  Contractor shall provide all necessary fire stopping of openings through which cable is installed under this specification, in accordance with NFPA 70 and all local codes.  This includes installation in conduits, raceways, or bare penetrations.  Provide and install UL 1479 approved (Fire Barrier Caulk) firestop material.

Power Strip.  The CCS Contractor shall provide and install at each MDF and IDF one (1) rack-mounted Cooper B-Line surge suppressor 12-outlet power strip, or OUSD approved equal.

MDF Shelving.  The CCS Contractor shall provide and install at each MDF one (1) Cooper B-Line SB-596S-19-15-02M double sided shelf and one (1) B-Line SB-745S-19-16 low profile shelf.  At OUSD’s request, an optional Cooper B-Line SB-743KB-19 shall be provided and installed by the CCS contractor.

Surface Mounted Raceway.  All cable pathways shall be concealed within walls, whenever possible.

Surface mounted raceway is to be utilized in dry interior locations only as covered in Article 352 part B of the National Electrical Code, as adopted by the National Fire Protection Association and as approved by the American National Standards Institute.  All surface-mounted raceway shall be listed as suitable for use in applications having up to 600 volts between conductors by Underwriters Laboratories, Inc., when screw secured and installed per instructions.

Metal Raceway.  Metallic surface mounted raceway shall be Wiremold 4000-type metallic or Hubbell 4000 series metallic surface mounted raceway.  A full compliment of fittings shall be available including but not limited to mounting clips and straps, couplings, flat, internal and external elbows, cover clips, tees, entrance fittings, conduit connectors and bushings.

A series of inserts shall also be available for retrofit applications that provide a controlled 2" cable bend radius which meets the specifications for Fiber optic and UTP/STP cabling and exceeds the TIA 569 requirements for communications pathways.

Notching or modifications of raceway and fittings will not be permitted.

Copper Patch Panels.  Patch panels shall consist of a metal patch panel with four (4) or six (6) port faceplates, which are removable from the front.  Such panels shall:

Mount to standard EIA 19” racks

Be modular, accepting all modules designed for that product line

Be available with labels that follow TIA/EIA 606 labeling standards.

Be manufactured by Panduit or OUSD approved equal.

One patch panel port shall be provided for each workstation cable served from the MDF, IDF or SMALL IDF, with a minimum of 12 spare ports required.  The CCS Contractor shall supply and install as many patch panels as necessary to service all workstations, plus the required spare count.  Quantities of modules shall be based on the number of UTP cables originating at wall outlets and terminating at the patch panel.

Fiber Optic Patch Panels.  The CCS Contract shall provide fiber optic patch panels as necessary for the maintenance and cross connecting of fiber optic cables.  Such panels shall be constructed of 0.125-inch minimum aluminum and shall have connectors which interface the inside plant fiber optic jumper cable with the outside plant fiber optic cable.  These units will terminate the fiber optic cables, provide a place for jumper cables and will provide room to terminate additional optics.

Panels shall be sized to support a minimum of 100% growth.  Rack-mounted and wall-mounted fiber patch panels shall be equipped to terminate or splice the incoming inter-building fiber and any required backbone or interconnect cables.  Each fiber optic cable must be properly dressed.

All rack-mounted fiber optic patch panels shall be Panduit FRME36EBL, FRME54EBL or FRME72EBL or OUSD approved equal.  All wall-mounted fiber optic patch panels shall be Panduit FWME12EBL, FWME24EBL or FWME48EBL or OUSD approved equal.

The fiber optic patch panel connections shall provide 0.4 dB or less insertion loss.  All fiber optic connectors will be Panduit FSCMBL type SC or OUSD approved equivalent.

Wire Management.  All equipment racks, wall-mount racks, and wall-mount cabinets shall be equipped with horizontal wire management.  All horizontal wire managers shall be heavy duty painted black metal units designed specifically to connect to equipment frames.  All vertical wire managers shall be aluminum with a black finish.  All wire managers shall be secured to the frames and shall provide a clear and unobstructed pathway in which to route the cables.

Each UTP and fiber optic patch panel will have one (1) horizontal wire manager above and below.  The in-frame horizontal managers shall be 2RU in height and shall extend from side rail to side rail.  Horizontal wire managers shall be equipped with a 3” X 3” slotted duct and cover on front and a 2” X 5” slotted duct and cover on back.  Horizontal wire managers shall be equipped with bend radius control clips and strain relief clips.  Horizontal wire managers shall be Panduit-WMPH2 or OUSD approved equivalent.

Type 66 Blocks.  Telephone station cables will terminate on standard split 50 pair M66 Block with wall mounting bracket.  All blocks shall be equipped with blue color-coded identification strips to identify horizontal voice station cable terminations.  All 66-block assemblies, unless otherwise stated in the contract documents, (each 50 pair terminal) shall include vertical and horizontal wire management panels per block assembly.  All such blocks shall be manufactured by Siemens or OUSD approved equal.

Communications Cabling.  All communications cabling used throughout this project shall comply with the requirements as outlined in the National Electric Code (NECÒ) Articles 725, 760, 770, and 800 and the appropriate local codes.  All copper cabling shall bear CM, CMP (Plenum Rated), CMR (Riser Rated) and/or appropriate markings for the environment in which they are installed.  All optical fiber cabling shall bear OFN, OFNP (Plenum Rated), OFNR (Riser Rated) and/or appropriate markings for the environment in which they are installed.  Indoor/Outdoor rated cable shall be used where required.

Fiber Optic Backbone Cabling:

Multimode fiber optic cables shall be 50/125 micron for all new installations (or 62.5/125 micron for installations where existing fiber optic cable is 62.5/125 micron), manufactured by Corning or AMP/Pirelli.

The Contractor shall provide all required count (per OUSD requirements) optical fiber cables.

All fiber optic cables for interior use shall be tight buffered, and shall be marked OFNP per NEC Table 750-50 (e.g., non-conductive plenum rated).

Fiber optic warning tags shall placed on exposed fiber optic backbone cables.

Fiber optic warning tags shall be orange in color.

Fiber optic warning tags shall contain “Caution Fiber Optic Cable”.  The text shall be permanent, black, block, letters, at least 3/16” high.

Fiber Optic SC-style Connectors

All fiber optic termination connectors will be type SC.

The fiber optic patch panel connections shall provide 0.4 dB or less insertion loss.

The fiber optic SC-style connectors shall be manufactured by Panduit or OUSD approved equal.

Fiber Optic Patch Cables.

Fiber Optic Patch Cables shall be multimode patch cords pre-made to connect fiber optic equipment with fiber optic cross connects, interconnects and outlets.

The fiber optic patch cables (jumpers) shall be impact-resistant duplex fiber cables, with SC and/or LC connectors as appropriate for installed equipment, of the same performance characteristics as the multimode fiber backbone being connected (62.5/125μm or 50/125μm).

These fiber optic patch panel connections shall provide 0.4 dB or less insertion loss and provide connection between the Active LAN devices and the Fiber Optic patch panel.  Quantities for 100% population plus 10% Spares.

The fiber optic patch cables shall be available in 2-meter lengths.

The fiber optic patch cables shall be manufactured by Panduit or OUSD approved equal.

Horizontal Cabling

Horizontal cabling shall comply with NFPA 70, NEMA WC 63, EIA TSB-36, EIA TSB40-A, ANSI/ICEA S-80-576, EIA TSB-67 and performance characteristics in TIA/EIA-568-B.1 and B.2 standards for UTP, four-pair 100 ohm cabling.

Horizontal cabling shall provide four each individually twisted pair, 24 AWG or 22 AWG conductors enclosed by an overall jacket.

Overall diameter of four pair cable shall not exceed 0.25 inches.

Ultimate breaking strength shall be minimum 90 pounds.

Four pair cable shall withstand a bend radius of one-inch minimum at a temperature of minus 20 degrees C maximum without jacket or insulation cracking.

Conductors shall be color coded and polarized in accordance with TIA/EIA-568-B.1 and B.2.

Category 6 cable for telephone systems and local area networks shall exceed TIA/EIA-568-B.1 and B.2 standards and requirements.  [NOTE:  Lesser standards may apply on a case-by-case basis.]

Conductor shall be 22 or 24 AWG solid annealed copper.

Cable shall be plenum rated where required and shall comply with NFPA 70, UL 444, and UL 910.

Category 6 cable jacket color shall be gray.

Horizontal cabling shall be manufactured by General, Mohawk, or OUSD approved equal.

Category 6 cable runs for data shall not exceed 100 meters in length.

Work Station Outlet Assemblies

Jacks shall comply with FCC Part 68.5, and TIA/EIA-568-B.1 and B.2.

Jacks shall accommodate UTP or OFN and work in concert with Panduit non-metallic raceway and Wiremold metallic raceway.

UTP jacks for data shall be RJ-45 designation T568B type, UL 1863 listed, eight position, constructed of high impact rated thermoplastic housing rated for Category 6 service.

UTP jacks for data shall be Category 6 hardware and shall comply with the attenuation requirements contained in TIA/EIA-568-B.1 and B.2.

UTP Jacks for data shall be blue in color.

UTP jacks shall be Panduit Category 6 Mini-Com CJ688OT3R or OUSD approved equivalent.

UTP jacks for voice, clocks, bells and speakers shall be off white in color.

Workstation outlet assemblies shall include Panduit CFPE2IW and CFPE42IW faceplates and CBX2IW-A and CBX4IW-A surface mount boxes

Stenciled lettering for voice and data circuits shall be provided using thermal ink transfer process.

UTP Patch Cables.  UTP patch cables for unshielded twisted pair cable shall be Category 6 rated for Category 6 horizontal cable installations.  Such cables shall be equipped with factory-attached connectors to interconnect equipment mounted on the racks of the distribution frame and to connect computer stations to outlet locations.  UTP patch cables shall be available in 3’, 5’, 7’, 10’ and 14’ lengths for MDF, IDF, SMALL IDF and workstation locations.  UTP patch cables may also be used for patching applications, not to exceed 20 feet.  Quantities required shall provide for 100% port population with 10% spare.

UTP patch cables shall be manufactured by Panduit or OUSD approved equal.

Miscellaneous Equipment:

Conduit Sealer Kit - Semco #PR-851

Aluminum Threaded Innerduct Couplings - Pyramid Products Part#FO9006

Corrugated Fiber Optic 1” Innerduct - Carlon Products Part# CID100-T (Orange & Yellow, and Blue)

Fiber Optic Innerduct Labels - Panduit or Wiremold #PVL 200 BY

900 Micron Buffered Fiber Label - Panduit or Wiremold #PMDR-0-9 GMM polyester film marker tape as a “flag”

Fiber Optic Caution Tag - Osburn #FO4002 1-3/4” x 3-1/2”

Unspecified Equipment & Material.  Any item of equipment or material not specifically addressed on the drawings or in this document and required to provide a complete and functional CCS installation shall be provided in a level of quantity and quality consistent with other specified items.

# 1.6	CCS Pathways Installation

Cable Pathway.  Comply with OUSD, TIA/EIA-569, NEC and CEC.

In suspended ceiling areas where duct, cable trays or conduit are not available, the Contractor shall bundle, in bundles of 48 or less, station wiring with cable ties snug, but not deforming the cable geometry.  Cable bundles shall be supported via "J" hooks attached to the existing building structure and framework at a maximum of four-foot intervals.  Properly rated cable ties will be used in all appropriate areas.  The Contractor shall adhere to the manufacturers’ requirements for bending radius and pulling tension of all data and voice cables.  Cables shall not be attached to lift out ceiling grid supports or laid directly on the ceiling grid.  Cables shall not be attached to or supported by fire sprinkler lines, HVAC ducting, electrical EMT, lighting fixture or any environmental sensing device located in the ceiling air space.  All cable shall be run in transverse or longitudinal paths.

Use of existing signal and other conduit must be approved in advance by OUSD.  The CCS contractor shall be responsible for all replacement cost for damage to cables currently occupying existing conduits.

Conceal interior conduit under floor slabs and within finished walls, ceilings, and floors where possible.  Run conduits in crawl spaces and under floor slabs as if exposed.  Install conduit parallel with or at right angles to ceilings, walls, and structural members where located above accessible ceilings and where conduit is visible after completion of project.  Keep conduit minimum 6 inches away from parallel runs of electrical power equipment, flues, steam, and hot water pipes.  Install no more than two 90-degree bends for a single horizontal cable run.

Run raceway as determined by site survey.

Any transitions between buildings or structures shall include an appropriate liquid tight flex joint with a drip loop.  Provide pullboxes with liquid tight flex conduit only where flexible connections are required.  OUSD approval required prior to all liquid tight flex conduit installations.

New underground conduit shall be 1”, 2” or 4” PVC schedule 40.  All sections shall be permanently glued together.  Transition from underground PVC to above ground stub up shall be via rigid conduit.

All conduits shall be properly reamed and bushed with pull ropes installed.

Conduits terminating inside of building through floor shall be installed so that the conduit extends a minimum of 4” above finished floor.  Conduits terminating inside of building through wall shall terminate in appropriately sized junction box.

Empty conduits shall be plugged with mechanical type seals to ensure that foreign matter does not enter the building.  All empty conduits shall be equipped with mechanical type seal plugs in all pull boxes, junction boxes and within all buildings.

All conduits, sleeves and other penetrations will be firestopped by the CCS Contractor prior to acceptance.  Such firestopping shall conform to OUSD’s requirements and shall be implemented in accordance with UL design guidelines for fire-rated assemblies.

Provide all coring, patching and painting as needed for Intra-Building and Inter-Building pathways.  Caulking is not an acceptable patching method for conduit penetrations into exterior walls.  Coordinate with OUSD for acceptable patching methods.

Underground Pull Boxes and Junction Boxes.  Underground pull boxes shall be made of concrete and the minimum size shall be 35 ½” x 17 ½” x 12”.  Underground pull box covers shall be rated for traffic (type T.05) and shall be marked communications.  Metal covers shall be used in all location subject to vehicle traffic.

Underground pull boxes and junction boxes shall not be placed in areas subject to flooding.  Gravel shall be installed below all Underground pull boxes for drainage.  Establish drainage to meet Public Works Construction Standards (Green Book).

Unless otherwise noted, exterior junction boxes shall have minimum dimensions of 24” x 24” 6”.  Interior junction boxes shall consist of 16 gauge steel minimum, unless otherwise noted on plans.  Indoor enclosures shall conform to NEMA Type 4, unless otherwise noted.  Size junction boxes to not less than minimum Code requirements.  Increase size above Code requirements where necessary to provide space for pulling, racking or splicing enclosed conductors, or where specified or indicated dimensions exceed Code requirements.

Exterior metal junction boxes exposed to weather (and not installed in or below grade) shall be equipped with rain-tight or weatherproof-hinged doors.  Exterior junction boxes shall have 16 gauge steel bodies and 14 gauge steel doors.  Exterior pull boxes shall be equipped with stainless steel door clamps on three sides, a removable stainless steel continuous hinge pin, a hasp and staple for padlocking, and external mounting feet.

Enclosures installed on vertical exterior walls shall conform to NEMA Type 3R.  Enclosures installed on exterior horizontal surfaces such as rooftops or breezeways shall conform to NEMA Type 4 unless otherwise noted.  Rain tight or weatherproof boxes shall use threaded watertight hubs for top or side entry and may use knockout for bottom entry only.

Exterior pull boxes shall conform to these industry standards:

UL 508 Type 4

NEMA/EEMAC Type 3, Type 4, Type 12, Type 13

JIC standard EGP-1-1967

CSA Type 4

IEC 529, IP66

Junction Boxes shall be labeled “Communications” with screw on 1/8” engraved, black plate, white letters.

Tamper resistant screws shall be used on all exterior aboveground junction boxes that are exposed to public/student areas.

Exterior pull boxes shall be manufactured by Hoffman or OUSD approved equal.

Communication Duct-Banks and Conduits.  Use of existing signal and other conduit must be approved in advance by OUSD.

Trenches.  All underground trenches shall be 24” wide by a minimum of 30” deep.  Trenches shall be back-filled at 95% compaction.  Contractor shall contact Dig Alert a minimum of 48 hours prior to excavation to verify the location of existing underground utilities.  Modifications to pathway design may be dictated by field conditions subject to approval by OUSD.  Conduits must be inspected by OUSD’s facilities inspector prior to backfill.  Contractor shall restore surface to same or better condition.  Compaction testing notification must be provided to OUSD 48 hours prior to testing so that an OUSD inspector may be present.

Slurry fill trenches to within three inches (3”) of finished grade whenever crossing paved areas.  “Two Sack” slurry shall be used.  Pavement removal and patching shall conform to specifications and standards listed in the Public Works Standards (Green Book 2000).

Underground Conduit.  All communications conduits shall be placed in a uniform manner between ground boxes and pull boxes.  Conduit in position #1 at one ground box or pull box shall maintain its position within the duct run and terminate in the #1 position at the next box.  The position of all conduits between ground boxes and pull boxes shall be maintained.

Long radius bends (over 30 feet) shall be used whenever possible to make changes in direction.  If it is found to be necessary to place a 90-degree bend in the conduit run, a factory-made sweep of no less than 60-inch radius shall be used.  No conduit run shall exceed a total of 180 degrees of bend between any two points (such as manholes or buildings) considering both vertical and horizontal sweeps.  Cold-formed trench bends shall have a radius of not less than 60 inches and shall pass mandrel integrity.  Bend radius criterion is 2" or less 6 times the diameter of the conduit and any conduit larger than 2" is 10 times the diameter of the conduit.

Where communications and power conduits occupy the same trench, all conduit structures shall be built with the telecommunications conduits placed above the power conduits and separated by a minimum of 12” of compact earth or 3” of concrete encasement, unless otherwise called out and approved by OUSD.  If this type of construction is required, it shall receive the prior approval of the contractor and OUSD.

Conduit shall have a factory formed bell on one end for interconnecting segments.  All conduits shall be equipped with mechanical seal plugs in all ground boxes and expansion rubber seal plugs within all buildings.

Conduit located under heavy use highways or railroad rights-of-ways shall be encased in steel casing consistent with the AASHTO or AREA specifications.  The thickness of the steel casing shall be engineered for each specific application.  This may vary based on campus codes.

High impact spacers shall be used in all multi-duct systems, for both solely owned and joint telecommunications/power construction.  A horizontal and vertical separation of 1 inch between the ducts shall be maintained by installing high impact spacers with horizontal and vertical locking intervals of ten feet.  Spacers shall conform to NEMA TC-2, TC-6, TC-8, and ASTM F 512 dimensions.

Utility marking tape shall be buried 18 inches above the conduits.

The length and destination of all conduits shall be identified in each ground box, pull box and building.  Embossed metal or heavy plastic tags strapped to each conduit shall be used.

After installation of communications conduits, the contractor shall prove all conduits by pulling a mandrel with a diameter ¼ inch smaller than the conduit and 6 inches long through each conduit end-to-end.  An inspector designated by the contractor and OUSD shall be notified 24 hours before this procedure.  Each conduit shall be cleaned with a bristle brush to remove any debris.

All conduits shall be equipped with seal plugs in all pull boxes and expansion rubber seal plugs within all junction boxes and building entrances.

Contractor shall install new ¼” pull rope in all conduits placed.

Overhead Conduit.  OUSD prohibits the installation and use of overhead conduit extending between buildings.

Communications Entrance Conduit.  To prevent shear, all inter-building conduit transitions (either underground or aerial) shall transition from PVC or metal to Sealtight conduit when attaching between permanent structures.  The contractor and OUSD shall determine the placement of all entrance conduits.  All applicable standards (i.e., OUSD, NEC, BICSI or G.O. 128) shall be adhered to.

Transition from underground PVC to above ground stub up shall be via rigid conduit.  Sealtight flex conduit drip loop lengths shall not exceed 24”, unless approved by OUSD.

Conduits terminating inside of building through floor shall be installed so that the conduit extends a minimum of 4” above finished floor.  Conduits terminating inside of building through wall shall terminate in appropriately sized junction box.

Provide all coring, patching and painting as needed for Intra-Building and Inter-Building pathways.  Caulking is not an acceptable patching method for conduit penetrations into exterior walls.  Coordinate with OUSD for acceptable patching methods.

All conduits shall be properly reamed and bushed.  Contractor shall install new ¼” pull rope in all conduits placed.  Empty conduits shall be plugged with mechanical type seals to ensure that foreign matter does not enter the building.

Ductbank Locating Cable (e.g., electronically detectable warning tape).  Warning tape shall be a minimum of 3" wide, orange in color, and shall have a non-degradable imprint as follows:

# “Caution Fiber Optic Cable Buried Below”

The tape shall be electronically detectable.

Pull Rope.  Pull rope shall be new ¼" polypropylene over polyester rope with a minimum 1700 lb. Tensile strength.  Pull rope shall be new material that is free of knots, kinks, and abrasions and shall be placed as a single continuous length in every new conduit.  Pull rope shall be secured at each end.

# 1.7	Bonding and Grounding

MDF/IDF Grounding.  All MDF Racks shall be provided with a Telecommunications Grounding Busbar (TGB), installed in accordance with TIA/EIA-607.  The TGB shall be grounded to the nearest access to the building ground with a #6 AWG insulated conductor.  Building ground is identified as building structural steel, or ground rod; gas pipes and electrical conduits are not acceptable ground attachment points.

Ground conductors are not to exceed 40’.  If building ground connection is beyond 40’, Contractor is to install a new ground round at the nearest outside location.  The ground rod location shall be approved by OUSD prior to installation.

The Contractor shall provide ohms testing for ground.  Ground connections shall not exceed 5 ohms.  MDF ground rods shall consist of:

Fargo clamp:  Shall be cast from copper, silver-plated, and furnished with copper bolt.  Ground rod: shall be manufactured of high strength high carbon steel, with electrolytically bonded jacket of copper on surface, and meet UL spec. 467 and ANSI C-33.8-1072.

# 1.8	CCS Installation

General Installation Practices.  The Structured Communication Cable System and pathway, including the horizontal and backbone cable, pathway systems, telecommunications outlet/connector assemblies, and associated hardware shall be installed in accordance with TIA/EIA-568-B.1 and B.2, TIA/EIA-569, NFPA 70, and UL standards as applicable.

Cabling shall be connected in a star topology network.  Installation methodologies shall adhere to manufacturer installation procedures so as to not violate certifications (i.e. UL).  All work shall be performed in a good workmanship-like manner leaving each location in the same or better condition as at the start of each project.

CCS Contractor shall provide all necessary tools and materials not specified, (tie wraps, “d” rings, screws, consumables, hardware, etc.) and equipment, (ladders, hydraulic lifts, storage containers, etc.) necessary to provide a complete and operating system.

The OUSD-designated representative shall be provided progress reports.  Periodic on-site inspections will be done during the course of installation.  OUSD reserves the right of “local jurisdiction” for final approval.

Copper Cable Installation Practices.  Install Category 6 and Fiber Optic Backbone cabling and pathway system in accordance with TIA/EIA-568-B.1, B.2, B.3 and TIA/EIA-569.  The cabling installation shall comply with EIA TSB40-A and EIA TSB-36.

Where additional conduit sleeves are required, but not provided by others, the CCS Contractor shall be responsible to provide and install such conduit sleeves.

Applicable practices include, but are not limited to, the following:

Screw terminals shall not be used except where specifically indicated on plans.

Do not untwist Category 6 UTP cables more than 1/4 inch from the point of termination to maintain cable geometry.

Do not exceed manufacturers' cable pull tensions for copper and fiber optic cables.  Provide a device to monitor cable pull tensions.  Do not exceed 25 pounds pull tension for four pair copper cables.

Do not chafe or damage outer jacket materials.

Use only lubricants approved by cable manufacturer.

Do not over cinch cables, or crush cables with staples.

For UTP cable bend radii shall not be less than four (4) times the cable diameter.

All CCS cables shall be identified at both ends; underground pull boxes and junction boxes to include cable I.D., type, and size, destination fiber or pair count and any other pertinent information in accordance with OUSD established labeling procedures.  Identification shall be easily visible, firmly attached and impervious to moisture and other elements.

Open Cable.  Use only where specifically designated by OUSD or determined during site surveys and only when approved by OUSD.  When not run in surface mounted raceway or conduit, utilize cable hooks above suspended ceilings and in all ceiling spaces; install cabling above suspended ceilings 6 to 12 inches above ceiling T-bar using cable hooks spaced on centers not to exceed 48 inches and securely attached to structural ceiling..  Comply with TIA/EIA-568-B.1, B.2 and TIA/EIA-569.  Do not exceed cable pull tensions recommended by the manufacturer.

Plenum cable shall be used where required by industry standards, building and safety codes and OUSD rules and regulations; plenum cables shall comply with flammability plenum requirements of NFPA 70 and shall comply with UL 910.

Avoid routing copper cable in areas where there may be high levels of electromagnetic interference (EMI).  EMI is caused by AC power lines, broadcast signals, X-ray equipment, motors, generators, and fluorescent lights.  UTP cables shall be routed at least 5 inches away from fluorescent lighting fixtures.

Cables shall be placed in the support device, J-hooks located every 4 feet, as long as they are separately bundled and tie-wrapped using Velcro ties.  Cabling shall be organized and identified so as to facilitate locating and handling individual sheaths for maintenance functions.  Each bundle shall be neatly tied without over cinching or stressing cable.  Bundles shall be clearly marked identifying the IDF and room to which routed, the station numbers served by the bundle, and any other information that may assist in administration.

Great care shall be taken to protect all cabling from physical damage.  An industry standard service loop shall be installed on each cable installation where possible.

Fiber Optic Backbone Cable.  CCS Contractor shall be responsible for determination of actual segment lengths; actual quantities will be determined by the routing established by OUSD.  Do not exceed manufacturer's recommended bending radii and pull tension.  All fibers shall be terminated into fiber optic SC-type connectors.

Each fiber optic backbone cable segment shall be labeled at each end with its respective IDF identifier.  At each location where fiber optic cable is exposed to human intrusion, it shall be marked with warning tags.  A warning tag shall be permanently affixed to each exposed cable or bundle of cables, at intervals of not less than five (5) feet.  Any section of exposed cable, which is less than five (5) feet in length, shall have at least one (1) warning tag affixed to it.

Telephone Backbone Cabling.  Install properly sized Category 6, outdoor and underground rated cable in pathways.  The CCS Contractor shall be responsible for determination of actual segment lengths; actual quantities will be determined by the routing established by OUSD where needed for analog phone lines.

Horizontal Cabling.  The following is a list of typical/default outlets to be installed; however, OUSD may elect to specify different requirements within any particular RFP/RFB.  Unless specifically noted otherwise, all cabling shall be EIA/TIA Category 6, installed to industry standards and, unless otherwise specified, at 18” AFF.  All MDF/IDF terminations shall be on patch panels.  In all cases, one duplex electrical outlet (NEMA 5-15R) is required for each cable drop, and, to the extent possible, electrical receptacles shall be within 12” of the communications outlet.  [NOTE:  For purposes herein, the word “drop” shall denote one communication cable (as opposed to an outlet location).]

Classroom Outlets:  9 Drops per classroom (typically 5 student, 2 teacher, 1 phone and 1 clock/bell drop).  No more than 1 single jack every 30 inches or 2 dual jacks every 60 inches, except for teacher station.

Computer Lab Outlets:  33 Drops per computer lab (typically 30 student drops, plus 1 teacher, 1 phone and 1 clock/bell drop).  No more than 1 single jack every 30 inches or 2 dual jacks every 60 inches, except for teacher station.

Auditorium/Multipurpose Room Outlets:  8 Drops per auditorium/multipurpose room.  No more than 1 single jack every 30 inches or 2 dual jacks every 60 inches.

Office Outlets:

Workstations:  Three drops per outlet in private administrative offices and shared administrative work areas (1 computer, 1 printer, 1 phone).

Printer, Copier and Other Needs:  One drop per outlet.

CATV Outlets:  One RG-6 cable per outlet, terminated on an “F” style connector.  Typical CATV outlet heights for fixed locations shall be 78” AFF unless otherwise specified; CATV outlets for portable units shall be at 18” AFF.

Wireless Access Point Outlets:  One drop per outlet, terminated within a surface-mount outlet box.  If the location is within an accessible ceiling plenum, 15 feet of slack shall be provided at the outlet location, neatly coiled and secured.

Clocks, speakers, bells: One drop per outlet at each clock, speaker or bell location.

Kitchen and Cafeteria: Three drops per kitchen office space, and 2 drops at each cafeteria Point-of-Sale (POS) location.

Install horizontal cabling and pathway as determined at site surveys, between MDF and/or IDF and telecommunications outlet assemblies at workstations, in accordance with TIA/EIA-568-B.1 and B.2 and TIA/EIA-569.

If the Minimumum Point of Entry (MPOE) for the phone systems is located in a different room than the MDF, the CCS Contractor will run a Category 5 25-Pair Riser Cable from the MPOE to the MDF, terminating at a Modular 66M Cross Connect Block, 4 x 25, 25-pair --HPW66M125 or similar.

The CCS Contractor will coordinate with OUSD for placement information of each outlet to be completed.  Basic outlet configurations will be designated by OUSD.  The CCS contractor will coordinate with OUSD for outlet configuration details.

In general, horizontal station cables will: originate at the outlet location; extend through the ceiling plenum via wire hanger, cable tray, conduits/sleeves and/or other cable pathways, enter the MDF or IDF as applicable, and transition to the appropriate rack, cabinet or panel for termination.

CCS Contractor shall provide and install to work station outlet locations, with suitable infrastructure for routing, cables from the outlet location to and into the appropriate rack or panel in the MDF, IDF or SMALL IDF.

MDF, IDF and SMALL IDF terminations of data cables shall be in rack-mounted patch panels.  Patch panels shall be sized to allow a minimum of twelve (12) spare ports for future CCS requirements.

Terminations of analog voice station cables shall be on wall-mounted 66 blocks.

The CCS Contractor is responsible for replacement and reinstallation of any installed cable that does not meet the latest TIA/EIA performance parameters, without cost to OUSD.

Terminate UTP cable in accordance with TIA/EIA-568-B.1, B.2 and wiring configuration T568B.

The CCS Contractor will coordinate with OUSD for placement information of each outlet to be completed.  Basic outlet configurations will be designated by OUSD.  Coordinate with OUSD for outlet configuration details.

CCS Contractor shall provide and install to work station outlet locations with suitable infrastructure for routing cables from the outlet location to and into the appropriate rack or panel in the MDF, IDF or SMALL IDF.  Blank Inserts are to match the faceplate color.

# 1.9	CATV Cable System Provisions

General Description.  As applicable, the CATV Contractor shall furnish and install a Cable access Television (CATV) Distribution System per the defined scopes of work.  This section of the Specifications is intended to describe the necessary system.

Workmanship.  Contractor shall furnish and install all materials, including incidentals, necessary to perform The Work as described in this section.  Components of the CCS shall be installed in a neat, workmanlike manner in accordance with all drawings, specifications, and documents described in the bid specifications.  Wiring color codes and labeling schemes as described in this document shall be strictly observed and terminations shall be uniform throughout the system as described in Section 2.10.

All testing documentation will be required in latest version Excel on an Owner approved format to be provided one month before project completion.

Contractor shall furnish preliminary as-built drawings immediately after cable rough in.  Handwritten drawings are acceptable.  These drawings will be used by Owner to establish move-in circuit schedules.

CATV Cable System Products and Practices.  The scope of work includes all work related to installing wiring, aligning and testing broadband system equipment as shown on the drawings and as outlined in this document.  This includes all work from the outlet of head-end equipment to all drop outlets.  With the approval of OUSD Technology Services’ designee, Contractor may substitute OUSD approved equivalent products for the component specifications listed below:

Active Equipment:

Port Bridging Amplifier (Mini-Bridger):  CATV dual, power-doubled output amplifier.  Passband – 50 to 750MHz.  Operational gain - 36dBmV.  Maximum Noise Figure @ 50MHZ = 13.0, @ 750MHz = 11.5.  Required output level –47dBmV.  Approved Manufacturer:  General Instruments, Model “Starline MB-750D-H or BlonderTongue eq.”

Line Extender:  Forward operational, optional 90Vac output voltage, Output Current 10 Amps, Passband – 50 to 750MHz.  Operational gain - 29dB.  Maximum Noise Figure @ 50MHZ = 7.0, @ 750MHz = 9.0.  Required output level –47dBmV.  Approved Manufacturer:  General Instruments, Model BLE-75SH or BlonderTongue eq.

Distribution Power Supply:  CATV distribution power supply.  Input Voltage 120 VAC, Output Voltage 60Vac, Output Current 9 Amps.  Rack-mounted, UL Listed.  Approved Manufacturers – Lectro, Alpha or BlonderTongue eq.

Passive Equipment

Trunk Splitters and Directional Couplers:  CATV hard line directional coupler.  Passband – 50 MHz to 1GHz.  Connections: swivel center seizure mechanism.  Manufacturer General Instrument SSP-K series with specifications as shown on the Drawings or BlonderTongue eq.

Trunk Taps:  CATV hard line splitter.  Passband – 50 MHz to 1GHz.  Connections: brass “F” type ports, swivel center seizure mechanism.  Manufacturer General Instrument FFT-K series with specifications as shown on the Drawings.

Trunk Connectors:

Male:  CATV aluminum connectors with integral sleeve and center conductor pin.  Return Loss – Minimum 30dB up to 1 GHz.  Approved Manufacturer:  Gilbert GRS625 and GRS500 series.

Male-to-Male Splice Adapter:  CATV aluminum connectors with integral sleeve and center conductor pin for housing-to-housing connections.  Non-rotational.  Approved Manufacturer:  Gilbert GUS series.

Female:  CATV aluminum female connectors with integral sleeve providing a female F connector from cable.  Approved Manufacturer: Gilbert GRS625 and GRS500 series, GF625 and GF500 series.

Housing to Terminator:  CATV aluminum male connectors with integral sleeve providing a line termination.  75-Ohm impedance.  Approved Manufacturer:  Gilbert GTRM.

Drop Connectors:  CATV male F connector for RG6 cable, one piece, modular, to fit wall plate cutout.  Contractor shall submit product data sheet with bid response.

Drop Terminators:  CATV male F connector terminators: impedance 75 Ohm; Return Loss = min. 25dB up to 1GHz; Tolerance 2%, 1/8 watt.  Approved Manufacturer: Gilbert GTR-59-S.

Cables

Trunk:  RG11 copper clad aluminum center, expanded polyethylene dielectric, solid aluminum sheath with black medium density polyethylene jacket, flooding compound between jacket and aluminum sheath.  Approved manufacturer:  Commscope, Part # 5913.

Trunk:  .625 OD copper clad aluminum center, expanded polyethylene dielectric, solid aluminum sheath with black medium density polyethylene jacket, flooding compound between jacket and aluminum sheath.  Approved manufacturer:  Commscope, Part # P-3-75-625JCASS.

Trunk:  .500 OD copper clad aluminum center, expanded polyethylene dielectric, solid aluminum sheath, riser rated with flame retardant polyethylene jacket.  Approved manufacturer:  Commscope, Part # P-3-500-JCAR.

Inside Horizontal

Plenum:  RG6, 90% braid, 75 Ohm impedance, copper covered steel center conductor, foamed Teflon dielectric (FEP), inner shielded aluminum tape, outer shield bare aluminum braid wire.  Plenum rated jacket.  Approved Manufacturer:  Commscope, Part # 2276V.

PVC (non-plenum):  RG6, 90% braid, 75 Ohm impedance, copper covered steel center conductor, foamed polyethylene (FP), inner shielded aluminum tape, outer shield bare aluminum braid wire.  PVC jacket.  Approved Manufacturer:  Commscope, Part # 5726.

# Testing

Pre-Installation Cable Testing.  The Contractor shall test all optical cables prior to the installation of the cable.  The Contractor shall assume all liability for the replacement of the cable should it be found defective at a later date.

Fiber links shall have a maximum loss of:

(Allowable cable loss per km) x (km of fiber in link) + (.4dB) x (number of mated connectors) = total loss.  The maximum allowable loss for a multi-mode link is 4db.  A mated connector-to-connector interface is defined as a single connector for the purpose of this SPECIFICATION.

Loss numbers for the installed link shall be calculated by taking the sum of the bi-directional measurements and dividing that sum by two.

Any links, not meeting the requirement of the standard, shall be brought into compliance by the Contractor, at no charge, to OUSD.

Documentation shall be provided in both hard copy and CD Rom to the point of contact.

Inspection.  Visually inspect UTP and OFN jacket materials for UL or third party certification markings.  Inspect cabling terminations in telecommunications rooms and at workstations to confirm color code for tip and ring pin assignments, and inspect cabling connections to confirm compliance with TIA/EIA-568-B.1, B.2 and TIA/EIA-570.  Visually confirm Category 6 marking of cables, jacks, patch panels and patch cables.

Telecommunications Cabling Testing.  Perform telecommunications cabling inspection, verification, and performance tests in accordance with TIA/EIA-568-B.1, B.2 and B.3.  All testing personnel shall be trained on testing equipment tools to assure that complete and accurate testing results are obtained and provided.

Final Verification Tests.  Perform verification tests for UTP and OFN systems after the complete telecommunications cabling and workstation jacks are installed.

Perform 100 MHz near end cross talk (NEXT) and attenuation tests for Category 6 installations.  Testing of all copper wiring shall be performed prior to system cutover.  100 percent of the OSP and horizontal wiring pairs shall be tested for opens, shorts, polarity reversals, transposition and presence of AC voltage.  Voice and data horizontal wiring pairs shall be tested from the information outlet to the CRSC.  The cable runs shall be tested for conformance to the specifications of EIA/TIA 568A specifications for the appropriate category.  Testing shall be done with a TIA/EIA TSB-67 UL Certified Level 2 test set.  Test shall include length, mutual capacitance, characteristic impedance, attenuation, and near-end and far end cross talk.  The Contractor, at no charge shall bring any pairs not meeting the requirements of the standard into compliance to OUSD.  Complete, end-to-end test results must be submitted to OUSD.

All fiber testing shall be performed on all fibers in the completed end-to-end system.  Testing shall consist of a bi-directional end to end OTDR trace performed per EIA/TIA 455-61 and bi-directional end to end power meter test performed per EIA/TIA 455-53A.  Perform OFN end-to-end attenuation tests using an optical time domain reflectometer (OTDR) and manufacturer's recommended test procedures.  Perform tests in accordance with TIA/EIA-526-14-A, Method B for horizontal, multimode OFN.  Perform verification acceptance tests and factory reel tests.  The system loss measurements shall be provided at 850 and 1300 nanometers for multi-mode fibers.

Provide OUSD representative with written final tests verification within 1 week of completion of installation.  Final test results shall include summary pages for each MDF/IDF/SMALL IDF as required.  Test results shall be provided in both hard and soft copy.

# 1.11	Warranty

A minimum twenty five (25) year Extended Product and Application Assurance Warranty for this wiring system by the manufacturer shall be provided as follows:

Minimum 25-Year Extended Product Warranty.  The 25-Year Extended Product Warranty shall ensure against product defects; all approved cabling components shall exceed the specifications of TIA/EIA 568A and ISO/IEC IS 11801 and exceed the attenuation and NEXT requirements of TIA/EIA TSB 67 and ISO/IEC IS 11801 for data cabling links/channels.  The cable installation will exceed the loss and bandwidth requirements of TIA/EIA TSB 67 and ISO/IEC IS 11801 for fiber links/channels, for a minimum fifteen (15) year period.  The warranty shall apply to all passive data CCS components.

The 25-Year Extended Product Warranty shall cover the replacement or repair of defective product(s) and labor for the replacement or repair of such defective product(s) for a twenty-five (25) year period.

Minimum 25-Year Application Assurance and Channel Performance Warranty.  The minimum 25-Year Application Assurance and Channel Performance warranty shall cover the failure of the data wiring system under normal and proper use.  All components of the data CCS solution shall exceed the specifications of the Telecommunications Systems Bulletin TIA568-A and IOS/IEC 11801 for component and link/channel specifications in support of applications currently standardized which include, but are not limited to, the following:  155 Mbps ATM, 100 Mbps Fast Ethernet, 100VG-AnyLan, 100 Mbps TP-PMD, and 1000Base-SX and 1000Base-T.

System Certification.  Upon successful completion of the installation and subsequent inspection, the customer shall be provided with a numbered certificate, from the manufacturing company(s), registering the installation.

Additional Warranty.  Contractor shall state any additional Contractor supplied warranty.

# 1.12	Voice and Data CCS Labeling

The labeling shall be in accordance with the TIA/EIA-606 standards for data and voice.  The labeling shall be computer software generated and printed with readable fonts and black ink.  The ink and label shall be water and smear-proof for both indoor and outdoor use.  Samples of each type of media showing label type, labeling format, font size and ink shall be submitted for OUSD approval.

Voice and Data Systems Labeling.  The voice and data systems labeling shall include all related equipment, cables, racks and RJ-45 outlets.  Label all cables at each end of the cable designating the rack and port number.  The labeling shall be delineated on any riser diagrams, floor plans and test reports.  The labeling shall be computer software generated and printed with readable fonts and black ink.  Each and every cable termination must be labeled, with each and every cable labeled within two (2) inches of each end.  Termination labels and cable tags identifying two ends of the same cable must be the same color.  All labeling must be securely fastened, either using heat shrink or self-laminating labels and must be machine generated; handwritten labels are not acceptable.  Approval of OUSD’s Representative for sample labels of each type must be secured prior to commencing application.

Patch Panel Labeling.  Patch panels shall be provided with factory-installed label fields.  CCS Contractor installed labels shall identify work station outlet location and its room number and related patch panel port number with machine generated labels.

Outlet Labeling.  Outlets faceplates will be provided with factory installed label field labels.  CCS Contractor installed labels shall identify the appropriate MDF/IDF/SMALL IDF as well as the related patch panel and port number with machine generated labels.

# 1.13	As-Built Documentation

The CCS Contractor shall provide complete documentation of as-built conditions within ten business days of each CCS installation completion; late delivery of all submittals (including, but not limited to, as-built documentation) will cause delay of Acceptance by OUSD.  CAD backgrounds shall be provided in electronic form to OUSD via a media to be mutually determined.

The CCS Contractor shall provide updated AutoCAD drawings utilizing release 2002 or higher; such drawings will indicate site plans, floor plans, as-built conditions of all outlet locations (including outlet numbering), MDF and IDF areas, as well as main cable runs within the ceiling (including cable pathway apparatus such as cable trays, conduits, sleeves, and trapeze systems).

The CCS Contractor shall provide for each CCS installation one (1) “D” size laminated hardcopy plot of each drawing installation drawing set.  Laminated copies shall be left at each OUSD installation site.

The CCS Contractor shall provide for each CCS installation one (1) “E” size hardcopy plot of each drawing installation drawing set.  Copies shall be delivered to OUSD’s Technology Services Department.

As-Built documentation shall be provided to OUSD on a compact disc (CD) or other media as otherwise mutually agreed.

# 1.14	Miscellaneous Specifications

Ordering of Equipment and Materials.  The CCS Contractor shall responsible for placing orders for all required materials, components, and supplies, securing and forwarding to OUSD’s Representative written confirmations (including orders and shipping dates) direct from each manufacturer/supplier.  The CCS Contractor shall expedite shipment of all materials, components and supplies as necessary to ensure the successful completion of each installation by the date required.  Expedite charges, if necessary, will be submitted to OUSD for written approval prior to ordering.

Implementation Planning and Execution.  The CCS Contractor shall work with OUSD and OUSD’s Representatives to plan implementation schedules and methodologies, which minimizes impacts to users or other trades during installation and cutover processes.  All costs for planning and coordination as well as for after normal business hours labor shall be included within the CCS Contractor's pricing as provided.  Please note that, due to academic and administrative activities, implementation may generally be effected after normal business hours; overtime will be incurred by CCS Contractor (without additional cost to OUSD) only as necessary to ensure compliance with mutually agreed CCS installation milestones.

Training Requirements.  Respondent’s project price shall include an orientation session with OUSD’s technical/facility support personnel.  This session, which for planning purposes may last up to four hours, shall: provide an overview of the CCS architecture and its functionality; discuss cross-connect and/or patch cord implementation; review as-built documentation; and establish recommendations for effective management and maintenance of the installed CCS.

# 2.0	Network System Infrastructures

# 2.1	Overview

OUSD’s data communications network should be able to support a combination of LAN electronics and transports including:  Gigabit switches, and 10/100Mb/s switches aggregated back to a switch installed in a centralized location on each campus.

The new gigabit network design will utilize a star topology with fiber links back to the core switch at each campus.  This network design will allow all multiple 10/100/1000 Mb/s access points to be aggregated into a gigabit distribution switch located in each MDF/IDF.

The Gigabit Ethernet solution must provide scalability, complete compatibility, and be easily integrated into OUSD’s future wide area networks fabric.  This upgrade must be seamless in its migration to higher bandwidth requirements and comply fully with current 802.3z standards.  With the implementation of the Gigabit backbone OUSD expects a significant increase in performance over its existing networks.

# 2.2	Cabling and Network Infrastructures

OUSD requires a star network topology design that will support a Gigabit Ethernet Backbone.  The backbone cabling will extend from the Main Distribution Frame (MDF), to each of the MDF/IDF/SMALL IDF.  All fiber optic terminations will be home runs back to the MDF.

OUSD will accept the following manufacturer’s products (that are compliant with these specifications) or OUSD approved equivalents:

Cisco

# 2.3	Enterprise Network Architecture

OUSD requires enterprise network equipment to implement an L3 and L4 (Layer 3 & 4) IP network service over an Ethernet switching fabric, which will encompass the core, distribution, and local access components of OUSD’s network architecture.  The following high-level points characterize the network architectural direction of OUSD:

To the maximum extent that market offerings make it feasible, OUSD shall acquire network products adhering to industry supported standards and pre-standard specifications from recognized standards-making bodies, such as the IEEE Project 802 and the IETF.  The standards specified below are those deemed appropriate by OUSD to meet its requirements.

The bandwidth of switched segments, in OUSD network; 1 Gb/s segments will be deployed, as OUSD requirements dictate, which will constitute the entire backbone, core network, and some special user distribution and local access segments.  Switched segments to network end-stations, switches, and routers will be full duplex.

OUSD will run various L4 Internet transport protocols, including Transmission Control Protocol (TCP), User Data gram Protocol (UDP), and others as robust implementations become available and requirements warrant.

Although OUSD expects to continue to run IPv4 for the near to intermediate future, it is expected that a transition to IPv6 will be implemented at an appropriate point, perhaps motivated by such features as authentication, Quality of Service (QoS) priorities, and L3 address space expansion.

End-stations will be organized logically into VLANs.  Inter-VLAN communication will be provided by L3 routing functions.

It is OUSD’s objective to provide an Integrated Services IP packet network to support both traditional loss-sensitive/delay-tolerant flows (e.g. DNS queries) and loss-tolerant/delay-sensitive real-time flows (e.g. playback video streaming applications).

Each edge switch shall be fully layer 3 compliant.

Edge switches may be stackable or chassis based.  All edge switches shall be connected via home run fiber to the Main Distribution Frame.  Bidders may bid a stackable switch at the core on the Elementary Schools as long as they meet all other requirements within Section 2 of this technology specifications document.

# 2.4	Switched Architecture Characteristics

OUSD requires a network with Ethernet MAC-frame-switched architecture, with the exception of L3 packet switching for inter-VLAN operations and routing to external destinations.  Contractors shall:

Provide conceptual drawings of the configurations called for.

Provide a description of how end-to-end connectivity is provided for all required protocols, and include all switches and router protocols used to provide connectivity (i.e. Spanning Tree, RIP, OSPF, P-NNI etc.).

Describe what differentiates your product from your competition.

Network & Component Characteristics.  OUSD desire the following characteristics for the network and its components:

Gigabit Technical Specifications:

All Gigabit Ethernet switches must support Layer 3 switching for IP.  (Note: In Cisco switch lingo L3 means the IP addressing and the enterprise routing image, which we don’t really require and which costs more.  I think that Cisco or approved alternative is a better language)

All Gigabit Ethernet switches must have redundant switching fabrics.

All Core Gigabit Ethernet switches must have at least a 40G switching fabric.

All switches must support Policy and Port based VLANs.

All Layer 3 implementations should be standards-based.  No proprietary protocols or pre-standard protocols should be used to implement routing.

All Gigabit Ethernet switches must have wire-speed forwarding for Layer 2 and Layer 3 on 10/100 and Gigabit ports.  Preferred deterministic latency is under 10 microseconds for both Layer 2 and Layer 3.

Gigabit Ethernet switches must be able to use and understand OSPF, PIM, DVMRP or RIP II for routing purposes.

Gigabit Ethernet switches should support at least 20,000 MAC and routing table entries.

Gigabit Ethernet switches must support 802.1d Spanning Tree as well as multiple spanning tree groups.

Gigabit Ethernet switches must support 802.1Q VLAN tagging.

Gigabit Ethernet switches must support conversation steering/port mirroring to allow packet monitoring.

All devices should support management via local console access as well as remote network protocols such as Telnet, SSH or SNMP.

10/100 Ethernet Specifications

All switch ports must be 10/100 auto-sensing.

Ethernet switches must support at least eight (8) VLANs.

Edge devices must appropriately handle multicast traffic and IGMP.

All switch ports used to terminate drops for telephone handsets, clocks, bells and speakers must support Power-Over-Ethernet (POE).

Virtual LAN Architecture (L3 Inter-VLAN Operations)

Client utilizes VLAN functionally to segment video/audio applications (i.e., teleconferencing) traffic from the rest of the network.  OUSD requires standards-based VLANs for the logical organization of all end-stations within its enterprise network.

VLANs should be defined by network equipment in accordance with IEEE P802.1Q/D10.  L2 switching operations should conform to specifications in IEEE P802.1Q/D10 and IEEE 802.1D/D16.

Architecture.  OUSD requires high-speed, highly efficient L2 switches and L3 routers to implement an enterprise-wide configuration of Ethernet switching fabrics and an L3 switching hierarchy.

Media Applications.  OUSD requires an IP network service supporting real-time flow (e.g. video-streaming) applications in both unicast and multicast configurations.

Quality of Service.  OUSD requires an IP network service providing QoS assurances for both traditional data and multimedia network service applications.  This requirement has two distinct parts: Classes of Service (CoS) and end-to-end Quality of Service (QoS) provision by resource reservation.

# 2.5	Power Protection

OUSD requires suitable Uninteruptable Power Supply systems in all data closets to insure continuous operation of all routers, POE switches and backbone switches for 1 hour in the event of a power failure.

# 2.6	Network Security

OUSD requires one integrated scheme of network service user authentication and authorization for access to specific applications and data resources.  This scheme should be based upon appropriate (see below) standards, as initial product implementations become available.

VLAN Authentication and Authorization requires an authentication facility, which must be provided and authenticates an end-user by personal identification or a device by MAC address or receiving L2 switch port address for operation within one or more specific VLANs.  In addition, authorization controls must be provided to determine which applications and data resources an end-user or her workstation will be able to access.  Specify how the Equipment will make that possible.

# 2.7	Systems Testing and Acceptance

The vendor is asked to submit an acceptance plan as part of their response.  A minimum acceptable plan will include testing of LAN and Wide Area Network access to the targeted applications for each device.

3.0	Voice Communication
System Infrastructures

# 3.1 Overview

This section is for the acquisition, implementation and support of Voice Communications Systems and peripheral applications for OUSD. OUSD has standardized on the Cisco Unified Communications solution for all sites.

Each project will include the provisioning, by the selected Systems Integrator, of the endpoint equipment required to deliver a WAN that will provide voice and data communications over a private IP network. This WAN will be configured as a converged voice and data network. OUSD has deployed a Cisco Call Manager and will grow this system to provide services district wide and will use it as a basis on which to build future applications. The system will have a centralized Auto Attendant, centralized Voice Mail, and a centralized Contact Center. Trunking to the PSTN will be via PRI circuits. School sites will be equipped with Survivable Remote Site Telephony on their router along with circuits to the PSTN for back up and 911 access. Voice mail and Unified Messaging will be provided by a Cisco Unity system.  Auto attendant and Call Center capabilites will be provided from a Cisco IP Call Center Express system (IPCC Express).

3.2 Clocks, Bells, and Paging

The Berbee Informacast system will be integrated into the Cisco Call Manager and will provide a centralized system for paging, clocks, and bells in the District. All clocks, bells and speakers must be remotely manageable through the Informacast system.

# 3.3 Scope of Work

It is required that the CCS Contractor provides a complete equipment list, a thorough implementation/integration guideline, a thorough outline of testing procedures for voice and data performance and security on an Ethernet network, a thorough outline of post service and support. Below is a brief summary of CCS Contractor responsibilities pertinent to this project:

1. Communicate to OUSD Technology Services Coordinator the plans, designs, and implementation schedules.

2. Provide, design, install, and implement Cisco Unified Communications System network equipment and software specified within this bid.

3. Configure and administer network systems and software encompassing best practices for Security, Quality of Service (QoS), Call Admission Control (CAC), Resiliency, and Reliability.

4. Test all systems, integration, and performance across entire LAN, WAN and voice networks.

5. Train all end-users on the functionality of the IP Phones on premises, tailored specifically to OUSD’s particular requirements (e.g., console operator, secretary, and general end-user functions). This can be accomplished by scheduling training sessions with a group of 15-30 users or providing one-on-one training on an as needed basis with necessary training materials. Training schedule will be agreed upon with District’s Technical Services Coordinator and CCS Contractor.

6. Provide remote consulting support for ten (10) calendar days after initial acceptance from OUSD to assist with troubleshooting network LAN and WAN issues, IPTelephony issues, and user experience issues during this timeframe.

7. Provide a complete set of “as-built” diagrams both in paper and electronic form (Visio or other commercially available format) of the LAN and WAN infrastructure. Provide administrative usernames and passwords for all equipment to District’s Technology Services Coordinator. Credential Requirements.

The following is a list of credential requirements the CCS Contractor shall deliver for the bid:

1. OUSD specifically requests new, unused equipment of current vintage and software version. So that ongoing support can be assured, a Cisco certification of Gold or Silver with Cisco IP-Telephony Services Specialization will be required to be considered as a vendor for this equipment purchase. OUSD requires products be procured only through authorized channels as defined by Cisco Systems. All equipment will include the standard Cisco warranty and Smartnet coverage, and OUSD will be registered at Cisco as the original end user. If these conditions are not met, the equipment will be returned to the CCS Contractor and the CCS Contractor may be excluded from Cisco opportunities in the future.

2. OUSD requires the CCS Contractor to have a least one Cisco Certified Internetwork Expert (CCIE) on staff with specialization in Voice who will advise with the project.

3. The CCS Contractor must provide a minimum of three (3) reference accounts at which similar work, both in scope and design, have been completed by the CCS Contractor within the last three (3) years (focused on those that qualify the respondent for the project with at least one public agency reference). OUSD will contract only with CCS Contractors having a successful history of sales, installation, service, and support.

4. OUSD requires a dedicated Account Executive who will be the main point of contact for communications between OUSD and the CCS Contractor.

5. OUSD requires a dedicated Project Manager (s) who has thorough technology knowledge applicable to this project as well as management skills to finish the project according to the schedule guidelines set forth by the BID. It is a requirement the Project Manager (s) is onsite during key facets of the project.

# 3.4 Technology and Guidelines

# 1. Local Area Network (LAN) and Wide Area Network (WAN)

- Vendor shall coordinate with OUSD the installation of all Telco circuits and services

- Fiber patch cords to connect new equipment to fiber patch panels shall be supplied by the CCS ContractorCCS Contractor.

- All switches, routers, voice gateways and uninterruptible power supplies will be installed by the CCS Contractor using existing equipment cabinets/racks.

- CCS Contractor will provide all labor and materials to mount equipment as needed.

- The CCS Contractor shall provide a highly scalable and flexible Internet Protocol Version 4 (IPv4) addressing scheme.

- OUSD requires a cost-effective level of network security that is adequate to prevent outside monitoring of telephones calls, file transfers, passwords, sensitive data, etc.

- OUSD requires a highly intelligent network infrastructure that supports end-to-end Quality of Service (QoS) for voice, video and data. QoS shall be configured on all equipment internet worked within the LAN and WAN. The G.711 codec shall be configured for all IP-Telephony LAN communications, and the G.729 codec shall be leveraged for WAN communications.

- The CCS Contractor shall coordinate with OUSD, integrating as necessary with telecommunication circuits, routing protocols, and other OUSD parameters.

# 2. IP Communications (IP-Telephony)

a. Design specifics relative to Cisco CallManager and Cisco Unity Messaging System configuration requirements, LEC/CLEC/ILEC circuit provisioning and interface requirements, and other aspects shall be coordinated with OUSD Technology Services.

b. CCS Contractor will install all IP phones and record auto-registered directory number and location of IP phone installation. OUSD will be responsible for creating user accounts and IP phones with CallManager.

c. For non-Berbee Informacast systems, overhead paging access shall be available through a Foreign Exchange Office (FXO) port located on the Cisco router.

d. IP Phones shall be segmented by a Virtual Local Area Network (VLAN) and entirely segmented from other devices on LAN. Ultimately, IP-Telephony devices and IP data devices should occur on two logically disparate segments.

e. OUSD will be responsible for building the dial plan and calling search spaces to accommodate the OUSD location and VoIP devices.

f. On Hold music shall be played when callers are placed on hold.

# 3. Additional Solution Requirements.

a. Delivery, Storage, and Handling. The CCS Contractor shall protect equipment during transit, storage, and handling to prevent damage, theft, soiling, and misalignment.

Coordinate with OUSD’s Technology Services Coordinator for secure storage of equipment and materials. Do not store equipment where conditions fall outside manufacturer’s recommendations for environmental conditions.

b. Equipment. The CCS Contractor will label each newly installed device on the LAN. OUSD will assign the CCS Contractor with device names and each device will be tagged with electronically generatedlabels.

c. System Administration. OUSD requires the CCS Contractor to provide all necessary user names and passwords to all password sensitive equipment and systems. This includes the different administrative level logon names and passwords.

d. Warranty. The IP-Telephony/communications systems, components of the systems, software, hardware, IP-Phones, data/voice switches, data/voice routers, data/voice components of the switches and routers, network design, and implementation must be warranted by the CCS Contractor and by the manufacturer to be free of defects in equipment software, and workmanship for a period of at least one (1) year following

customer acceptance.

# 3.5 Required Station and Attendant Equipment

# 1. Station Equipment:

OUSD has standardized on these Cisco phone models:

Classrooms – CP-7940G with locking wallmount kit (cp-lckngwallmount=)

Office/Administration – CP-7960G

Receptionists – CP-7960G with CP-7914 expansion module

Executive offices – CP-7970G

Public Areas – CP-7912G with locking wallmount kit (cp-lckngwallmount=)

Wireless – CP-7920

Conference Stations– CP-7936

Softphone – Cisco IP Communicator, SW-IPCOMM-E

Vendor must also provide appropriate call manager licenses, SRST licenses, Informacast licenses and voicemail/unified messaging licenses for all handsets.

# 2. Operator/Attendant Console Position(s):

At minimum, the following functionality must be provided by the Bid system at the sites where a console is requested:

- Alphanumeric display for identification of internal callers, incoming calls, and for assistance in processing and extending calls. Please state the display capabilities of your attendant console equipment. • Secondary port for headset or handset to be used for training and quality control.

- Directory look-up capability that features a search function by name, department or extension number, and extends the call with a single keystroke (OUSD Office only).

- All Attendant Console(s) must be equipped with handset and headset equipment. The system must provide the ability to program the Attendant Console with individual DID extension number call appearances. This function will allow OUSD Operators to page individuals to a private DID telephone number.

a	Appendix A: Data Cabling System Design Standards

# Cabinet in MDF

- Install full-size, floor-mounted, fully enclosed, lockable cabinet in MDF.  Minimum of one cabinet per MDF.  (Note: if there is insufficient room for a fully enclosed cabinet, a two-post aluminum rack may be substituted only with the written permission of technology services).

- Properly mount and ground all racks.

- Install 19" rack-mounted horizontal patch cord/cable organizers for cable management in MDF.

- Install vertical jumper retainer cable organizers mounted to front of rack, on sides of rack frame (two per rack), running the full height of rack.

- Install 18" wide ladder rack between the top of rack and backboard with associated hanger supports and seismic bracing.

- Install one 12-port 19" rack mountable, one unit high combination patch panel LIU.  (One LIU for each 12-strand fiber cable).  LIU shall contain rear fiber entry slots, wire retainers, fiber storage drum, slide out rails for front access, and jumper trough for cable management in MDF.

- Install one 19" surge protected rack-mounted 3-wire electrical power strip with a minimum of 12-single outlets, mounted horizontally in MDF.  One power strip per rack.

- Install center weighted shelves for district supplied servers, keypads and monitor with associated seismic straps.  Minimum of one shelf per rack.

- Install a minimum of two dedicated 20 Amp circuit quadplex receptacle outlets in MDF to be used solely for network active components.

- MDF must be vented to industry standards.

# Cabinets in Large IDFs (greater than 48 terminations)

- Install full-size, floor-mounted, fully enclosed, lockable cabinet in each IDF.  Minimum of one cabinet per IDF.  (Note: if there is insufficient room for a fully enclosed cabinet, a two-post aluminum rack may be substituted only with the written permission of technology services).

- Properly mount and ground all cabinets/racks.

- Install 19" rack mounted horizontal patch cord/cable organizers for cable management in IDF.

- Install vertical jumper retainer cable organizers mounted to front of rack, on sides of rack frame (two per rack), running the full height of rack.

- Install 18" wide ladder rack between the top of rack and backboard with associated hanger supports and seismic bracing.

- Install one 6-port 19" rack mountable, one unit high combination patch panel LIU.  (One LIU for each 6-strand fiber cable).  LIU shall contain rear fiber entry slots, wire retainers, fiber storage drum, slide out rails for front access, and jumper trough for cable management in IDF.

- Install a minimum of one 19" surge protected rack-mounted 3-wire electrical power strip with a minimum of 12-single outlets, mounted horizontally in IDF.  Install a minimum of one power strip per rack.

- Install a minimum of one dedicated 20 Amp circuit quadplex receptacle outlet at each IDF location to be used solely for network active components.

- IDFs must be vented to industry standards.

# Cabinets in Small IDFs (48 terminations or fewer)

- Install one 16-gauge wall-mount cabinet with dual hinged lockable solid doors (front and back), having minimum dimensions of 36" high x 24" wide x 24" and maximum dimensions of 48" high x 24" wide x 24", 250 cfm exhaust fan, drilled EIA standard hole spacing, and vented side panels for mounting equipment specified herein at the Small IDF.

- Properly mount and ground all cabinets.

- Install one 6-port 19" rack mountable, one unit high combination patch panel LIU.  (One LIU for each 6-strand fiber cable).  LIU shall contain rear fiber entry slots, wire retainers, fiber storage drum, slide out rails for front access, and jumper trough for cable management in small IDF.  Install SC couplings for termination of fiber cables.

- Install a minimum of one 19" surge protected rack-mounted 3-wire electrical power strip with a minimum of 12-single outlets, mounted horizontally in the Small IDF.

- Install a minimum of one dedicated 20 Amp circuit for every two small IDF locations with a quadplex receptacle outlet at each Small IDF location.

- Small IDFs must be vented to industry standards.

# Fiber Optic Cables

- Install 6-strand multi-mode outside plant Fiber Optic cable from the MDF to each IDF.

- Fiber Optic cable shall have continuous sheath continuity.

- Each Fiber Optic cable shall be identified with a pre-established uniform numbering system.  Identification will be securely attached to the cable at each end, whenever it enters or leaves a conduit, and at the MDF, or IDF.

- Fiber Optic cable must be installed in 1" corrugated type innerduct (orange in color) when running in shared conduit.  Armored fiber is an acceptable alternative.

- Terminate all 6 fiber strands at each end of the cable with SC type connectors.

- Labeling of all terminations will be done to industry standards.

# Category 6 Cables

- Install 9 new PVC rated Category 6 cables for each classroom and 33 cables per computer lab.

- 5 data cables are for student use and 2 data cables are for teacher use, 1 data cable is for telephone handset and 1 data cable is for clock/bell/speaker.

- Install 1 new PVC rated Category 6 cable for each clock, bell or speaker location, both internal and external.

- Install 2-channel metal (aluminum model AL4000 or steel model 4000) surface-mounted raceway for the accommodation of new data cables and new AC electrical cable in the classrooms and computer labs to industry standards.  A total of 36 feet of surface-mounted raceway per classroom and computer lab.  Install one dedicated 20 amp circuit for every four network data jacks installed.  Install one duplex electrical receptacle for every network data jack installed.

- The CAT 6 4-pair cable will meet EIA/TIA Commercial Building Telecommunications Wiring Standards.

- Terminate the new Category 6 station cable on jacks at the station end and at the patch panel at the MDF or IDF end.

- Maintain the outer jacket of all Category 6 cables up to the leading edge of the wiring block at both ends of the cable.

- All jacks will use the EIA/TIA-568B wiring configuration.

- Maintain twists on all Category 6 cables up to the edge of the termination point of the data jack.

- No more than 2 data jacks will be terminated at each receptacle.

- Data Receptacles shall be placed in appropriate locations according to industry standards.

- Data receptacles shall be separated by no less than 30 inches for a single data jack receptacle, and no less than 60 inches for a dual data jack receptacle.

- Labeling of all terminations will be done to industry standards.

- Install new Category 6 patch cords in varying lengths (equal numbers of 3, 5, 7, 10 and 14 feet) as needed.  Provide one patch cord of varying length and one 3 foot patch cord for each small IDF switch port.  Provide one patch cord of varying length and one 7 foot patch cord for each large IDF or MDF switch port.

- Install two new Category 6 cables for each access point.  Data jacks for access points are to be installed to industry standards.  All cables will route through newly installed pathways.

- Install 32 new Category 6 cables for each computer laboratory.  Data jacks for access points are to be installed to industry standards.  All cables will route through newly installed pathways.

- Install two new Category 6 cables in each private administrative office.

- Install two Category 6 cable per workstation in shared administrative work area.

- Install minimum of one Category 6 cables for network printers in shared administrative work areas.

- Install a minimum of one Category 6 cables for network copiers in shared administrative work areas.

- Install eight Category 6 cables in the Auditorium/Multipurpose Rooms for workstations and printers.  Install one duplex electrical receptacle for every network data jack installed.  Locations for the data jacks in the Auditorium/Multipurpose rooms to be determined by OUSD Senior Architect and a representative from OUSD Technology Services Department.

# Networking Hardware in MDF

- Install one Cisco 3845 Router with SRST Voice Bundle in MDF, two 10/100/1000 Ethernet ports, 128 MB of Flash Memory and 256 MB of Main Memory.  Install High density voice/fax extension module (EVM-HD-8FXS/DID) and Four-Port Voice Interface Card (VIC2-4FXO). Install Cisco GLC-SX-MM SFP module.

- Install minimum of one Cisco 3750G-12S (WS-C3750G-12S) switch.  Install additional Cisco 3750G-12S Switches as needed to provide additional IDF connectivity.

- Install sufficient WS-C3560-24PS (WS-C3560-24PS-S) switches to provide sufficient ports for all phone, wireless access point and clock/bell/speaker drops, with a minimum of one WS-C3560-24PS (WS-C3560-24PS-S) switch per MDF, with 3560-24TS (WS-C3560-24TS-S) non-powered switches for the remaining terminations.

- Install Cisco 4400 series LAN wireless controller (or approved equivalent).

- Install two Cisco GLC-T 1000 Base-T SFP’s in the 3750G-12S switch.

- Install Cisco GLC-SX-MM SFP modules (Multimode Only) in all remaining SFP ports.

- Install 2 meter LC to SC Multimode Fiber Patch Cables in all fiber ports.

- Install one rack-mounted UPS for all switches and servers 1 hour minimum up time and appropriately rated for equipment in the MDF.

- Install CAT6 patch cables in each port.

- Install Tripp Lite Uninterruptable Power Supply (SU2200RTXL2U) with SNMP card (SNMPWEBCARD) and sufficient battery packs (BP48V212U) to provide 1 hour power protection for router, all POE switches and all backbone switching equipment.

- All Cisco equipment installed will include Cisco SmartNet 8x5xNBD warranty.

# Networking Hardware in each IDF

- Install sufficient WS-C3560-24PS (WS-C3560-24PS-S) switches to provide sufficient ports for all phone, wireless access point and clock/bell/speaker drops, with a minimum of one WS-C3560-24PS (WS-C3560-24PS-S) switch per IDF, with 3560-24TS (WS-C3560-24TS-S) non-powered switches for the remaining terminations.

- Install GLC-SX-MM SFP modules (Multimode Only) in all SFP ports.

- Install 2 meter LC to LC Multimode Fiber Patch Cables in all fiber ports.

- Install one rack-mounted UPS for all switches and servers (1 hour) in IDF.

- Install CAT 6 patch cables in each port.

- Install Tripp Lite Uninterruptable Power Supply (SU1000RTXL2U) with SNMP Card (SNMPWEBCARD) and sufficient battery packs (BP36V142U) to provide 1 hour power protection for all POE switches and backbone switching equipment.

- All Cisco equipment installed will include Cisco SmartNet 8x5xNBD warranty.

# Wireless Hardware.

- Install Wireless Access Points to allow full wireless coverage for all internal areas, including classrooms, lounges, administrative areas and hallways.

- Wireless Access Points will be installed to minimize overlapping areas of coverage between Access Points.

- Wireless Access Points shall be Cisco AP1250 with 802.11n and IOS Wireless LAN support.

- Install antenna and cable appropriate to the coverage area.

- Wireless access point, antenna and antenna cabling shall be installed in an area not visible to public access whenever possible, such as within the ceiling or a secured utilities closet.

- When a wireless access point must be installed in a public access area such as a hallway, it must be positioned at least 10 feet above floor level or installed in a secure, locking cabinet.

- All Cisco equipment installed will include Cisco SmartNet 8x5xNBD warranty.

- Equivalent non-Cisco equipment can be used with prior approval from Tech Services.