DEPARTMENT OF LABOR AND INDUSTRY

Safety and Health Codes Board

Title of Regulation: 16 VAC 25-50. Boiler and Pressure Vessel Regulations (amending 16 VAC 25-50-20, 16 VAC 25-50-150, 16 VAC 25-50-340, and 16 VAC 25-50-440; adding 16 VAC 25-50-445).

Statutory Authority: §§ 40.1-51.6 through 40.1-51.10 of the Code of Virginia.

Public Hearing Date: September 24, 2002 - 1 p.m.

Public comments may be submitted until 5 p.m. on November 8, 2002.

(See Calendar of Events section

for additional information)

Agency Contact: Fred P. Barton, Boiler Safety Compliance Director/Chief Boiler Inspector, Department of Labor and Industry, Powers-Taylor Building, 13 S. Thirteenth Street, Richmond, VA 23219, telephone (804) 786-3262, FAX (804) 371-2324 or e-mail fpb@doli.state.va.us.

Basis: The regulation is mandated by §§ 40.1-51.6 through 40.1-51.10 of the Code of Virginia. The scope of the mandate is that “no boiler or pressure vessel which does not conform to the rules and regulations of the (Safety and Health Codes) Board governing new construction and installation and which has been certified by the Board shall be installed or operated in this Commonwealth after twelve months from July 1, 1973.” There is no federal mandate for the regulation.

Purpose: The proposed amendments (i) protect the public’s health, safety and welfare with the least possible cost and intrusiveness to the citizens and businesses of the Commonwealth and (ii) continue evaluation of the need for changes to ensure current technical standards are met. The amendments regarding hobby boilers, redundant controls and manual resets, and national boiler and pressure vessel safety codes are public and workplace safety measures that bring the regulations up to date with state and national laws, standards and practices. The provision to allow certificate fees to be paid by credit card will provide an additional option and convenience to owners and users. The purpose of the amendments is to bring regulations into conformity with statutory changes regarding hobby boilers and provide for certificate fees to be paid by credit card. The amendments also adopt national standard provisions for two low-water fuel cutoffs on low-pressure boilers, a safety measure now required on high-pressure boilers, plus manual resets on all boilers. Further, the amendments incorporate references to the latest technological safety advances, such as manual resets, offered by national safety and inspection codes.

Substance: The amendments (i) remove language so as to eliminate possible conflicts with the recently enacted statute (§ 40.1-51.19 of the Code of Virginia) governing hobby boilers; (ii) provide for acceptance and processing of credit card payments for certificate fees; (iii) adopt Part CW (Steam and Waterside Control) of CSD-1-1998 to replace a reference to CSD-1-1992 in 16 VAC 25-50-340 and 6 VAC 25-50-440. This national standard contains provisions for improving the safe operation of steam boilers and pressure vessels by requiring redundant controls with manual resets on new installations; and (iv) update references to 2001 editions of the NFPA 85 Boiler and Combustion Systems Hazards Code, ASME Code and National Board Inspection Code to take advantage of the latest technological advances in safety.

Issues: Employees and the general public, where exposed, will benefit from a safer work environment by reduced exposure to unsafe equipment and a reduction in the probability of a boiler explosion. Boiler and pressure vessel owners and users will have the option of paying certificate fees by credit card. The use of credit cards will facilitate electronic reporting and allow the department to receive payments more quickly. The changes eliminate potential regulatory conflicts with hobby boiler statutes. The requirement of the manual reset (lockout) will draw users’ attention to the fact that the boiler is not functioning in a normal manner. The amendments adopt national standard provisions for two low-water fuel cutoffs on low-pressure boilers, a safety measure now required on high-pressure boilers, plus manual resets on all boilers. Presently, a low water condition is the second-leading cause for boiler accidents throughout the United States. Requiring two controls will result in fewer such accidents. Owners and users will be made aware of technological safety advances contained in prevailing national safety and inspection codes.

There are no disadvantages to the public or the Commonwealth relative to the amendments.

Department of Planning and Budget's Economic Impact Analysis: The Department of Planning and Budget (DPB) has analyzed the economic impact of this proposed regulation in accordance with § 2.2-4007 G of the Administrative Process Act and Executive Order Number 25 (98). Section 2.2-4007 G requires that such economic impact analyses include, but need not be limited to, the projected number of businesses or other entities to whom the regulation would apply, the identity of any localities and types of businesses or other entities particularly affected, the projected number of persons and employment positions to be affected, the projected costs to affected businesses or entities to implement or comply with the regulation, and the impact on the use and value of private property. The analysis presented below represents DPB’s best estimate of these economic impacts.

Summary of the proposed regulation. The Virginia Safety and Health Codes Board proposes to (i) accept credit card payments for certificate fees and (ii) require that newly installed steam boilers have two automatic low-water fuel cutoffs with manual resets.

Estimated economic impact. The proposed regulations add credit cards to the list of acceptable methods of certificate payment. Since no payment option has been eliminated and some boiler and pressure vessel owners may prefer to pay by credit card, this proposed change is beneficial for boiler and pressure vessel owners. The Department of Labor and Industry (department) finds payment by credit card to be advantageous in that the agency receives payment more quickly than under other methods. Thus, adding credit cards to the list of acceptable methods of certificate payment creates a net benefit.

Consistent with national standards, the board proposes to require that newly installed low-pressure boilers have two low-water fuel cutoffs and that all newly installed boilers have manual resets. Several manufacturers are already producing boilers that meet the new standards. A manual reset helps to prevent an explosion of a boiler by causing a safety shutdown and lockout in the event a safety valve malfunctions or the boiler material fails. The agency reports that, according to the National Board of Boiler and Pressure Vessel Inspectors, there have been 4,000 reported incidents in the U.S. involving low water conditions in the past five years. In Virginia, during this same period, there were eight incidents reported involving low water conditions. These events resulted in injuries and significant property damage. According to the department, such explosions have the potential to destroy an entire city block. The agency believes that the proposed additional controls significantly lower the probability of such accidental explosions. No data or research is available to estimate the reduced probability.1

The department estimates that boilers with a second low-water fuel cutoff and manual resets would cost $500 to $800 more than boilers without the additional controls. Without any estimate of the reduction in likelihood of boiler explosions due to the presence of the additional controls, it cannot be determined whether the benefits garnered from reduced probability of bodily injury and property damage exceed the $500 to $800 higher cost per new boiler.

Since the additional controls requirement only applies to new installations and adds non-negligible cost, some boiler owners may delay replacing their old boilers with new installations. In the short term, assuming that old boilers may be somewhat more likely to fail, the risk of accidents may increase. In the longer term, once all or most of the current boilers that do not meet the proposed requirements are replaced, the risk of accidents should decrease.

Businesses and entities affected. The proposed amendments potentially affect current and future steam boiler owners, firms that sell steam boilers, firms that manufacture the newly required controls, and individuals who spend time within the vicinity of steam boilers. The department estimates that up to 1,000 new steam boilers will be purchased per year.

Localities particularly affected. The proposed amendments potentially affect all Virginia localities.

Projected impact on employment. The proposed amendments may increase employment for firms that manufacture the proposed new required controls.

Effects on the use and value of private property. The manufacturers of the proposed new required controls will likely be able to sell more of their product and increase their firms’ value. Purchasers of steam boilers will face higher costs, which will likely reduce their firms’ value somewhat. Some firms that currently use steam boilers may opt to use a different heat source when the usable lifespan of their current boiler ends.

Agency's Response to the Department of Planning and Budget's Economic Impact Analysis: The Department of Labor and Industry and the Safety and Health Codes Board concur with the economic impact analysis prepared by the Department of Planning and Budget for the proposed amendments to 16 VAC 25-50.

Summary:

The proposed amendments eliminate possible conflicts with a recently enacted statute (§ 40.1-51.19 of the Code of Virginia) governing hobby boilers; allow certificate fees to be paid by credit card; adopt current Part CW of ANSI/ASME-CSD-1 provisions for burner controls and safety devices; and update references to prevailing National Fire Protection Association, American Society of Mechanical Engineers and National Board Codes.

16 VAC 25-50-20. Minimum construction standards for boilers and pressure vessels.

A. Boilers and pressure vessels to be installed for operation in this Commonwealth shall be designed, constructed, inspected, stamped and installed in accordance with the applicable ASME Boiler and Pressure Vessel Code including all addenda and applicable code case(s), other international construction standards which are acceptable to the chief inspector, and this chapter.

B. Boilers and pressure vessels shall bear the National Board stamping, except cast iron boilers and UM vessels. A copy of the Manufacturers' Data Report, signed by the manufacturer's representative and the National Board commissioned inspector, shall be filed by the owner or user with the chief inspector prior to its operation in the Commonwealth.

C. Pressure piping--(including welded piping)--Piping external to power boilers extending from the boiler to the first stop valve of a single boiler, and to the second stop valve in a battery of two or more boilers is subject to the requirements of ASME Power Boiler Code, Section I, and the design, fabrication, installation and testing of the valves and piping shall be in conformity with the applicable paragraphs of ASME Code. Applicable ASME data report forms for this piping shall be furnished by the owner to the chief inspector. Construction rules for materials, design, fabrication, installation and testing both for the boiler external piping and the power piping beyond the valve or valves required by ASME Power Boiler Code, Section I, are referenced in ANSI B31.1, Power piping, and the code.

D. Boilers and pressure vessels brought into the Commonwealth and not meeting code requirements shall not be operated unless the owner/user is granted a variance in accordance with § 40.1-51.19 of the Act.

The request for variance shall include all documentation related to the boiler or pressure vessel that will provide evidence of equivalent fabrication standards, i.e., design specification, calculations, material specifications, detailed construction drawings, fabrication and inspection procedures and qualification records, examination, inspection and test records, and any available manufacturers' data report.

In order to facilitate such a variance approval, the submission of documentation, in the English language and in current U.S. standard units of measure would be helpful. The following list of documents, while not all inclusive, would be useful in providing evidence of safety equivalent to ASME Code construction:

1. List of materials used for each pressure part;

2. The design calculations to determine the maximum allowable working pressure in accordance with the ASME Boiler and Pressure Vessel Code, applicable section, edition and addenda;

3. The design code used and the source of stress values for the materials used in the design calculations;

4. The welding procedures used and the qualification records for each procedure;

5. The material identification for each type of welding material used;

6. The performance qualification records for each welder or welding operator used in the construction of the boiler or pressure vessel;

7. The extent of any nondestructive examination (NDE) performed and the qualification records of NDE operators;

8. Record of final pressure test signed by a third party inspector;

9. Name and organization of the third party inspection agency;

10. A certification from a licensed professional engineer stating that the boiler or pressure vessel has been constructed to a standard providing equivalent safety to that of the ASME Boiler and Pressure Vessel Code. A signature, date and seal of the certifying engineer is required;

11. Where applicable, a matrix of differences between the actual construction of the boiler or pressure vessel for which a variance is requested and a similar boiler or pressure vessel that is code stamped; and

12. Where applicable, a letter from an insurance company stating that it will insure the boiler or pressure vessel.

After notification of a violation of these rules and regulations, an owner/user desiring a variance shall submit a request for variance within 30 days.

The chief inspector shall respond to any request for a variance within 30 days of receipt of all required documentation, and shall submit a recommendation to the commissioner, who will make the decision on the variance.

E. Before secondhand equipment is installed, application for permission to install shall be filed by the owner or user with the chief inspector and approval obtained.

F. Electric boilers, subject to the requirements of the Act and this chapter, shall bear the Underwriters' Laboratories label on the completed unit or assembly by the manufacturer. This label shall be in addition to the code symbol stamping requirements of the ASME and the National Board.

G. Replica or model boilers of historical nature; preserved, restored or maintained for hobby use; not intended for commercial use; and having an inside diameter less than or equal to 10 inches and a grate area less than or equal to 1 1/2 square feet and equipped with an ASME safety valve of adequate size, a water level indicator and a pressure gauge may have a certificate inspection every two years provided the owner provides a certification of safety valve testing annually.

16 VAC 25-50-150. Inspection certificate and inspection fees.

A. Upon the inspection and determination that a boiler or pressure vessel is suitable and conforms to this chapter, the owner or user shall remit the payment for an inspection certificate in one of the following forms and amounts for each item required to be inspected under the Act.

1. Payment of $20 may be mailed sent from the owner or user to the chief inspector by check, credit card or money order. Payment of inspection certificate fees should be made payable to the Treasurer of Virginia; or

2. Payment may be presented to a special inspector, where the inspector is authorized to collect and forward such fees on the department's behalf. The commissioner may authorize special inspectors to collect and forward to the chief inspector $16 for each inspection certificate. Pursuant to § 40.1-51.10:1 of the Code of Virginia, special inspectors may charge owners or users a fee not exceeding $4.00 for collecting and forwarding inspection certificate fees.

An inspection certificate will not be issued to the owner or user until payment is received by either the department or, if previously authorized, by a special inspector.

B. The chief inspector may extend an inspection certificate for up to three additional months beyond a two month grace period following the expiration of a certificate. Such extension is subject to a satisfactory external inspection of the boiler or pressure vessel and receipt of a fee of $20 for each month of extension.

C. When the chief inspector determines that no contract fee inspectors are available to inspect a regulated uninsured boiler or pressure vessel in a timely manner, a commonwealth inspector may be directed to conduct a certification inspection. Contract fee inspection service shall be determined unavailable where (i) at least two contract fee inspectors contacted will not agree to provide inspection services to the owner or user within at least 21 days from the request and (ii) the owner's or user's inspection certificate will expire within that same period.

The following rates per inspected object, in addition to inspection certificate fees, shall apply for certification inspections conducted by a commonwealth inspector:

1.	Power boilers and high pressure, 
high temperature water boilers	$135

2. Heating boilers	$70

3. Pressure vessels	$50

D. The review of a manufacturer's or repair organization's facility for the purpose of national accreditation will be performed by the chief inspector or his qualified designee for an additional fee of $800 per review or survey.

E. The owner or user who causes a boiler or pressure vessel to be operated without a valid certificate shall be subject to the penalty as provided for in§ 40.1-51.12 of the Act.

F. Inspection certificates are not required for unfired pressure vessels inspected by an authorized owner-user inspection agency. However, the agency shall keep on file in its office in the establishment where the equipment is located a true record or copy of the report of the latest of each inspection signed by the inspector who made the inspection.

16 VAC 25-50-340. Burner controls and safety devices.

Gas Fired burner installations shall conform to the requirements of the following nationally recognized standards including: the American Gas Association, Underwriters Laboratories, Part CW (Steam and Waterside Control) of ANSI/ASME-CSD-1 or National Fire Protection Association (NFPA) No. 85 series as applicable.

16 VAC 25-50-440. Automatic low-water fuel cutoff and/or water-feeding device.

A. Each automatically fired and unattended steam or vapor system boiler, except miniature boilers, shall be equipped with at least one two automatic low-water fuel cutoff cutoffs located so as to cut off the fuel or energy supply automatically when the surface of the water falls to the lowest safe water line. Power boilers, except miniature boilers, shall have two automatic low-water fuel cutoffs. Functioning of the lower of the two controls shall cause safety shutdown and lockout. The manual reset may be incorporated in the lower cutoff control. If a water-feeding device is installed, it shall be constructed so that the water inlet valves cannot feed water into the boiler through the float chamber and located so as to supply requisite feedwater. The lowest safe water line should be not lower than the lowest visible part of the water glass.

B. The fuel cutoff or water feeding device shall be attached directly to a boiler or in the tapped openings available for attaching a water glass directly to a boiler, provided the connections are made to the boiler with nonferrous tees or Y's not less than 1/2-inch pipe size between the boiler and the water glass so that the water glass is attached directly and as close as possible to the boiler; the run of the tee or Y shall take the water glass fittings, and the side outlet or branch of the tee or Y shall take the fuel cutoff or water feeding device. The ends of all nipples shall be reamed to full-size diameter.

C. Fuel cutoffs and water feeding devices embodying a separate chamber shall have a vertical drain pipe and a blowoff valve not less than 3/4-inch pipe size, located at the lowest point in the water equalizing pipe connections so that the chamber and the equalizing pipe can be flushed and the device tested.

D. A forced circulation coil or water tube type boiler, with a heat input greater than 400,000 BTU's per hour shall have a flow sensing device installed to cut off the fuel supply at a minimum water circulation flow rate in the boiler. The boiler manufacturer's specifications for the safe minimum flow rate, setting, and location of the flow sensing device shall be utilized.

16 VAC 25-50-445. Pressure control devices.

Each automatically fired steam boiler or system of commonly connected steam boilers shall have at least one steam pressure control device that will shut off the fuel supply to each boiler or system of commonly connected boilers when the steam pressure reaches a preset maximum operating pressure. In addition, each individual automatically fired steam boiler shall have a high steam pressure limit control with a manual reset that will prevent generation of steam pressure in excess of the maximum allowable working pressure and can cause safety shutdown and lockout.

DOCUMENTS INCORPORATED BY REFERENCE

1998 2001 Boiler and Pressure Vessel Code, ASME Code, American Society of Mechanical Engineers.

National Board Bylaws, National Board of Boiler and Pressure Vessel Inspectors, August 8, 1996.

ANSI/NB 23, 1998 2001 National Board Inspection Code, National Board of Boiler and Pressure Vessel Inspectors.

ASME B31.1, ASME Code for Pressure Piping, American National Standards Institute, 1995 and Addenda through 1997 1998.

NFPA 85C, Standards for the Prevention of Furnace Explosions/Implosions in Multiple Burner Boiler-Furnaces, 1991 85 Boiler and Combustion Systems Hazards, 2001 Edition, National Fire Protection Association.

Part CW (Steam and Waterside Control) and Part CF (Combustion Side Control) Flame Safeguard of ANSI/ASME CSD-1, Controls and Safety Devices for Automatically Fired Boilers, 1992 1998, American Society of Mechanical Engineers.

"Boiler Blowoff Equipment," National Board of Boiler and Pressure Vessel Inspectors, Rules and Recommendations for the Design and Construction of Boiler Blowoff Systems, 1991.

API510, Pressure Vessel Inspection Code, Maintenance Inspection, Rating, Repair and Alteration, Sixth Edition, June 1989, American Petroleum Institute.

VA.R. Doc. No. R02-16; Filed August 13, 2002, 10:45 a.m.

# Footnotes

1 Source: Department of Labor and Industry.